## ESP PLANT DATA
ESP PLANT DATA
| TIME LINE | BOILER LOAD | PARTICULATE ASH OUT OF ESP | DUST OUT OF ESP | FLUE GAS TEMPERATURE IN ESP, SOUTH (1) | FLUE GAS TEMPERATURE IN ESP SOUTH (2) | FLUE GAS TEMPERATURE IN ESP NORTH (1) | FLUE GAS TEMPERATURE IN ESP NORTH (2) | AVERAGE FLUE GAS TEMPERATURE IN ESP | FLUE GAS FLOW IN ESP, SOUTH | FLUE GAS FLOW IN ESP, NORTH | AVERAGE FLUE GAS FLOW IN ESP | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | ASH MEASUREMENTS | TOTAL ASH MEASUREMENT | TOTAL ASH + Mg BASED ADDITIVE | ASH REMOVAL EFFICIENCY
[5 empty] | (S) | (S) | (N) | (N) |  | (S) | (N)
| USE |  | IMPORT DATA |  | 17 | 18 | 21 | 22 | CALCULATE | 12 | 13 | CALCULATE | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | total | calc ash | CALCULATE | calc ash | ESP%
Time | 0.020833 | MW | kg/h | mg/Nm3 | degC | degC | degC | degC | degC | 000m3/h | 000m3/h | 000m3/h | kg/s | kg/s | kg/s | kg/s | kg/s | kg/s | kg/s | kg/s | kg/s | kg/s | kg/h | +Mg(OH)2 | %
19980501003000 | 1998-05-01 00:30 | 256.874 |  | 0.169 | 150.518 | 151.355 | 151.25 | 150.612 |  | 691.187 | 634.768 |  | 0.0032 | 0.007 | 3.4921 | 3.2404 | 4.4282 | 4.606 | 4.6418 | 4.4631 | 24.8818 | 0.022394 |  | 62.069 | 100
19980501010000 | 1998-05-01 01:00 | 255.563 |  | 0.904 | 150.37 | 153.062 | 151.466 | 151.577 |  | 696.77 | 654.852 |  | 0.0032 | 0.0078 | 3.4806 | 3.2273 | 4.4053 | 4.5784 | 4.5967 | 4.4319 | 24.7312 | 0.022258 |  | 62.069 | 100
19980501013000 | 1998-05-01 01:30 | 255.825 |  | 0.081 | 151.292 | 151.85 | 152.056 | 151.108 |  | 704.104 | 659.269 |  | 0.004 | 0.007 | 3.4875 | 3.2281 | 4.425 | 4.5618 | 4.6157 | 4.4404 | 24.7695 | 0.022293 |  | 62.069 | 100
19980501020000 | 1998-05-01 02:00 | 257.267 |  | 20.344 | 150.317 | 150.731 | 151.261 | 149.988 |  | 695.02 | 660.769 |  | 0.0047 | 0.0078 | 3.4897 | 3.1968 | 4.4258 | 4.5396 | 4.5769 | 4.4143 | 24.6556 | 0.02219 |  | 62.069 | 100
19980501023000 | 1998-05-01 02:30 | 256.454 |  | 0.415 | 150.059 | 151.695 | 150.714 | 150.953 |  | 704.02 | 655.185 |  | 0.0032 | 0.0078 | 3.4982 | 3.2289 | 4.4214 | 4.5571 | 4.6021 | 4.4351 | 24.7538 | 0.022278 |  | 62.069 | 100
19980501030000 | 1998-05-01 03:00 | 252.994 |  | 1.278 | 150.461 | 152.19 | 151.379 | 151.695 |  | 708.354 | 651.352 |  | 0.0032 | 0.0078 | 3.4845 | 3.2319 | 4.4136 | 4.5845 | 4.6121 | 4.4465 | 24.7841 | 0.022306 |  | 62.069 | 100
19980501033000 | 1998-05-01 03:30 | 257.083 |  | 0.17 | 150.114 | 150.432 | 150.729 | 149.689 |  | 693.52 | 633.185 |  | 0.0032 | 0.0093 | 3.4479 | 3.2129 | 4.3755 | 4.5479 | 4.583 | 4.4189 | 24.5986 | 0.022139 |  | 62.069 | 100
19980501040000 | 1998-05-01 04:00 | 254.279 |  | 0.783 | 149.797 | 151.618 | 150.45 | 151.37 |  | 689.353 | 632.518 |  | 0.0047 | 0.0078 | 3.4432 | 3.2174 | 4.3801 | 4.5579 | 4.5784 | 4.4304 | 24.6199 | 0.022158 |  | 62.069 | 100
19980501043000 | 1998-05-01 04:30 | 255.72 |  | 0.089 | 150.701 | 152.061 | 151.369 | 151.813 |  | 684.853 | 640.602 |  | 0.0032 | 0.0078 | 3.4554 | 3.2059 | 4.3787 | 4.5618 | 4.5747 | 4.4297 | 24.6172 | 0.022155 |  | 62.069 | 100
19980501050000 | 1998-05-01 05:00 | 253.99 |  | 0.785 | 150.358 | 151.932 | 151.65 | 150.199 |  | 692.187 | 633.768 |  | 0.0032 | 0.0078 | 3.4562 | 3.2242 | 4.3992 | 4.5586 | 4.5769 | 4.4365 | 24.6626 | 0.022196 |  | 62.069 | 100
19980501053000 | 1998-05-01 05:30 | 254.567 |  | 0.168 | 150.383 | 152.128 | 151.05 | 151.88 |  | 680.436 | 628.851 |  | 0.004 | 0.007 | 3.454 | 3.2242 | 4.3787 | 4.5449 | 4.5776 | 4.4502 | 24.6406 | 0.022177 |  | 62.069 | 100
19980501060000 | 1998-05-01 06:00 | 256.402 |  | 1.153 | 150.77 | 150.787 | 151.459 | 150.787 |  | 684.52 | 640.352 |  | 0.0032 | 0.0078 | 3.4631 | 3.222 | 4.406 | 4.5632 | 4.6204 | 4.4412 | 24.7269 | 0.022254 |  | 62.069 | 100
19980501063000 | 1998-05-01 06:30 | 258.42 |  | 0.173 | 149.855 | 151.426 | 150.71 | 150.931 |  | 683.27 | 631.101 |  | 0.0024 | 0.007 | 3.4738 | 3.2365 | 4.4136 | 4.5715 | 4.6204 | 4.4534 | 24.7786 | 0.022301 |  | 62.069 | 100
19980501070000 | 1998-05-01 07:00 | 257.319 |  | 0.904 | 150.7 | 152.313 | 151.459 | 152.313 |  | 685.27 | 633.102 |  | 0.0047 | 0.007 | 3.4479 | 3.2098 | 4.4014 | 4.5503 | 4.6106 | 4.4412 | 24.6729 | 0.022206 |  | 62.069 | 100
19980501073000 | 1998-05-01 07:30 | 252.784 |  | 0.165 | 150.773 | 150.776 | 151.689 | 150.528 |  | 678.186 | 644.602 |  | 0.0032 | 0.0078 | 3.4592 | 3.2327 | 4.4167 | 4.5632 | 4.6113 | 4.4656 | 24.7597 | 0.022284 |  | 62.069 | 100
19980501080000 | 1998-05-01 08:00 | 257.529 |  | 1.276 | 150.201 | 151.271 | 151.013 | 151.023 |  | 687.686 | 635.018 |  | 0.0032 | 0.0078 | 3.4653 | 3.1976 | 4.4045 | 4.5435 | 4.5923 | 4.4204 | 24.6346 | 0.022171 |  | 62.069 | 100
19980501083000 | 1998-05-01 08:30 | 259.81 |  | 0.169 | 150.489 | 151.637 | 151.29 | 150.647 |  | 686.603 | 639.518 |  | 0.0032 | 0.0085 | 3.4784 | 3.2159 | 4.4099 | 4.5479 | 4.5808 | 4.4326 | 24.6772 | 0.022209 |  | 62.069 | 100
19980501090000 | 1998-05-01 09:00 | 258.027 |  | 1.027 | 150.635 | 151.859 | 151.358 | 151.116 |  | 682.27 | 642.352 |  | 0.0032 | 0.0078 | 3.4998 | 3.2441 | 4.4387 | 4.5701 | 4.6135 | 4.4541 | 24.8313 | 0.022348 |  | 62.069 | 100
19980501093000 | 1998-05-01 09:30 | 257.713 |  | 0.293 | 150.636 | 151.936 | 151.609 | 151.936 |  | 696.353 | 645.852 |  | 0.0032 | 0.0078 | 3.4723 | 3.2235 | 4.4229 | 4.5601 | 4.6157 | 4.4587 | 24.7642 | 0.022288 |  | 62.069 | 100
19980501100000 | 1998-05-01 10:00 | 254.174 |  | 1.641 | 151.405 | 152.313 | 152.153 | 151.818 |  | 708.52 | 655.102 |  | 0.0032 | 0.0078 | 3.4592 | 3.2266 | 4.3916 | 4.5625 | 4.5869 | 4.4526 | 24.6904 | 0.022221 |  | 62.069 | 100
19980501103000 | 1998-05-01 10:30 | 254.488 |  | 0.291 | 150.878 | 150.358 | 151.757 | 150.111 |  | 708.854 | 663.269 |  | 0.0032 | 0.0078 | 3.5203 | 3.2228 | 4.448 | 4.5906 | 4.6433 | 4.4587 | 24.8947 | 0.022405 |  | 62.069 | 100
19980501110000 | 1998-05-01 11:00 | 250.871 |  | 1.274 | 150.022 | 151.282 | 150.829 | 149.797 |  | 700.437 | 670.019 |  | 0.0032 | 0.007 | 3.4845 | 3.238 | 4.4167 | 4.5801 | 4.6228 | 4.4509 | 24.8032 | 0.022323 |  | 62.069 | 100
19980501113000 | 1998-05-01 11:30 | 253.78 |  | 0.168 | 150.229 | 151.736 | 151.108 | 150.993 |  | 706.687 | 669.269 |  | 0.0032 | 0.0078 | 3.5181 | 3.2327 | 4.4624 | 4.5991 | 4.6548 | 4.458 | 24.9361 | 0.022442 |  | 62.069 | 100
19980501120000 | 1998-05-01 12:00 | 254.2 |  | 0.78 | 150.477 | 149.807 | 151.262 | 149.065 |  | 691.437 | 639.685 |  | 0.0032 | 0.007 | 3.4913 | 3.2242 | 4.4167 | 4.583 | 4.6394 | 4.4473 | 24.8121 | 0.022331 |  | 62.069 | 100
19980501123000 | 1998-05-01 12:30 | 258.342 |  | 0.288 | 149.517 | 151.669 | 150.135 | 151.174 |  | 695.103 | 644.268 |  | 0.0032 | 0.0085 | 3.4692 | 3.2136 | 4.4099 | 4.5754 | 4.6204 | 4.4365 | 24.7367 | 0.022263 |  | 62.069 | 100
19980501130000 | 1998-05-01 13:00 | 257.844 |  | 1.023 | 150.361 | 152.67 | 151.191 | 151.433 |  | 686.436 | 632.518 |  | 0.0032 | 0.0085 | 3.4509 | 3.1937 | 4.3884 | 4.5374 | 4.5938 | 4.4053 | 24.5812 | 0.022123 |  | 62.069 | 100
19980501133000 | 1998-05-01 13:30 | 258.814 |  | 17.777 | 150.205 | 150.742 | 151.192 | 149.752 |  | 676.853 | 631.435 |  | 0.0032 | 0.0078 | 3.4395 | 3.1862 | 4.374 | 4.5388 | 4.5906 | 4.3984 | 24.5385 | 0.022085 |  | 62.069 | 100
19980501140000 | 1998-05-01 14:00 | 259.076 |  | 1.024 | 150.394 | 152.825 | 150.854 | 151.835 |  | 680.186 | 639.935 |  | 0.0032 | 0.0085 | 3.4181 | 3.1549 | 4.3411 | 4.522 | 4.5679 | 4.3923 | 24.408 | 0.021967 |  | 62.069 | 100
19980501143000 | 1998-05-01 14:30 | 256.402 |  | 0.653 | 150.701 | 151.443 | 151.738 | 150.701 |  | 688.436 | 633.102 |  | 0.0032 | 0.007 | 3.4402 | 3.193 | 4.3777 | 4.5396 | 4.6052 | 4.4136 | 24.5795 | 0.022122 |  | 62.069 | 100
19980501150000 | 1998-05-01 15:00 | 258.158 |  | 1.024 | 150.476 | 152.068 | 151.392 | 151.078 |  | 681.27 | 632.935 |  | 0.0024 | 0.007 | 3.444 | 3.1984 | 4.377 | 4.5632 | 4.6143 | 4.4258 | 24.6321 | 0.022169 |  | 62.069 | 100
19980501153000 | 1998-05-01 15:30 | 256.376 |  | 0.162 | 150.657 | 151.103 | 151.332 | 150.113 |  | 682.27 | 635.352 |  | 0.0032 | 0.007 | 3.4432 | 3.1846 | 4.387 | 4.5547 | 4.6082 | 4.4121 | 24.6 | 0.02214 |  | 62.069 | 100
19980501160000 | 1998-05-01 16:00 | 259.364 |  | 1.269 | 150.222 | 152.496 | 150.972 | 151.258 |  | 678.519 | 641.602 |  | 0.0032 | 0.007 | 3.4333 | 3.1831 | 4.3564 | 4.5059 | 4.5464 | 4.3816 | 24.4169 | 0.021975 |  | 62.069 | 100
19980501163000 | 1998-05-01 16:30 | 257.136 |  | 19.835 | 150.773 | 152.223 | 151.638 | 150.737 |  | 683.27 | 635.685 |  | 0.0032 | 0.007 | 3.4554 | 3.1709 | 4.3945 | 4.5266 | 4.5784 | 4.3977 | 24.5337 | 0.02208 |  | 62.069 | 100
19980501170000 | 1998-05-01 17:00 | 254.934 |  | 1.023 | 150.599 | 151.14 | 151.398 | 152.13 |  | 684.52 | 634.018 |  | 0.0032 | 0.0085 | 3.4745 | 3.2021 | 4.4182 | 4.5425 | 4.5791 | 4.4182 | 24.6463 | 0.022182 |  | 62.069 | 100
19980501173000 | 1998-05-01 17:30 | 259.207 |  | 0.165 | 150.399 | 151.661 | 151.397 | 150.918 |  | 684.603 | 639.935 |  | 0.0032 | 0.0085 | 3.4615 | 3.1984 | 4.4099 | 4.5464 | 4.5913 | 4.4167 | 24.6359 | 0.022172 |  | 62.069 | 100
19980501180000 | 1998-05-01 18:00 | 256.743 |  | 5.184 | 150.621 | 151.816 | 151.586 | 151.073 |  | 666.519 | 642.352 |  | 0.0032 | 0.0078 | 3.4761 | 3.2205 | 4.4221 | 4.5479 | 4.5845 | 4.4243 | 24.6864 | 0.022218 |  | 62.069 | 100
19980501183000 | 1998-05-01 18:30 | 258.342 |  | 0.075 | 150.73 | 152.533 | 151.322 | 150.305 |  | 678.019 | 640.852 |  | 0.0032 | 0.0078 | 3.4836 | 3.1953 | 4.4397 | 4.5564 | 4.6243 | 4.425 | 24.7353 | 0.022262 |  | 62.069 | 100
19980501190000 | 1998-05-01 19:00 | 257.319 |  | 3.106 | 150.778 | 151.986 | 150.999 | 150.006 |  | 678.186 | 648.019 |  | 0.0032 | 0.0085 | 3.4958 | 3.2404 | 4.4448 | 4.5906 | 4.6272 | 4.4519 | 24.8624 | 0.022376 |  | 62.069 | 100
19980501193000 | 1998-05-01 19:30 | 257.896 |  | 0.077 | 150.633 | 151.347 | 151.201 | 151.842 |  | 685.353 | 637.102 |  | 0.0032 | 0.0078 | 3.5226 | 3.2472 | 4.457 | 4.5815 | 4.6296 | 4.4587 | 24.9076 | 0.022417 |  | 62.069 | 100
19980501200000 | 1998-05-01 20:00 | 256.271 |  | 0.903 | 150.306 | 151.62 | 151.575 | 150.63 |  | 689.853 | 630.518 |  | 0.004 | 0.0078 | 3.5012 | 3.2083 | 4.4548 | 4.5632 | 4.625 | 4.4441 | 24.8084 | 0.022328 |  | 62.069 | 100
19980501203000 | 1998-05-01 20:30 | 256.454 |  | 0.166 | 150.202 | 151.099 | 151.089 | 149.119 |  | 679.686 | 631.435 |  | 0.0032 | 0.0078 | 3.4662 | 3.1869 | 4.406 | 4.5525 | 4.6006 | 4.4221 | 24.6453 | 0.022181 |  | 62.069 | 100
19980501210000 | 1998-05-01 21:00 | 258.945 |  | 1.638 | 150.284 | 152.337 | 150.888 | 151.099 |  | 674.353 | 634.768 |  | 0.0032 | 0.0085 | 3.4845 | 3.2296 | 4.429 | 4.551 | 4.5974 | 4.4365 | 24.7397 | 0.022266 |  | 62.069 | 100
19980501213000 | 1998-05-01 21:30 | 258.997 |  | 0.075 | 150.677 | 151.321 | 151.557 | 150.826 |  | 681.936 | 624.351 |  | 0.0032 | 0.0093 | 3.4723 | 3.1862 | 4.4204 | 4.5266 | 4.5884 | 4.4053 | 24.6117 | 0.022151 |  | 62.069 | 100
19980501220000 | 1998-05-01 22:00 | 258.08 |  | 1.147 | 150.402 | 151.96 | 151.304 | 150.227 |  | 683.603 | 624.601 |  | 0.0055 | 0.0078 | 3.4738 | 3.2129 | 4.3992 | 4.541 | 4.5747 | 4.4214 | 24.6363 | 0.022173 |  | 62.069 | 100
19980501223000 | 1998-05-01 22:30 | 258.761 |  | 0.293 | 150.489 | 151.713 | 151.335 | 150.722 |  | 685.103 | 627.101 |  | 0.0024 | 0.0078 | 3.4875 | 3.2129 | 4.4487 | 4.5564 | 4.6143 | 4.4358 | 24.7658 | 0.022289 |  | 62.069 | 100
19980501230000 | 1998-05-01 23:00 | 256.638 |  | 1.15 | 150.277 | 152.156 | 151.336 | 150.671 |  | 687.686 | 635.935 |  | 0.0032 | 0.0085 | 3.5142 | 3.2251 | 4.4609 | 4.5632 | 4.6243 | 4.4487 | 24.8481 | 0.022363 |  | 62.069 | 100
19980501233000 | 1998-05-01 23:30 | 257.372 |  | 0.168 | 150.571 | 152.548 | 151.369 | 150.815 |  | 689.186 | 637.602 |  | 0.0024 | 0.0078 | 3.5104 | 3.2517 | 4.4763 | 4.6021 | 4.6296 | 4.4663 | 24.9466 | 0.022452 |  | 62.069 | 100
19980502000000 | 1998-05-02 | 255.17 |  | 2.255 | 150.898 | 151.233 | 151.734 | 150.49 |  | 689.77 | 646.602 |  | 0.0032 | 0.007 | 3.5111 | 3.2434 | 4.4663 | 4.6006 | 4.6394 | 4.4763 | 24.9473 | 0.022453 |  | 62.069 | 100
19980502003000 | 1998-05-02 00:30 | 255.851 |  | 0.168 | 150.252 | 151.676 | 151.186 | 150.686 |  | 684.52 | 642.518 |  | 0.0032 | 0.0078 | 3.4906 | 3.2159 | 4.4319 | 4.5564 | 4.6045 | 4.4365 | 24.7468 | 0.022272 |  | 62.069 | 100
19980502010000 | 1998-05-02 01:00 | 258.499 |  | 0.659 | 150.686 | 152.393 | 150.947 | 150.908 |  | 686.686 | 644.185 |  | 0.0047 | 0.0078 | 3.5348 | 3.2594 | 4.4724 | 4.5723 | 4.6326 | 4.458 | 24.942 | 0.022448 |  | 62.069 | 100
19980502013000 | 1998-05-02 01:30 | 257.11 |  | 0.165 | 150.798 | 151.964 | 151.503 | 150.727 |  | 685.77 | 637.352 |  | 0.0032 | 0.0085 | 3.4836 | 3.2174 | 4.4214 | 4.5251 | 4.5784 | 4.4243 | 24.6619 | 0.022196 |  | 62.069 | 100
19980502020000 | 1998-05-02 02:00 | 259.705 |  | 0.908 | 150.425 | 151.392 | 151.234 | 150.154 |  | 682.603 | 642.518 |  | 0.004 | 0.0085 | 3.5432 | 3.2709 | 4.4854 | 4.5959 | 4.6433 | 4.4807 | 25.0319 | 0.022529 |  | 62.069 | 100
19980502023000 | 1998-05-02 02:30 | 255.013 |  | 0.292 | 150.228 | 151.835 | 151.28 | 151.34 |  | 695.52 | 653.852 |  | 0.0024 | 0.0085 | 3.531 | 3.2434 | 4.48 | 4.583 | 4.6426 | 4.4724 | 24.9633 | 0.022467 |  | 62.069 | 100
19980502030000 | 1998-05-02 03:00 | 258.158 |  | 1.025 | 150.959 | 151.979 | 151.889 | 151.979 |  | 696.937 | 660.352 |  | 0.0024 | 0.0078 | 3.4913 | 3.2281 | 4.4265 | 4.5754 | 4.6143 | 4.4587 | 24.8045 | 0.022324 |  | 62.069 | 100
19980502033000 | 1998-05-02 03:30 | 257.11 |  | 0.165 | 150.658 | 151.562 | 151.478 | 151.067 |  | 697.437 | 650.685 |  | 0.0032 | 0.0078 | 3.4761 | 3.2136 | 4.4053 | 4.5313 | 4.5784 | 4.4304 | 24.6461 | 0.022181 |  | 62.069 | 100
19980502040000 | 1998-05-02 04:00 | 255.511 |  | 20.831 | 150.293 | 152.031 | 151.11 | 150.793 |  | 680.603 | 643.102 |  | 0.0032 | 0.0078 | 3.489 | 3.2059 | 4.425 | 4.5295 | 4.6052 | 4.4221 | 24.6877 | 0.022219 |  | 62.069 | 100
19980502043000 | 1998-05-02 04:30 | 255.013 |  | 0.169 | 150.493 | 150.025 | 150.834 | 150.272 |  | 692.187 | 649.435 |  | 0.0032 | 0.0078 | 3.4921 | 3.2327 | 4.4351 | 4.5396 | 4.5938 | 4.4473 | 24.7516 | 0.022276 |  | 62.069 | 100
19980502050000 | 1998-05-02 05:00 | 254.881 |  | 0.903 | 150.191 | 151.928 | 151.19 | 150.938 |  | 695.603 | 648.519 |  | 0.0032 | 0.0078 | 3.5272 | 3.2456 | 4.4663 | 4.5669 | 4.6279 | 4.457 | 24.9019 | 0.022412 |  | 62.069 | 100
19980502053000 | 1998-05-02 05:30 | 256.114 |  | 0.29 | 150.764 | 151.458 | 151.568 | 150.963 |  | 698.937 | 630.935 |  | 0.0032 | 0.007 | 3.489 | 3.2273 | 4.425 | 4.5449 | 4.583 | 4.4397 | 24.7191 | 0.022247 |  | 62.069 | 100
19980502060000 | 1998-05-02 06:00 | 256.035 |  | 0.779 | 150.178 | 150.391 | 151.096 | 148.906 |  | 691.853 | 641.185 |  | 0.004 | 0.0078 | 3.4958 | 3.2556 | 4.4502 | 4.5654 | 4.6067 | 4.467 | 24.8525 | 0.022367 |  | 62.069 | 100
19980502063000 | 1998-05-02 06:30 | 255.799 |  | 0.293 | 150.024 | 152.345 | 150.571 | 150.86 |  | 692.437 | 639.518 |  | 0.0032 | 0.0085 | 3.505 | 3.2418 | 4.4509 | 4.5625 | 4.6096 | 4.4702 | 24.8517 | 0.022367 |  | 62.069 | 100
19980502070000 | 1998-05-02 07:00 | 260.124 |  | 20.222 | 150.742 | 151.03 | 151.376 | 151.03 |  | 701.437 | 643.852 |  | 0.0032 | 0.0078 | 3.5745 | 3.2648 | 4.5151 | 4.5815 | 4.6509 | 4.5037 | 25.1015 | 0.022591 |  | 62.069 | 100
19980502073000 | 1998-05-02 07:30 | 258.63 |  | 0.168 | 150.401 | 151.628 | 151.539 | 151.133 |  | 691.353 | 641.935 |  | 0.0032 | 0.0078 | 3.5256 | 3.2648 | 4.4778 | 4.6096 | 4.6501 | 4.499 | 25.0379 | 0.022534 |  | 62.069 | 100
19980502080000 | 1998-05-02 08:00 | 261.12 |  | 1.026 | 150.4 | 151.082 | 151.212 | 150.339 |  | 693.27 | 650.769 |  | 0.0032 | 0.0078 | 3.5256 | 3.2639 | 4.4465 | 4.5815 | 4.6021 | 4.4854 | 24.916 | 0.022424 |  | 62.069 | 100
19980502083000 | 1998-05-02 08:30 | 258.63 |  | 0.078 | 150.4 | 151.473 | 151.104 | 150.483 |  | 696.853 | 644.018 |  | 0.0047 | 0.0078 | 3.5181 | 3.2556 | 4.4556 | 4.5754 | 4.6135 | 4.4771 | 24.9078 | 0.022417 |  | 62.069 | 100
19980502090000 | 1998-05-02 09:00 | 258.918 |  | 1.026 | 150.51 | 151.968 | 151.117 | 150.483 |  | 699.687 | 650.685 |  | 0.0032 | 0.0078 | 3.5294 | 3.2922 | 4.4724 | 4.5913 | 4.6455 | 4.5022 | 25.044 | 0.02254 |  | 62.069 | 100
19980502093000 | 1998-05-02 09:30 | 259.312 |  | 0.288 | 150.67 | 151.695 | 151.334 | 150.705 |  | 696.853 | 636.768 |  | 0.004 | 0.007 | 3.5355 | 3.2761 | 4.4656 | 4.5999 | 4.6479 | 4.5068 | 25.0428 | 0.022539 |  | 62.069 | 100
19980502100000 | 1998-05-02 10:00 | 260.727 |  | 0.781 | 150.586 | 152.046 | 151.523 | 152.789 |  | 698.853 | 636.518 |  | 0.0024 | 0.0078 | 3.5111 | 3.2861 | 4.4397 | 4.6189 | 4.6663 | 4.4954 | 25.0277 | 0.022525 |  | 62.069 | 100
19980502103000 | 1998-05-02 10:30 | 262.405 |  | 0.079 | 150.488 | 151.108 | 151.368 | 150.365 |  | 701.02 | 636.935 |  | 0.0024 | 0.0078 | 3.5005 | 3.2861 | 4.4387 | 4.6296 | 4.667 | 4.5198 | 25.0519 | 0.022547 |  | 62.069 | 100
19980502110000 | 1998-05-02 11:00 | 256.533 |  | 1.147 | 150.23 | 151.902 | 151.361 | 151.654 |  | 697.77 | 637.518 |  | 0.0032 | 0.0078 | 3.5538 | 3.2968 | 4.4763 | 4.6401 | 4.6951 | 4.5327 | 25.2058 | 0.022685 |  | 62.069 | 100
19980502113000 | 1998-05-02 11:30 | 260.596 |  | 0.079 | 150.597 | 151.458 | 151.392 | 150.221 |  | 699.437 | 642.268 |  | 0.0032 | 0.0085 | 3.5699 | 3.312 | 4.5059 | 4.6372 | 4.7112 | 4.5442 | 25.2921 | 0.022763 |  | 62.069 | 100
19980502120000 | 1998-05-02 12:00 | 256.428 |  | 0.901 | 150.715 | 151.979 | 151.218 | 150.742 |  | 696.187 | 638.602 |  | 0.0032 | 0.0078 | 3.5294 | 3.296 | 4.4648 | 4.6472 | 4.6943 | 4.5334 | 25.1761 | 0.022658 |  | 62.069 | 100
19980502123000 | 1998-05-02 12:30 | 258.735 |  | 0.164 | 150.468 | 150.768 | 151.51 | 150.768 |  | 693.853 | 648.019 |  | 0.0032 | 0.0085 | 3.5333 | 3.3052 | 4.4724 | 4.6333 | 4.689 | 4.5334 | 25.1783 | 0.02266 |  | 62.069 | 100
19980502130000 | 1998-05-02 13:00 | 258.866 |  | 1.515 | 150.16 | 151.495 | 151.288 | 150.257 |  | 687.936 | 647.769 |  | 0.0032 | 0.0078 | 3.5707 | 3.3029 | 4.522 | 4.6326 | 4.7083 | 4.5327 | 25.2802 | 0.022752 |  | 62.069 | 100
19980502133000 | 1998-05-02 13:30 | 260.046 |  | 0.164 | 149.987 | 151.887 | 150.656 | 150.897 |  | 690.02 | 646.102 |  | 0.0032 | 0.0085 | 3.4974 | 3.2678 | 4.448 | 4.5862 | 4.6326 | 4.4968 | 24.9405 | 0.022446 |  | 62.069 | 100
19980502140000 | 1998-05-02 14:00 | 259.364 |  | 4.083 | 150.804 | 151.598 | 151.543 | 150.361 |  | 685.52 | 651.852 |  | 0.0032 | 0.0085 | 3.5104 | 3.2784 | 4.458 | 4.5913 | 4.6548 | 4.5076 | 25.0122 | 0.022511 |  | 62.069 | 100
19980502143000 | 1998-05-02 14:30 | 260.439 |  | 0.164 | 150.306 | 151.923 | 151.384 | 150.933 |  | 685.27 | 651.435 |  | 0.0032 | 0.0078 | 3.5059 | 3.2754 | 4.4434 | 4.6021 | 4.6609 | 4.5112 | 25.0099 | 0.022509 |  | 62.069 | 100
19980502150000 | 1998-05-02 15:00 | 258.08 |  | 1.149 | 150.688 | 152.001 | 151.335 | 150.516 |  | 692.27 | 640.852 |  | 0.0032 | 0.0078 | 3.5516 | 3.2937 | 4.5015 | 4.6296 | 4.6997 | 4.5334 | 25.2205 | 0.022698 |  | 62.069 | 100
19980502153000 | 1998-05-02 15:30 | 258.918 |  | 0.165 | 150.437 | 152.001 | 151.369 | 150.763 |  | 693.187 | 643.102 |  | 0.0032 | 0.0093 | 3.5233 | 3.2953 | 4.4548 | 4.6272 | 4.6853 | 4.5295 | 25.1279 | 0.022615 |  | 62.069 | 100
19980502160000 | 1998-05-02 16:00 | 259.652 |  | 1.025 | 150.401 | 151.934 | 151.034 | 150.202 |  | 689.77 | 651.852 |  | 0.0024 | 0.0078 | 3.5592 | 3.3219 | 4.4946 | 4.6218 | 4.6951 | 4.5364 | 25.2392 | 0.022715 |  | 62.069 | 100
19980502163000 | 1998-05-02 16:30 | 256.454 |  | 0.168 | 150.474 | 152.053 | 151.367 | 151.063 |  | 695.687 | 652.019 |  | 0.0032 | 0.0078 | 3.5508 | 3.3014 | 4.4968 | 4.6243 | 4.676 | 4.5327 | 25.193 | 0.022674 |  | 62.069 | 100
19980502170000 | 1998-05-02 17:00 | 259.417 |  | 0.779 | 150.78 | 151.388 | 151.607 | 150.645 |  | 696.187 | 644.435 |  | 0.0032 | 0.0078 | 3.5325 | 3.3036 | 4.4807 | 4.6272 | 4.6731 | 4.5281 | 25.1562 | 0.022641 |  | 62.069 | 100
19980502173000 | 1998-05-02 17:30 | 254.724 |  | 0.655 | 150.312 | 153.641 | 151.231 | 151.661 |  | 716.187 | 669.519 |  | 0.0024 | 0.0078 | 3.5416 | 3.3296 | 4.5022 | 4.6548 | 4.7126 | 4.5532 | 25.3042 | 0.022774 |  | 62.069 | 100
19980502180000 | 1998-05-02 18:00 | 255.537 |  | 2.009 | 151.144 | 150.918 | 151.91 | 150.671 |  | 706.437 | 667.019 |  | 0.0032 | 0.0078 | 3.5226 | 3.2899 | 4.4548 | 4.6228 | 4.6646 | 4.5129 | 25.0786 | 0.022571 |  | 62.069 | 100
19980502183000 | 1998-05-02 18:30 | 254.96 |  | 20.948 | 149.984 | 151.14 | 150.772 | 149.16 |  | 708.187 | 666.769 |  | 0.0032 | 0.0093 | 3.5089 | 3.2861 | 4.4548 | 4.6106 | 4.6501 | 4.5105 | 25.0335 | 0.02253 |  | 62.069 | 100
19980502190000 | 1998-05-02 19:00 | 254.436 |  | 5.062 | 149.895 | 150.671 | 150.614 | 150.423 |  | 700.353 | 679.186 |  | 0.0032 | 0.0078 | 3.5256 | 3.293 | 4.4663 | 4.5747 | 4.6602 | 4.499 | 25.0298 | 0.022527 |  | 62.069 | 100
19980502193000 | 1998-05-02 19:30 | 255.196 |  | 0.658 | 150.098 | 151.413 | 150.926 | 150.423 |  | 703.02 | 668.936 |  | 0.0032 | 0.0101 | 3.5439 | 3.3151 | 4.4824 | 4.6333 | 4.6777 | 4.5388 | 25.2045 | 0.022684 |  | 62.069 | 100
19980502200000 | 1998-05-02 20:00 | 253.387 |  | 1.028 | 150.147 | 152.899 | 150.922 | 150.918 |  | 708.104 | 661.269 |  | 0.0047 | 0.0101 | 3.5439 | 3.2975 | 4.4893 | 4.5952 | 4.6616 | 4.5151 | 25.1174 | 0.022606 |  | 62.069 | 100
19980502203000 | 1998-05-02 20:30 | 254.147 |  | 0.168 | 150.648 | 151.635 | 151.122 | 150.397 |  | 704.604 | 667.102 |  | 0.004 | 0.0093 | 3.5653 | 3.328 | 4.5112 | 4.6372 | 4.6997 | 4.5496 | 25.3043 | 0.022774 |  | 62.069 | 100
19980502210000 | 1998-05-02 21:00 | 252.627 |  | 1.397 | 150.287 | 151.388 | 151.104 | 151.14 |  | 707.354 | 673.603 |  | 0.0047 | 0.0078 | 3.5317 | 3.3181 | 4.4731 | 4.6013 | 4.6563 | 4.522 | 25.115 | 0.022604 |  | 62.069 | 100
19980502213000 | 1998-05-02 21:30 | 253.099 |  | 19.369 | 150.304 | 151.702 | 151.585 | 151.454 |  | 713.604 | 678.353 |  | 0.0032 | 0.007 | 3.5355 | 3.3105 | 4.4763 | 4.5959 | 4.644 | 4.5151 | 25.0875 | 0.022579 |  | 62.069 | 100
19980502220000 | 1998-05-02 22:00 | 259.652 |  | 0.909 | 150.232 | 150.66 | 151.17 | 148.927 |  | 698.77 | 644.185 |  | 0.0032 | 0.0078 | 3.5059 | 3.3029 | 4.4495 | 4.5876 | 4.6433 | 4.5144 | 25.0146 | 0.022513 |  | 62.069 | 100
19980502223000 | 1998-05-02 22:30 | 258.971 |  | 0.169 | 150.102 | 151.872 | 150.421 | 151.624 |  | 694.52 | 646.269 |  | 0.0024 | 0.0085 | 3.5203 | 3.2883 | 4.4519 | 4.5869 | 4.6426 | 4.5137 | 25.0146 | 0.022513 |  | 62.069 | 100
19980502230000 | 1998-05-02 23:00 | 260.36 |  | 4.454 | 150.394 | 150.727 | 151.206 | 150.232 |  | 680.436 | 657.769 |  | 0.0032 | 0.0078 | 3.531 | 3.3005 | 4.4678 | 4.6052 | 4.6501 | 4.512 | 25.0776 | 0.02257 |  | 62.069 | 100
19980502233000 | 1998-05-02 23:30 | 257.398 |  | 0.168 | 150.114 | 153.228 | 151.009 | 151.248 |  | 697.02 | 650.519 |  | 0.0047 | 0.007 | 3.5432 | 3.293 | 4.4854 | 4.5862 | 4.6685 | 4.5144 | 25.1024 | 0.022592 |  | 62.069 | 100
19980503000000 | 1998-05-03 | 263.06 |  | 0.904 | 150.905 | 152.134 | 151.811 | 151.392 |  | 694.187 | 662.602 |  | 0.0032 | 0.0078 | 3.5066 | 3.2731 | 4.4365 | 4.5769 | 4.6289 | 4.4968 | 24.9298 | 0.022437 |  | 62.069 | 100
19980503003000 | 1998-05-03 00:30 | 262.588 |  | 0.081 | 150.752 | 150.427 | 151.812 | 150.427 |  | 697.52 | 656.685 |  | 0.0032 | 0.0078 | 3.5111 | 3.2601 | 4.4441 | 4.5579 | 4.6394 | 4.4868 | 24.9104 | 0.022419 |  | 62.069 | 100
19980503010000 | 1998-05-03 01:00 | 263.244 |  | 2.133 | 150.218 | 152.16 | 151.2 | 151.17 |  | 692.353 | 663.269 |  | 0.0032 | 0.0085 | 3.5325 | 3.2883 | 4.4609 | 4.5884 | 4.6387 | 4.5068 | 25.0273 | 0.022525 |  | 62.069 | 100
19980503013000 | 1998-05-03 01:30 | 261.54 |  | 0.293 | 150.665 | 151.443 | 151.109 | 150.453 |  | 701.853 | 653.019 |  | 0.0032 | 0.0078 | 3.4958 | 3.2655 | 4.4373 | 4.5496 | 4.6289 | 4.4832 | 24.8713 | 0.022384 |  | 62.069 | 100
19980503020000 | 1998-05-03 02:00 | 260.282 |  | 0.908 | 150.346 | 152.083 | 151.135 | 150.845 |  | 699.27 | 658.352 |  | 0.0024 | 0.0093 | 3.4928 | 3.2777 | 4.4282 | 4.5571 | 4.6121 | 4.4746 | 24.8542 | 0.022369 |  | 62.069 | 100
19980503023000 | 1998-05-03 02:30 | 258.761 |  | 0.17 | 150.673 | 151.562 | 151.341 | 150.819 |  | 700.02 | 657.186 |  | 0.0024 | 0.0078 | 3.5165 | 3.2808 | 4.4434 | 4.5776 | 4.6121 | 4.5076 | 24.9482 | 0.022453 |  | 62.069 | 100
19980503030000 | 1998-05-03 03:00 | 261.435 |  | 1.523 | 150.543 | 151.783 | 151.484 | 151.783 |  | 699.187 | 651.102 |  | 0.0032 | 0.0085 | 3.5089 | 3.2853 | 4.4465 | 4.5754 | 4.6326 | 4.4998 | 24.9602 | 0.022464 |  | 62.069 | 100
19980503033000 | 1998-05-03 03:30 | 264.214 |  | 0.08 | 150.555 | 151.237 | 151.506 | 150.742 |  | 696.187 | 649.769 |  | 0.0032 | 0.0085 | 3.5142 | 3.2838 | 4.4663 | 4.5625 | 4.6494 | 4.4885 | 24.9764 | 0.022479 |  | 62.069 | 100
19980503040000 | 1998-05-03 04:00 | 262.064 |  | 1.276 | 150.009 | 151.85 | 150.928 | 150.117 |  | 690.77 | 646.185 |  | 0.0032 | 0.0078 | 3.5256 | 3.2822 | 4.4509 | 4.5654 | 4.634 | 4.4954 | 24.9645 | 0.022468 |  | 62.069 | 100
19980503043000 | 1998-05-03 04:30 | 259.39 |  | 0.174 | 150.588 | 152.242 | 151.039 | 151.499 |  | 696.353 | 646.435 |  | 0.0032 | 0.0078 | 3.5172 | 3.3105 | 4.4556 | 4.6021 | 4.657 | 4.5356 | 25.089 | 0.02258 |  | 62.069 | 100
19980503050000 | 1998-05-03 05:00 | 257.582 |  | 1.889 | 151.106 | 152.19 | 152.021 | 151.695 |  | 703.854 | 666.686 |  | 0.0024 | 0.0078 | 3.5181 | 3.3151 | 4.4509 | 4.6035 | 4.6426 | 4.5342 | 25.0746 | 0.022567 |  | 62.069 | 100
19980503053000 | 1998-05-03 05:30 | 257.686 |  | 0.082 | 150.726 | 150.849 | 151.622 | 150.602 |  | 710.52 | 666.102 |  | 0.0032 | 0.007 | 3.5516 | 3.3402 | 4.4937 | 4.6326 | 4.6929 | 4.5608 | 25.282 | 0.022754 |  | 62.069 | 100
19980503060000 | 1998-05-03 06:00 | 257.136 |  | 1.034 | 149.918 | 150.302 | 150.801 | 148.817 |  | 702.937 | 661.686 |  | 0.0032 | 0.0085 | 3.5233 | 3.2914 | 4.4495 | 4.583 | 4.6418 | 4.519 | 25.0197 | 0.022518 |  | 62.069 | 100
19980503063000 | 1998-05-03 06:30 | 256.297 |  | 0.172 | 150.214 | 152.401 | 150.837 | 151.411 |  | 714.854 | 666.102 |  | 0.0032 | 0.0078 | 3.5439 | 3.296 | 4.4763 | 4.583 | 4.6731 | 4.5159 | 25.0992 | 0.022589 |  | 62.069 | 100
19980503070000 | 1998-05-03 07:00 | 259.705 |  | 1.401 | 150.538 | 149.601 | 151.491 | 148.611 |  | 697.603 | 636.435 |  | 0.0032 | 0.0085 | 3.5142 | 3.2845 | 4.4426 | 4.573 | 4.6272 | 4.4968 | 24.95 | 0.022455 |  | 62.069 | 100
19980503073000 | 1998-05-03 07:30 | 259.469 |  | 0.172 | 149.594 | 151.529 | 150.223 | 150.787 |  | 692.27 | 643.518 |  | 0.0032 | 0.0093 | 3.5181 | 3.2953 | 4.4509 | 4.5923 | 4.6462 | 4.519 | 25.0343 | 0.022531 |  | 62.069 | 100
19980503080000 | 1998-05-03 08:00 | 255.851 |  | 2.26 | 150.538 | 151.751 | 151.244 | 151.256 |  | 686.603 | 652.019 |  | 0.0032 | 0.0101 | 3.5256 | 3.3105 | 4.4624 | 4.6013 | 4.6548 | 4.5374 | 25.1053 | 0.022595 |  | 62.069 | 100
19980503083000 | 1998-05-03 08:30 | 256.874 |  | 0.172 | 150.729 | 151.426 | 151.633 | 150.436 |  | 693.103 | 645.018 |  | 0.0032 | 0.0055 | 3.5172 | 3.3181 | 4.4434 | 4.6143 | 4.6541 | 4.5388 | 25.0946 | 0.022585 |  | 62.069 | 100
19980503090000 | 1998-05-03 09:00 | 257.686 |  | 0.205 | 150.42 | 151.101 | 151.305 | 150.606 |  | 696.353 | 644.852 |  | 0.0032 | 0.0078 | 3.5142 | 3.3014 | 4.4509 | 4.5974 | 4.6509 | 4.5281 | 25.0539 | 0.022549 |  | 62.069 | 100
19980503093000 | 1998-05-03 09:30 | 254.331 |  | 0.174 | 150.511 | 151.766 | 151.296 | 151.271 |  | 692.603 | 649.019 |  | 0.0032 | 0.0078 | 3.5249 | 3.3029 | 4.4587 | 4.5974 | 4.6716 | 4.5374 | 25.1039 | 0.022594 |  | 62.069 | 100
19980503100000 | 1998-05-03 10:00 | 257.293 |  | 1.028 | 150.801 | 151.91 | 151.576 | 150.673 |  | 694.02 | 647.602 |  | 0.0032 | 0.0078 | 3.5142 | 3.3029 | 4.4434 | 4.5906 | 4.6411 | 4.5381 | 25.0413 | 0.022537 |  | 62.069 | 100
19980503103000 | 1998-05-03 10:30 | 254.331 |  | 0.295 | 150.569 | 151.585 | 151.26 | 150.843 |  | 693.687 | 648.769 |  | 0.0032 | 0.0078 | 3.5317 | 3.3212 | 4.467 | 4.6365 | 4.689 | 4.5625 | 25.2189 | 0.022697 |  | 62.069 | 100
19980503110000 | 1998-05-03 11:00 | 254.593 |  | 2.137 | 150.661 | 153.019 | 151.66 | 151.781 |  | 708.437 | 668.019 |  | 0.0047 | 0.0078 | 3.5111 | 3.3204 | 4.4509 | 4.606 | 4.6594 | 4.5374 | 25.0977 | 0.022588 |  | 62.069 | 100
19980503113000 | 1998-05-03 11:30 | 255.013 |  | 0.084 | 151.005 | 151.234 | 151.59 | 149.997 |  | 709.854 | 666.102 |  | 0.0032 | 0.0085 | 3.5264 | 3.3228 | 4.4534 | 4.6289 | 4.6707 | 4.5503 | 25.1642 | 0.022648 |  | 62.069 | 100
19980503120000 | 1998-05-03 12:00 | 256.061 |  | 20.248 | 150.078 | 151.234 | 150.891 | 150.739 |  | 711.604 | 656.936 |  | 0.0032 | 0.007 | 3.547 | 3.3052 | 4.4785 | 4.6121 | 4.6655 | 4.5381 | 25.1566 | 0.022641 |  | 62.069 | 100
19980503123000 | 1998-05-03 12:30 | 252.732 |  | 0.082 | 150.444 | 152.147 | 151.277 | 151.404 |  | 707.604 | 653.769 |  | 0.0032 | 0.0078 | 3.5226 | 3.2953 | 4.457 | 4.5784 | 4.6121 | 4.5076 | 24.984 | 0.022486 |  | 62.069 | 100
19980503130000 | 1998-05-03 13:00 | 260.255 |  | 1.278 | 150.337 | 149.476 | 151.126 | 148.733 |  | 682.27 | 647.102 |  | 0.0032 | 0.0078 | 3.5355 | 3.267 | 4.4678 | 4.5593 | 4.6272 | 4.4929 | 24.9607 | 0.022465 |  | 62.069 | 100
19980503133000 | 1998-05-03 13:30 | 256.297 |  | 0.172 | 149.73 | 152.121 | 150.362 | 150.883 |  | 696.02 | 644.935 |  | 0.0032 | 0.007 | 3.5028 | 3.2709 | 4.4404 | 4.5632 | 4.6006 | 4.4937 | 24.8818 | 0.022394 |  | 62.069 | 100
19980503140000 | 1998-05-03 14:00 | 257.922 |  | 2.137 | 150.727 | 151.013 | 151.724 | 151.013 |  | 692.187 | 659.936 |  | 0.0032 | 0.0085 | 3.4937 | 3.2479 | 4.4204 | 4.5342 | 4.5823 | 4.4648 | 24.755 | 0.02228 |  | 62.069 | 100
19980503143000 | 1998-05-03 14:30 | 251.159 |  | 0.172 | 150.237 | 152.132 | 151.535 | 151.142 |  | 685.686 | 620.601 |  | 0.0032 | 0.0078 | 3.3868 | 3.1373 | 4.303 | 4.4175 | 4.4946 | 4.3579 | 24.1081 | 0.021697 |  | 62.069 | 100
19980503150000 | 1998-05-03 15:00 | 251.71 |  | 1.771 | 150.731 | 149.852 | 151.157 | 150.595 |  | 684.603 | 634.518 |  | 0.0032 | 0.007 | 3.4211 | 3.1785 | 4.3281 | 4.4563 | 4.5198 | 4.387 | 24.301 | 0.021871 |  | 62.069 | 100
19980503153000 | 1998-05-03 15:30 | 249.822 |  | 0.171 | 150.128 | 151.988 | 150.868 | 150.998 |  | 689.77 | 633.352 |  | 0.0032 | 0.0078 | 3.447 | 3.2007 | 4.3542 | 4.4868 | 4.5273 | 4.4229 | 24.4499 | 0.022005 |  | 62.069 | 100
19980503160000 | 1998-05-03 16:00 | 249.665 |  | 1.403 | 150.613 | 152.354 | 151.514 | 150.126 |  | 686.103 | 629.351 |  | 0.0032 | 0.0078 | 3.4196 | 3.1709 | 4.3542 | 4.4448 | 4.5464 | 4.3823 | 24.3292 | 0.021896 |  | 62.069 | 100
19980503163000 | 1998-05-03 16:30 | 252.811 |  | 0.176 | 150.718 | 151.441 | 151.093 | 151.441 |  | 689.52 | 634.602 |  | 0.004 | 0.0078 | 3.4174 | 3.1671 | 4.3442 | 4.457 | 4.4998 | 4.374 | 24.2713 | 0.021844 |  | 62.069 | 100
19980503170000 | 1998-05-03 17:00 | 252.889 |  | 1.035 | 150.576 | 150.843 | 151.459 | 150.595 |  | 688.186 | 625.851 |  | 0.0047 | 0.0078 | 3.4402 | 3.1632 | 4.3564 | 4.4609 | 4.5403 | 4.3831 | 24.3566 | 0.021921 |  | 62.069 | 100
19980503173000 | 1998-05-03 17:30 | 249.691 |  | 0.083 | 150.038 | 151.833 | 150.93 | 151.338 |  | 685.353 | 626.018 |  | 0.0032 | 0.0078 | 3.4135 | 3.196 | 4.3442 | 4.467 | 4.5374 | 4.3992 | 24.3683 | 0.021931 |  | 62.069 | 100
19980503180000 | 1998-05-03 18:00 | 249.665 |  | 1.155 | 150.691 | 152.472 | 151.33 | 151.482 |  | 684.52 | 626.768 |  | 0.0032 | 0.0101 | 3.4714 | 3.2174 | 4.387 | 4.5059 | 4.5791 | 4.4326 | 24.6067 | 0.022146 |  | 62.069 | 100
19980503183000 | 1998-05-03 18:30 | 251.657 |  | 0.664 | 150.444 | 151.26 | 151.614 | 150.765 |  | 684.686 | 623.351 |  | 0.0032 | 0.0078 | 3.4174 | 3.1869 | 4.3289 | 4.4648 | 4.4907 | 4.3862 | 24.2859 | 0.021857 |  | 62.069 | 100
19980503190000 | 1998-05-03 19:00 | 253.833 |  | 1.035 | 150.383 | 151.77 | 151.156 | 150.78 |  | 685.186 | 633.852 |  | 0.0055 | 0.0085 | 3.4242 | 3.2113 | 4.3396 | 4.4753 | 4.5242 | 4.4021 | 24.3907 | 0.021952 |  | 62.069 | 100
19980503193000 | 1998-05-03 19:30 | 249.927 |  | 0.208 | 150.772 | 151.822 | 151.06 | 151.327 |  | 677.936 | 631.935 |  | 0.004 | 0.0078 | 3.444 | 3.2098 | 4.3625 | 4.4861 | 4.5417 | 4.4128 | 24.4687 | 0.022022 |  | 62.069 | 100
19980503200000 | 1998-05-03 20:00 | 253.833 |  | 0.913 | 150.025 | 151.172 | 150.75 | 150.429 |  | 681.686 | 617.768 |  | 0.0024 | 0.0078 | 3.4554 | 3.1862 | 4.3618 | 4.4702 | 4.5313 | 4.3899 | 24.405 | 0.021965 |  | 62.069 | 100
19980503203000 | 1998-05-03 20:30 | 252.365 |  | 0.176 | 150.449 | 152.136 | 151.189 | 150.898 |  | 687.27 | 616.768 |  | 0.0032 | 0.0078 | 3.444 | 3.1946 | 4.3557 | 4.4702 | 4.5425 | 4.3916 | 24.4096 | 0.021969 |  | 62.069 | 100
19980503210000 | 1998-05-03 21:00 | 252.889 |  | 1.035 | 150.791 | 150.821 | 151.494 | 151.563 |  | 684.02 | 617.434 |  | 0.0032 | 0.0085 | 3.4402 | 3.174 | 4.3518 | 4.4563 | 4.519 | 4.3862 | 24.3392 | 0.021905 |  | 62.069 | 100
19980503213000 | 1998-05-03 21:30 | 253.151 |  | 0.176 | 150.332 | 151.63 | 151.587 | 151.135 |  | 690.436 | 617.268 |  | 0.0032 | 0.007 | 3.4554 | 3.1869 | 4.3542 | 4.4763 | 4.5288 | 4.3953 | 24.4071 | 0.021966 |  | 62.069 | 100
19980503220000 | 1998-05-03 22:00 | 243.164 |  | 1.159 | 150.403 | 151.279 | 151.274 | 150.537 |  | 586.517 | 668.936 |  | 0.0047 | 0.0078 | 1.8159 | 3.0756 | 4.2305 | 4.3525 | 4.3909 | 4.2749 | 22.1528 | 0.019938 |  | 62.069 | 100
19980503223000 | 1998-05-03 22:30 | 249.639 |  | 0.296 | 150.264 | 150.928 | 150.795 | 150.186 |  | 582.767 | 670.269 |  | 0.0032 | 0.0078 | 0.0032 | 0.0055 | -0.0021 | 5.7083 | 5.7405 | 0.0024 | 11.4688 | 0.010322 |  | 62.069 | 100
19980503230000 | 1998-05-03 23:00 | 243.373 |  | 1.402 | 149.917 | 151.501 | 150.58 | 150.016 |  | 592.017 | 682.686 |  | 0.0047 | 0.0078 | 0.004 | 0.0063 | -0.0021 | 5.2322 | 5.3093 | 0.0017 | 10.5639 | 0.0095075 |  | 62.069 | 100
19980503233000 | 1998-05-03 23:30 | 208.246 |  | 0 | 150.178 | 151.098 | 150.909 | 150.603 |  | 654.602 | 571.183 |  | 0.0032 | 0.0078 | 0.0047 | 0.007 | -0.0006 | 0.0009 | 0.0017 | 0.0032 | 0.0279 | 2.511e-05 |  | 62.069 | 100
19980504000000 | 1998-05-04 | 125.593 |  | 1.653 | 149.692 | 149.639 | 150.507 | 149.144 |  | 607.517 | 478.43 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | -0.0029 | 0.0009 | 0.0017 | 0.0063 | 0.0272 | 2.448e-05 |  | 62.069 | 100
19980504003000 | 1998-05-04 00:30 | 0.026 |  | 1.281 | 143.701 | 107.852 | 144.153 | 109.579 |  | 479.514 | 418.512 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | -0.0014 | 0.0009 | 0.0002 | 0.004 | 0.0265 | 2.385e-05 |  | 62.069 | 100
19980504010000 | 1998-05-04 01:00 | 0 |  | 25.489 | 113.81 | 92.489 | 117.992 | 103.815 |  | -0.5 | 148.588 |  | 0.0032 | 0.007 | 0.004 | 0.0055 | -0.0037 | 0.0002 | 0.0017 | 0.004 | 0.0219 | 1.971e-05 |  | 62.069 | 100
19980504013000 | 1998-05-04 01:30 | 0 |  | 0.303 | 104.976 | 117.433 | 113.816 | 130.284 |  | 123.587 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | -0.0021 | 0.0009 | 0.0017 | 0.0047 | 0.0272 | 2.448e-05 |  | 62.069 | 100
19980504020000 | 1998-05-04 02:00 | 0 |  | 0.824 | 117.799 | 140.51 | 127.192 | 150.162 |  | 124.587 | 0 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | -0.0006 | 0.0009 | -0.0006 | 0.004 | 0.0249 | 2.241e-05 |  | 62.069 | 100
19980504023000 | 1998-05-04 02:30 | -0.026 |  | 18.934 | 134.393 | 151.588 | 142.995 | 158.766 |  | 108.67 | -0.083 |  | 0.0032 | 0.0078 | 0.0024 | 0.0055 | -0.0021 | 0.0009 | -0.0006 | 0.004 | 0.0211 | 1.899e-05 |  | 62.069 | 100
19980504030000 | 1998-05-04 03:00 | 0 |  | 0.177 | 144.204 | 156.545 | 151.294 | 161.991 |  | 107.753 | 0.083 |  | 0.0047 | 0.007 | 0.004 | 0.007 | -0.0037 | 0.0009 | -0.0006 | 0.004 | 0.0233 | 2.097e-05 |  | 62.069 | 100
19980504033000 | 1998-05-04 03:30 | -0.026 |  | 0.088 | 150.663 | 161.843 | 156.222 | 166.051 |  | 111.337 | 0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | -0.0044 | 0.0009 | 0.0002 | 0.004 | 0.0212 | 1.908e-05 |  | 62.069 | 100
19980504040000 | 1998-05-04 04:00 | 0 |  | 0.086 | 156.077 | 165.902 | 160.304 | 169.12 |  | 110.92 | 0 |  | 0.004 | 0.007 | 0.004 | 0.007 | -0.0014 | 0.0009 | -0.0006 | 0.0032 | 0.0241 | 2.169e-05 |  | 62.069 | 100
19980504043000 | 1998-05-04 04:30 | 0 |  | 0.426 | 160.483 | 168.816 | 163.619 | 170.549 |  | 112.337 | 0 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | -0.0037 | 0.0009 | -0.0006 | 0.0032 | 0.0218 | 1.962e-05 |  | 62.069 | 100
19980504050000 | 1998-05-04 05:00 | 0 |  | 0.425 | 163.903 | 170.781 | 166.137 | 172.761 |  | 113.587 | 0.167 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | 0.0009 | 0.0009 | -0.0006 | 0.0047 | 0.0287 | 2.583e-05 |  | 62.069 | 100
19980504053000 | 1998-05-04 05:30 | 0 |  | 0.426 | 166.506 | 172.55 | 167.981 | 172.798 |  | 115.753 | 0 |  | 0.004 | 0.0085 | 0.0047 | 0.007 | -0.0014 | 0.0009 | -0.0006 | 0.0032 | 0.0263 | 2.367e-05 |  | 62.069 | 100
19980504060000 | 1998-05-04 06:00 | 0 |  | 0.426 | 168.246 | 172.849 | 169.196 | 173.097 |  | 117.003 | 0 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | -0.0014 | 0.0009 | -0.0006 | 0.0032 | 0.0241 | 2.169e-05 |  | 62.069 | 100
19980504063000 | 1998-05-04 06:30 | 0 |  | 0.208 | 169.28 | 172.576 | 169.776 | 172.824 |  | 117.753 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | -0.0006 | 0.0002 | 0.0017 | 0.004 | 0.0266 | 2.394e-05 |  | 62.069 | 100
19980504070000 | 1998-05-04 07:00 | -0.026 |  | 0.428 | 169.662 | 172.524 | 169.783 | 172.277 |  | 118.253 | 0 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | -0.0014 | 0.0009 | 0.0009 | 0.004 | 0.0249 | 2.241e-05 |  | 62.069 | 100
19980504073000 | 1998-05-04 07:30 | -0.026 |  | 0.212 | 169.365 | 171.313 | 169.334 | 170.818 |  | 117.837 | 0.167 |  | 0.0032 | 0.0093 | 0.0024 | 0.0063 | -0.0006 | 0.0009 | 0.0002 | 0.004 | 0.0257 | 2.313e-05 |  | 62.069 | 100
19980504080000 | 1998-05-04 08:00 | -0.026 |  | 0.181 | 168.726 | 170.467 | 168.494 | 169.477 |  | 119.253 | 0 |  | 0.0032 | 0.0101 | 0.0047 | 0.0063 | -0.0014 | 0.0009 | -0.0021 | 0.0032 | 0.0249 | 2.241e-05 |  | 62.069 | 100
19980504083000 | 1998-05-04 08:30 | -0.026 |  | 0.088 | 167.679 | 168.059 | 167.345 | 168.059 |  | 120.337 | 0.083 |  | 0.0047 | 0.0078 | 0.004 | 0.0063 | -0.0006 | 0.0024 | 0.0017 | 0.0032 | 0.0295 | 2.655e-05 |  | 62.069 | 100
19980504090000 | 1998-05-04 09:00 | -0.026 |  | 0.178 | 166.323 | 167.239 | 165.857 | 166.001 |  | 121.337 | 0 |  | 0.0024 | 0.0078 | 0.0032 | 0.0063 | -0.0006 | 0.0002 | -0.0006 | 0.0032 | 0.0219 | 1.971e-05 |  | 62.069 | 100
19980504093000 | 1998-05-04 09:30 | 0 |  | 0.178 | 164.605 | 164.062 | 164.081 | 163.814 |  | 123.004 | 0 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | -0.0029 | 0.0002 | 0.0017 | 0.0032 | 0.025 | 2.25e-05 |  | 62.069 | 100
19980504100000 | 1998-05-04 10:00 | -0.026 |  | 0.092 | 162.774 | 162.566 | 162.09 | 161.081 |  | 125.087 | 0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.007 | -0.0014 | 0.0017 | 0.0009 | 0.0047 | 0.0286 | 2.574e-05 |  | 62.069 | 100
19980504103000 | 1998-05-04 10:30 | -0.026 |  | 0.09 | 160.642 | 160.013 | 159.925 | 158.28 |  | 123.92 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | -0.0021 | 0.0002 | 0.0017 | 0.004 | 0.0265 | 2.385e-05 |  | 62.069 | 100
19980504110000 | 1998-05-04 11:00 | 0 |  | 0.094 | 158.386 | 156.784 | 157.581 | 156.537 |  | 122.337 | 0.083 |  | 0.0047 | 0.0093 | 0.004 | 0.0085 | -0.0021 | 0.0009 | 0.0002 | 0.0032 | 0.0287 | 2.583e-05 |  | 62.069 | 100
19980504113000 | 1998-05-04 11:30 | 0 |  | 0.091 | 155.964 | 154.246 | 155.091 | 153.256 |  | 126.17 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | -0.0021 | 0.0009 | -0.0006 | 0.004 | 0.0235 | 2.115e-05 |  | 62.069 | 100
19980504120000 | 1998-05-04 12:00 | -0.026 |  | 0.094 | 153.39 | 151.616 | 152.468 | 150.131 |  | 126.67 | -0.167 |  | 0.0047 | 0.0085 | 0.0047 | 0.007 | -0.0029 | 0.0009 | -0.0006 | 0.0024 | 0.0247 | 2.223e-05 |  | 62.069 | 100
19980504123000 | 1998-05-04 12:30 | 0 |  | 0 | 150.711 | 148.583 | 149.739 | 146.603 |  | 127.337 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | -0.0021 | 0.0002 | 0.0002 | 0.0032 | 0.0228 | 2.052e-05 |  | 62.069 | 100
19980504130000 | 1998-05-04 13:00 | 0 |  | 0.179 | 147.947 | 145.525 | 146.943 | 144.04 |  | 126.17 | 0.167 |  | 0.0024 | 0.0078 | 0.0032 | 0.0055 | 0.0017 | 0.0009 | 0.0009 | 0.0047 | 0.0271 | 2.439e-05 |  | 62.069 | 100
19980504133000 | 1998-05-04 13:30 | 0 |  | 0 | 145.123 | 142.817 | 144.104 | 141.085 |  | 124.754 | 0.083 |  | 0.004 | 0.0078 | 0.004 | 0.007 | -0.0014 | 0.0002 | 0.0002 | 0.004 | 0.0258 | 2.322e-05 |  | 62.069 | 100
19980504140000 | 1998-05-04 14:00 | -0.026 |  | 0 | 142.293 | 140.084 | 141.246 | 138.105 |  | 125.004 | 0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0055 | 2.0837 | 0.0009 | 0.0017 | 0.0024 | 2.1084 | 0.0018976 |  | 62.069 | 100
19980504143000 | 1998-05-04 14:30 | 0 |  | 5.696 | 139.216 | 134.435 | 138.25 | 134.93 |  | 159.338 | 119.503 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 2.7925 | 0.0017 | -0.0006 | 0.0085 | 2.8241 | 0.0025417 |  | 62.069 | 100
19980504150000 | 1998-05-04 15:00 | -0.026 |  | 1.038 | 135.431 | 130.987 | 135.215 | 131.977 |  | 156.504 | 118.753 |  | 0.0032 | 0.0085 | 0.0032 | 0.007 | 3.09 | 0.0009 | -0.0006 | 0.004 | 3.1162 | 0.0028046 |  | 62.069 | 100
19980504153000 | 1998-05-04 15:30 | -0.026 |  | 0.794 | 132.297 | 128.555 | 132.312 | 128.555 |  | 153.921 | 117.003 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 3.2625 | 0.0002 | 0.0017 | 0.0032 | 3.2888 | 0.0029599 |  | 62.069 | 100
19980504160000 | 1998-05-04 16:00 | 0 |  | 16.458 | 129.377 | 126.032 | 128.509 | 125.29 |  | 153.254 | -0.083 |  | 0.0032 | 0.007 | 0.004 | 0.0063 | 3.3768 | 0.0009 | -0.0006 | 0.0032 | 3.4008 | 0.0030607 |  | 62.069 | 100
19980504163000 | 1998-05-04 16:30 | -0.026 |  | 0.305 | 126.14 | 116.215 | 124.261 | 122.144 |  | 153.004 | -0.083 |  | 0.0024 | 0.0078 | 0.004 | 0.0063 | 3.4631 | 0.0002 | -0.0006 | 0.004 | 3.4872 | 0.0031385 |  | 62.069 | 100
19980504170000 | 1998-05-04 17:00 | -0.026 |  | 18.899 | 121.751 | 114.657 | 119.873 | 117.867 |  | 152.671 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0078 | 3.5402 | 0.0009 | 0.0002 | 0.0047 | 3.5688 | 0.0032119 |  | 62.069 | 100
19980504173000 | 1998-05-04 17:30 | -0.026 |  | 0.179 | 117.5 | 109.073 | 115.713 | 114.255 |  | 150.754 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 3.6111 | 0.0017 | 0.0002 | 0.004 | 3.639 | 0.0032751 |  | 62.069 | 100
19980504180000 | 1998-05-04 18:00 | -0.026 |  | 0 | 113.151 | 99.824 | 111.886 | 110.424 |  | 152.504 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.007 | 3.6714 | 0.0002 | -0.0014 | 0.0032 | 3.6953 | 0.0033258 |  | 62.069 | 100
19980504183000 | 1998-05-04 18:30 | 0 |  | 0.546 | 108.902 | 92.635 | 108.313 | 107.413 |  | 151.421 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.007 | 3.7347 | 0.7333 | 0.0017 | 0.0024 | 4.4941 | 0.0040447 |  | 62.069 | 100
19980504190000 | 1998-05-04 19:00 | 0 |  | 0 | 104.835 | 87.099 | 104.866 | 103.093 |  | 152.421 | 0 |  | 0.0032 | 0.007 | 0.0032 | 0.0063 | 3.7958 | 0.0002 | -0.0006 | 0.0024 | 3.8175 | 0.0034357 |  | 62.069 | 100
19980504193000 | 1998-05-04 19:30 | 0 |  | 0.088 | 100.825 | 82.899 | 101.514 | 98.879 |  | 151.588 | -0.083 |  | 0.0024 | 0.0078 | 0.0047 | 0.0055 | 3.8499 | 0.0002 | 0.0009 | 0.0032 | 3.8746 | 0.0034871 |  | 62.069 | 100
19980504200000 | 1998-05-04 20:00 | -0.026 |  | 0 | 97.158 | 79.093 | 98.425 | 96.043 |  | 150.838 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 3.8979 | 0.0002 | 0.0002 | 0.0047 | 3.9243 | 0.0035319 |  | 62.069 | 100
19980504203000 | 1998-05-04 20:30 | -0.026 |  | 0 | 94.129 | 76.887 | 95.681 | 92.844 |  | 152.838 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0078 | 3.9423 | 0.0017 | -0.0014 | 0.0032 | 3.9693 | 0.0035724 |  | 62.069 | 100
19980504210000 | 1998-05-04 21:00 | 0.026 |  | 0 | 91.637 | 74.657 | 93.126 | 90.605 |  | 152.171 | 0 |  | 0.0032 | 0.0078 | 0.0055 | 0.0055 | 3.9712 | 0.0009 | -0.0014 | 0.0032 | 3.9959 | 0.0035963 |  | 62.069 | 100
19980504213000 | 1998-05-04 21:30 | -0.052 |  | 0 | 89.384 | 72.352 | 90.719 | 87.062 |  | 152.921 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.0071 | 0.0002 | 0.0002 | 0.0063 | 4.0365 | 0.0036329 |  | 62.069 | 100
19980504220000 | 1998-05-04 22:00 | 0 |  | 0 | 87.267 | 70.217 | 88.529 | 84.427 |  | 152.004 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0085 | 4.0337 | 0.0017 | -0.0006 | 0.0055 | 4.0638 | 0.0036574 |  | 62.069 | 100
19980504223000 | 1998-05-04 22:30 | 0 |  | 0 | 85.374 | 68.969 | 86.522 | 82.684 |  | 154.504 | -0.167 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.0566 | 0.0002 | 0.0017 | 0.004 | 4.0837 | 0.0036753 |  | 62.069 | 100
19980504230000 | 1998-05-04 23:00 | 0 |  | 0.086 | 83.734 | 67.131 | 84.716 | 81.82 |  | 154.171 | -0.083 |  | 0.0032 | 0.0085 | 0.0055 | 0.0055 | 4.0757 | 0.0009 | 0.0002 | 0.004 | 4.1035 | 0.0036931 |  | 62.069 | 100
19980504233000 | 1998-05-04 23:30 | 0 |  | 0 | 82.305 | 66.297 | 83.17 | 83.19 |  | 154.088 | 0 |  | 0.0024 | 0.0078 | 0.0032 | 0.0063 | 4.0969 | 0.0002 | 0.0009 | 0.0032 | 4.1209 | 0.0037088 |  | 62.069 | 100
19980505000000 | 1998-05-05 | 0 |  | 0 | 81.239 | 64.897 | 81.985 | 79.576 |  | 156.004 | 0 |  | 0.0024 | 0.0078 | 0.0032 | 0.0063 | 4.113 | 0.0009 | -0.0006 | 0.0017 | 4.1347 | 0.0037212 |  | 62.069 | 100
19980505003000 | 1998-05-05 00:30 | 0.026 |  | 0 | 79.963 | 63.357 | 80.601 | 77.784 |  | 158.671 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.1199 | 0.0002 | -0.0006 | 0.0032 | 4.144 | 0.0037296 |  | 62.069 | 100
19980505010000 | 1998-05-05 01:00 | 0 |  | 0.096 | 78.693 | 62.371 | 79.199 | 75.078 |  | 157.088 | -0.083 |  | 0.0047 | 0.0093 | 0.0024 | 0.007 | 4.1213 | 0.0002 | 0.0009 | 0.7578 | 4.9036 | 0.0044132 |  | 62.069 | 100
19980505013000 | 1998-05-05 01:30 | 0 |  | 0.184 | 77.511 | 61.09 | 77.767 | 73.548 |  | 156.588 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.1313 | 0.0009 | 0.0002 | 1.1316 | 5.2853 | 0.0047568 |  | 62.069 | 100
19980505020000 | 1998-05-05 02:00 | -0.026 |  | 0.181 | 76.401 | 59.962 | 76.478 | 72.416 |  | 156.088 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.1458 | 0.0009 | -0.0006 | 0.004 | 4.1714 | 0.0037543 |  | 62.069 | 100
19980505023000 | 1998-05-05 02:30 | 0 |  | 0.184 | 75.277 | 59.13 | 75.251 | 69.623 |  | 157.088 | 0 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.1428 | 0.0009 | -0.0006 | 0.0047 | 4.1698 | 0.0037528 |  | 62.069 | 100
19980505030000 | 1998-05-05 03:00 | 0 |  | 0.088 | 74.21 | 57.952 | 73.992 | 68.93 |  | 158.671 | -0.083 |  | 0.0024 | 0.0085 | 0.004 | 0.0063 | 4.1458 | 0.0017 | -0.0006 | 0.004 | 4.1721 | 0.0037549 |  | 62.069 | 100
19980505033000 | 1998-05-05 03:30 | 0 |  | 0 | 73.321 | 58.479 | 72.877 | 67.749 |  | 159.421 | 0.083 |  | 0.0017 | 0.0078 | 0.0047 | 0.0063 | 4.1284 | 0.0009 | 0.0009 | 0.0024 | 4.1531 | 0.0037378 |  | 62.069 | 100
19980505040000 | 1998-05-05 04:00 | 0 |  | 0 | 72.439 | 57.764 | 71.795 | 66.298 |  | 159.921 | 0 |  | 0.0024 | 0.0101 | 0.004 | 0.0055 | 4.1199 | 0.0009 | -0.0006 | 0.0024 | 4.1446 | 0.0037301 |  | 62.069 | 100
19980505043000 | 1998-05-05 04:30 | 0 |  | 0 | 71.565 | 56.394 | 70.691 | 64.681 |  | 160.505 | 0 |  | 0.0047 | 0.0078 | 0.0032 | 0.0063 | 4.1199 | 0.0009 | -0.0006 | 0.0024 | 4.1446 | 0.0037301 |  | 62.069 | 100
19980505050000 | 1998-05-05 05:00 | 0 |  | 0.088 | 70.626 | 55.846 | 69.637 | 63.155 |  | 160.421 | 0 |  | 0.0047 | 0.0078 | 0.0047 | 0.0063 | 4.1267 | -0.0006 | 0.0009 | 0.0032 | 4.1537 | 0.0037383 |  | 62.069 | 100
19980505053000 | 1998-05-05 05:30 | 0 |  | 0.086 | 69.936 | 55.668 | 68.602 | 62.001 |  | 160.421 | 0.083 |  | 0.0032 | 0.0085 | 0.0032 | 0.007 | 4.062 | 0.0017 | 0.0002 | 0.0024 | 4.0882 | 0.0036794 |  | 62.069 | 100
19980505060000 | 1998-05-05 06:00 | 0 |  | 0 | 69.332 | 55.197 | 67.635 | 59.579 |  | 160.171 | -0.25 |  | 0.0032 | 0.0093 | 0.004 | 0.0063 | 4.071 | 0.0009 | -0.0014 | 0.0032 | 4.0965 | 0.0036868 |  | 62.069 | 100
19980505063000 | 1998-05-05 06:30 | -0.026 |  | 16.004 | 68.658 | 54.315 | 66.68 | 59.67 |  | 162.921 | -0.167 |  | 0.004 | 0.0085 | 0.0032 | 0.0063 | 4.1665 | 0.0009 | 0.0009 | 0.004 | 4.1943 | 0.0037749 |  | 62.069 | 100
19980505070000 | 1998-05-05 07:00 | 0 |  | 0 | 68.003 | 55.328 | 65.816 | 58.979 |  | 160.171 | -0.25 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.1047 | 0.0009 | -0.0006 | 0.0032 | 4.1309 | 0.0037178 |  | 62.069 | 100
19980505073000 | 1998-05-05 07:30 | 0 |  | 18.571 | 67.462 | 54.689 | 64.992 | 57.365 |  | 160.421 | -0.167 |  | 0.0024 | 0.0078 | 0.0047 | 0.0055 | 4.0779 | 0.0009 | -0.0006 | 0.004 | 4.1026 | 0.0036923 |  | 62.069 | 100
19980505080000 | 1998-05-05 08:00 | -0.026 |  | 0.096 | 66.762 | 54.511 | 64.096 | 56.944 |  | 161.338 | 0 |  | 0.004 | 0.0078 | 0.0047 | 0.0055 | 4.071 | 0.0009 | 0.0002 | 0.0032 | 4.0973 | 0.0036876 |  | 62.069 | 100
19980505083000 | 1998-05-05 08:30 | 0 |  | 0.097 | 66.134 | 53.412 | 63.244 | 56.087 |  | 164.005 | 0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | 4.0779 | 0.0009 | -0.0014 | 0.004 | 4.1018 | 0.0036916 |  | 62.069 | 100
19980505090000 | 1998-05-05 09:00 | -0.026 |  | 0 | 65.483 | 54.232 | 62.417 | 54.719 |  | 162.588 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.004 | 4.0771 | 0.0002 | -0.0006 | 0.0032 | 4.0996 | 0.0036896 |  | 62.069 | 100
19980505093000 | 1998-05-05 09:30 | 0 |  | 0.089 | 64.757 | 53.594 | 61.603 | 54.323 |  | 161.671 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | 4.0933 | 0.0009 | -0.0021 | 0.0024 | 4.1173 | 0.0037056 |  | 62.069 | 100
19980505100000 | 1998-05-05 10:00 | 0 |  | 0.087 | 64.067 | 53.224 | 60.881 | 53.224 |  | 161.588 | -0.167 |  | 0.0024 | 0.0078 | 0.0047 | 0.007 | 4.0786 | 0.0009 | 0.0002 | 0.0032 | 4.1048 | 0.0036943 |  | 62.069 | 100
19980505103000 | 1998-05-05 10:30 | 0 |  | 0 | 63.51 | 52.778 | 60.129 | 53.021 |  | 163.171 | 0 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.1084 | 0.0009 | -0.0006 | 0.004 | 4.1339 | 0.0037205 |  | 62.069 | 100
19980505110000 | 1998-05-05 11:00 | 0 |  | 0.09 | 62.902 | 52.55 | 59.424 | 52.307 |  | 162.171 | -0.083 |  | 0.0047 | 0.0085 | 0.4564 | 0.0047 | 4.1353 | 0.0017 | -0.0014 | 0.0032 | 4.6131 | 0.0041518 |  | 62.069 | 100
19980505113000 | 1998-05-05 11:30 | 0 |  | 0.089 | 62.411 | 52.524 | 58.859 | 52.281 |  | 162.671 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.007 | 4.1809 | 0.0002 | -0.0006 | 0.0024 | 4.2056 | 0.003785 |  | 62.069 | 100
19980505120000 | 1998-05-05 12:00 | 0 |  | 0 | 61.96 | 52.473 | 58.19 | 51.259 |  | 162.421 | -0.25 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.3159 | 0.0009 | -0.0014 | 0.0032 | 4.3405 | 0.0039064 |  | 62.069 | 100
19980505123000 | 1998-05-05 12:30 | 0 |  | 0.087 | 61.37 | 51.912 | 57.498 | 50.697 |  | 163.921 | -0.167 |  | 0.0047 | 0.0063 | 0.004 | 0.0063 | 4.3801 | 0.0009 | 0.0017 | 0.0032 | 4.4072 | 0.0039665 |  | 62.069 | 100
19980505130000 | 1998-05-05 13:00 | 0 |  | 0 | 60.843 | 52.296 | 56.935 | 49.868 |  | 163.088 | -0.167 |  | 0.0047 | 0.0085 | 0.0032 | 0.0055 | 4.3945 | 0.0002 | 0.0009 | 0.0032 | 4.4207 | 0.0039786 |  | 62.069 | 100
19980505133000 | 1998-05-05 13:30 | -0.026 |  | 0 | 60.217 | 52.296 | 56.37 | 49.382 |  | 161.005 | -0.25 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.3862 | 0.0024 | 0.0009 | 0.0055 | 4.4163 | 0.0039747 |  | 62.069 | 100
19980505140000 | 1998-05-05 14:00 | 0 |  | 0 | 59.634 | 51.81 | 55.81 | 49.14 |  | 160.671 | -0.167 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 4.4099 | 0.0017 | -0.0006 | 0.004 | 4.4362 | 0.0039926 |  | 62.069 | 100
19980505143000 | 1998-05-05 14:30 | -0.026 |  | 0 | 58.878 | 51.593 | 55.291 | 48.922 |  | 161.921 | -0.167 |  | 0.0024 | 0.0078 | 0.0032 | 0.0055 | 4.4092 | 0.0017 | -0.0006 | 0.0063 | 4.4355 | 0.0039919 |  | 62.069 | 100
19980505150000 | 1998-05-05 15:00 | 0 |  | 0.089 | 58.174 | 50.444 | 54.89 | 48.988 |  | 161.838 | -0.167 |  | 0.0032 | 0.007 | 0.0047 | 0.0055 | 4.4006 | 0.0009 | -0.0006 | 0.004 | 4.4253 | 0.0039828 |  | 62.069 | 100
19980505153000 | 1998-05-05 15:30 | 0 |  | 0.094 | 57.325 | 48.043 | 54.489 | 48.285 |  | 160.838 | 0.083 |  | 0.0032 | 0.0063 | 0.0047 | 0.0063 | 4.3787 | 0.0002 | 0.0017 | 0.0055 | 4.4066 | 0.0039659 |  | 62.069 | 100
19980505160000 | 1998-05-05 16:00 | -0.026 |  | 0.085 | 56.311 | 47.456 | 54.002 | 47.699 |  | 159.421 | 0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.007 | 4.3647 | 0.0017 | -0.0006 | 0.0047 | 4.3917 | 0.0039525 |  | 62.069 | 100
19980505163000 | 1998-05-05 16:30 | -0.026 |  | 0.183 | 55.352 | 46.345 | 53.479 | 46.83 |  | 160.921 | -0.167 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 4.3328 | 0.0017 | -0.0014 | 0.0032 | 4.3575 | 0.0039217 |  | 62.069 | 100
19980505170000 | 1998-05-05 17:00 | 0 |  | 0.086 | 54.542 | 45.568 | 52.982 | 46.295 |  | 160.671 | -0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.0055 | 4.3091 | 0.0002 | 0.0017 | 0.0032 | 4.3339 | 0.0039005 |  | 62.069 | 100
19980505173000 | 1998-05-05 17:30 | 0 |  | 0.086 | 53.823 | 44.982 | 52.562 | 46.678 |  | 160.421 | -0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.313 | 0.0002 | -0.0006 | 0.0032 | 4.3363 | 0.0039027 |  | 62.069 | 100
19980505180000 | 1998-05-05 18:00 | -0.026 |  | 0 | 53.233 | 44.715 | 52.219 | 46.653 |  | 159.005 | 0 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.2976 | 0.0009 | -0.0006 | 0.0032 | 4.3223 | 0.0038901 |  | 62.069 | 100
19980505183000 | 1998-05-05 18:30 | -0.026 |  | 0 | 52.727 | 44.881 | 51.872 | 45.85 |  | 161.338 | -0.083 |  | 0.004 | 0.0101 | 0.0047 | 0.0063 | 4.2764 | 0.0009 | 0.0002 | 0.0032 | 4.3058 | 0.0038752 |  | 62.069 | 100
19980505190000 | 1998-05-05 19:00 | 0 |  | 0 | 52.287 | 44.155 | 51.472 | 46.577 |  | 160.255 | -0.25 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.2642 | 0.0017 | -0.0006 | 0.0017 | 4.2904 | 0.0038614 |  | 62.069 | 100
19980505193000 | 1998-05-05 19:30 | -0.026 |  | 0 | 51.945 | 43.544 | 51.202 | 45.966 |  | 159.421 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.2764 | 0.0017 | 0.0009 | 0.0032 | 4.3034 | 0.0038731 |  | 62.069 | 100
19980505200000 | 1998-05-05 20:00 | -0.026 |  | 0 | 51.484 | 43.201 | 50.841 | 46.35 |  | 158.338 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.2595 | 0.0002 | 0.0009 | 0.004 | 4.2859 | 0.0038573 |  | 62.069 | 100
19980505203000 | 1998-05-05 20:30 | 0 |  | 0 | 51.142 | 43.826 | 50.537 | 47.703 |  | 161.338 | -0.167 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.2725 | 0.0002 | -0.0006 | 0.0055 | 4.2988 | 0.0038689 |  | 62.069 | 100
19980505210000 | 1998-05-05 21:00 | -0.052 |  | 20.647 | 50.902 | 44.31 | 50.383 | 48.431 |  | 161.088 | -0.333 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2466 | 0.0009 | 0.0017 | 0.0047 | 4.2759 | 0.0038483 |  | 62.069 | 100
19980505213000 | 1998-05-05 21:30 | -0.052 |  | 0 | 50.866 | 43.14 | 50.184 | 48.956 |  | 161.338 | -0.083 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | 4.2603 | 0.0009 | 0.0017 | 0.0032 | 4.2873 | 0.0038586 |  | 62.069 | 100
19980505220000 | 1998-05-05 22:00 | -0.026 |  | 18.571 | 50.628 | 43.685 | 50.045 | 47.804 |  | 160.421 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.007 | 4.2954 | 0.0009 | -0.0006 | 0.0032 | 4.3209 | 0.0038888 |  | 62.069 | 100
19980505223000 | 1998-05-05 22:30 | 0 |  | 0 | 50.336 | 42.363 | 49.648 | 46.48 |  | 161.088 | -0.083 |  | 0.0047 | 0.0085 | 0.0032 | 0.0063 | 4.3091 | 0.0024 | 0.0009 | 0.0063 | 4.3414 | 0.0039073 |  | 62.069 | 100
19980505230000 | 1998-05-05 23:00 | -0.026 |  | 0 | 49.989 | 42.107 | 49.265 | 45.981 |  | 161.005 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.007 | 4.3069 | 0.0002 | -0.0006 | 0.0017 | 4.3317 | 0.0038985 |  | 62.069 | 100
19980505233000 | 1998-05-05 23:30 | 0 |  | 0 | 49.509 | 41.608 | 48.819 | 46.208 |  | 160.338 | 0.083 |  | 0.0024 | 0.0078 | 0.0047 | 0.0055 | 4.3152 | 0.0017 | 0.0009 | 0.0024 | 4.3406 | 0.0039065 |  | 62.069 | 100
19980506000000 | 1998-05-06 | 0 |  | 0.096 | 49.128 | 41.179 | 48.466 | 46.99 |  | 160.338 | -0.083 |  | 0.0024 | 0.0093 | 0.0032 | 0.0055 | 4.3159 | 0.0017 | -0.0006 | 0.0032 | 4.3406 | 0.0039065 |  | 62.069 | 100
19980506003000 | 1998-05-06 00:30 | 0 |  | 0.098 | 48.804 | 41.356 | 48.146 | 46.925 |  | 161.838 | -0.167 |  | 0.0032 | 0.007 | 0.004 | 0.0055 | 4.3022 | 0.0017 | -0.0006 | 0.0032 | 4.3262 | 0.0038936 |  | 62.069 | 100
19980506010000 | 1998-05-06 01:00 | 0 |  | 0.096 | 48.51 | 40.872 | 47.846 | 45.229 |  | 160.755 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.2947 | 0.0024 | 0.0002 | 0.004 | 4.324 | 0.0038916 |  | 62.069 | 100
19980506013000 | 1998-05-06 01:30 | 0 |  | 0 | 48.162 | 40.158 | 47.477 | 45.239 |  | 161.171 | -0.167 |  | 0.0047 | 0.0078 | 0.0047 | 0.0063 | 4.2717 | 0.0017 | -0.0014 | 0.004 | 4.2995 | 0.0038695 |  | 62.069 | 100
19980506020000 | 1998-05-06 02:00 | 0 |  | 0 | 47.824 | 39.599 | 47.094 | 43.71 |  | 162.588 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.2627 | 0.0017 | -0.0006 | 0.0032 | 4.2904 | 0.0038614 |  | 62.069 | 100
19980506023000 | 1998-05-06 02:30 | -0.026 |  | 0 | 46.795 | 38.124 | 46.362 | 39.815 |  | 162.338 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.2351 | 0.0002 | 0.0017 | 0.0024 | 4.2613 | 0.0038352 |  | 62.069 | 100
19980506030000 | 1998-05-06 03:00 | 0 |  | 0 | 45.68 | 38.124 | 45.592 | 40.057 |  | 163.921 | 0 |  | 0.0032 | 0.0085 | 0.0032 | 0.0055 | 4.22 | 0.0017 | 0.0002 | 0.0032 | 4.2455 | 0.0038209 |  | 62.069 | 100
19980506033000 | 1998-05-06 03:30 | 0 |  | 0 | 44.989 | 37.883 | 45.132 | 39.574 |  | 163.921 | -0.083 |  | 0.0024 | 0.007 | 0.0032 | 0.0055 | 4.2161 | 0.0009 | -0.0006 | 0.0024 | 4.2369 | 0.0038132 |  | 62.069 | 100
19980506040000 | 1998-05-06 04:00 | 0 |  | 0 | 44.572 | 37.908 | 44.81 | 39.841 |  | 163.921 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.2007 | 0.0009 | 0.0002 | 0.0032 | 4.2284 | 0.0038056 |  | 62.069 | 100
19980506043000 | 1998-05-06 04:30 | 0 |  | 0 | 44.255 | 37.451 | 44.536 | 39.866 |  | 164.255 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1885 | 0.0009 | -0.0014 | 0.0032 | 4.2132 | 0.0037919 |  | 62.069 | 100
19980506050000 | 1998-05-06 05:00 | 0 |  | 0 | 43.918 | 37.094 | 44.256 | 39.025 |  | 164.338 | -0.167 |  | 0.004 | 0.0101 | 0.0032 | 0.0047 | 4.1963 | 0.0009 | -0.0014 | 0.004 | 4.2218 | 0.0037996 |  | 62.069 | 100
19980506053000 | 1998-05-06 05:30 | -0.026 |  | 0 | 43.746 | 37.234 | 44.047 | 39.166 |  | 165.088 | -0.25 |  | 0.0047 | 0.0078 | 0.004 | 0.0063 | 4.1794 | 0.0009 | 0.0002 | 0.0024 | 4.2057 | 0.0037851 |  | 62.069 | 100
19980506060000 | 1998-05-06 06:00 | 0 |  | 0 | 43.747 | 37.375 | 44.046 | 39.79 |  | 167.005 | -0.083 |  | 0.004 | 0.0101 | 0.0047 | 0.0063 | 4.168 | 0.0002 | -0.0006 | 0.0032 | 4.1959 | 0.0037763 |  | 62.069 | 100
19980506063000 | 1998-05-06 06:30 | -0.026 |  | 0 | 43.746 | 37.476 | 43.98 | 39.891 |  | 169.172 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.007 | 4.1414 | 0.0017 | -0.0006 | 0.0063 | 4.1715 | 0.0037543 |  | 62.069 | 100
19980506070000 | 1998-05-06 07:00 | 0 |  | 0 | 43.746 | 37.984 | 43.789 | 40.4 |  | 170.672 | 0 |  | 0.0032 | 0.0085 | 0.0055 | 0.007 | 4.1238 | 0.0009 | -0.0006 | 0.0032 | 4.1515 | 0.0037363 |  | 62.069 | 100
19980506073000 | 1998-05-06 07:30 | 0 |  | 0.096 | 43.746 | 38.085 | 43.788 | 40.5 |  | 171.755 | 0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.1047 | 0.0017 | 0.0002 | 0.0047 | 4.1326 | 0.0037193 |  | 62.069 | 100
19980506080000 | 1998-05-06 08:00 | 0 |  | 0.097 | 43.985 | 38.784 | 43.635 | 41.442 |  | 174.588 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.0908 | 0.0009 | -0.0006 | 0.0032 | 4.1148 | 0.0037033 |  | 62.069 | 100
19980506083000 | 1998-05-06 08:30 | 0.026 |  | 0.095 | 44.235 | 39.292 | 43.566 | 43.403 |  | 177.588 | 0 |  | 0.004 | 0.0078 | 0.0047 | 0.0055 | 4.0613 | 0.0009 | -0.0006 | 0.004 | 4.0876 | 0.0036788 |  | 62.069 | 100
19980506090000 | 1998-05-06 09:00 | -0.026 |  | 0.097 | 44.54 | 40.591 | 43.779 | 44.22 |  | 177.672 | -0.083 |  | 0.004 | 0.0085 | 0.0047 | 0.0063 | 4.0132 | 0.0017 | -0.0021 | 0.004 | 4.0403 | 0.0036363 |  | 62.069 | 100
19980506093000 | 1998-05-06 09:30 | 0 |  | 0.096 | 44.758 | 41.392 | 43.787 | 44.538 |  | 179.422 | -0.167 |  | 0.0032 | 0.007 | 0.0032 | 0.0063 | 3.9956 | 0.0002 | -0.0006 | 0.0032 | 4.0181 | 0.0036163 |  | 62.069 | 100
19980506100000 | 1998-05-06 10:00 | -0.026 |  | 0.095 | 44.934 | 39.177 | 43.776 | 43.045 |  | 178.422 | -0.083 |  | 0.0032 | 0.0085 | 0.0024 | 0.0055 | 4.0222 | 0.0017 | -0.0006 | 0.0024 | 4.0453 | 0.0036408 |  | 62.069 | 100
19980506103000 | 1998-05-06 10:30 | 0 |  | 0.098 | 44.588 | 39.469 | 43.554 | 43.822 |  | 182.339 | 0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.0247 | 0.0009 | -0.0006 | 0.0032 | 4.0501 | 0.0036451 |  | 62.069 | 100
19980506110000 | 1998-05-06 11:00 | -0.026 |  | 0.093 | 44.333 | 39.736 | 43.327 | 43.605 |  | 181.839 | -0.167 |  | 0.0032 | 0.0093 | 0.0047 | 0.007 | 4.0168 | 0.0017 | -0.0014 | 0.0032 | 4.0445 | 0.00364 |  | 62.069 | 100
19980506113000 | 1998-05-06 11:30 | 0 |  | 0.097 | 44.23 | 39.393 | 43.215 | 43.504 |  | 179.839 | 0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 3.9872 | 0.0009 | -0.0006 | 0.0017 | 4.0119 | 0.0036107 |  | 62.069 | 100
19980506120000 | 1998-05-06 12:00 | 0 |  | 0.309 | 43.87 | 39.534 | 42.939 | 43.403 |  | 178.255 | 0 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 3.9888 | 0.0017 | -0.0021 | 0.004 | 4.0129 | 0.0036116 |  | 62.069 | 100
19980506123000 | 1998-05-06 12:30 | -0.052 |  | 20.744 | 43.571 | 37.994 | 42.618 | 40.41 |  | 177.005 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 3.9841 | 0.0002 | -0.0006 | 0.0032 | 4.0081 | 0.0036073 |  | 62.069 | 100
19980506130000 | 1998-05-06 13:00 | 0.026 |  | 0.221 | 42.924 | 36.737 | 42.019 | 37.944 |  | 175.338 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0047 | 4.0107 | 0.0009 | -0.0021 | 0.0024 | 4.0323 | 0.0036291 |  | 62.069 | 100
19980506133000 | 1998-05-06 13:30 | 0 |  | 0.34 | 42.094 | 35.405 | 41.338 | 37.335 |  | 172.338 | -0.167 |  | 0.0047 | 0.0085 | 0.0047 | 0.0063 | 4.0261 | 0.0009 | -0.0014 | 0.0032 | 4.053 | 0.0036477 |  | 62.069 | 100
19980506140000 | 1998-05-06 14:00 | 0 |  | 0.098 | 41.322 | 35.164 | 40.707 | 36.852 |  | 173.255 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.0055 | 4.0535 | 0.0009 | -0.0006 | 0.0032 | 4.079 | 0.0036711 |  | 62.069 | 100
19980506143000 | 1998-05-06 14:30 | -0.026 |  | 0.096 | 40.739 | 34.657 | 40.274 | 36.345 |  | 173.672 | -0.083 |  | 0.0047 | 0.0101 | 0.0032 | 0.0055 | 4.0444 | 0.0017 | -0.0006 | 0.004 | 4.073 | 0.0036657 |  | 62.069 | 100
19980506150000 | 1998-05-06 15:00 | 0 |  | 0.098 | 40.206 | 34.757 | 39.847 | 35.963 |  | 173.588 | -0.167 |  | 0.0032 | 0.0093 | 0.0032 | 0.0047 | 4.0933 | 0.0002 | -0.0014 | 0.0047 | 4.1172 | 0.0037055 |  | 62.069 | 100
19980506153000 | 1998-05-06 15:30 | -0.026 |  | 0 | 39.708 | 34.275 | 39.498 | 36.204 |  | 171.672 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.004 | 4.1238 | 0.0009 | -0.0006 | 0.0032 | 4.147 | 0.0037323 |  | 62.069 | 100
19980506160000 | 1998-05-06 16:00 | -0.026 |  | 0 | 39.461 | 34.692 | 39.248 | 35.657 |  | 171.505 | 0 |  | 0.0032 | 0.0093 | 0.0047 | 0.0055 | 4.1238 | 0.0017 | -0.0006 | 0.0032 | 4.1508 | 0.0037357 |  | 62.069 | 100
19980506163000 | 1998-05-06 16:30 | -0.026 |  | 0 | 39.231 | 33.844 | 38.998 | 35.531 |  | 173.255 | -0.083 |  | 0.0047 | 0.0078 | 0.004 | 0.0055 | 4.1177 | 0.0017 | -0.0006 | 0.0032 | 4.144 | 0.0037296 |  | 62.069 | 100
19980506170000 | 1998-05-06 17:00 | -0.026 |  | 0 | 39.04 | 34.642 | 38.743 | 36.089 |  | 170.338 | -0.25 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.1123 | 0.0002 | 0.0002 | 0.0017 | 4.1363 | 0.0037227 |  | 62.069 | 100
19980506173000 | 1998-05-06 17:30 | -0.026 |  | 0 | 38.953 | 34.16 | 38.577 | 35.606 |  | 172.755 | -0.25 |  | 0.0024 | 0.007 | 0.004 | 0.0063 | 4.0947 | 0.0009 | -0.0006 | 0.0032 | 4.1179 | 0.0037061 |  | 62.069 | 100
19980506180000 | 1998-05-06 18:00 | 0 |  | 0.097 | 38.863 | 34.275 | 38.425 | 35.963 |  | 171.172 | -0.25 |  | 0.0024 | 0.0078 | 0.0024 | 0.0055 | 4.0718 | 0.0009 | -0.0006 | 0.004 | 4.0942 | 0.0036848 |  | 62.069 | 100
19980506183000 | 1998-05-06 18:30 | -0.026 |  | 0 | 38.674 | 33.818 | 38.188 | 35.024 |  | 170.672 | -0.083 |  | 0.004 | 0.0085 | 0.004 | 0.0055 | 4.0742 | 0.0009 | -0.0006 | 0.0032 | 4.0997 | 0.0036897 |  | 62.069 | 100
19980506190000 | 1998-05-06 19:00 | -0.026 |  | 0.096 | 38.442 | 33.552 | 37.923 | 34.516 |  | 171.505 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.007 | 4.0718 | 0.0009 | -0.0006 | 0.0017 | 4.0965 | 0.0036868 |  | 62.069 | 100
19980506193000 | 1998-05-06 19:30 | 0 |  | 0 | 37.954 | 32.689 | 37.607 | 34.135 |  | 168.255 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.0986 | 0.0009 | -0.0006 | 0.0032 | 4.1234 | 0.0037111 |  | 62.069 | 100
19980506200000 | 1998-05-06 20:00 | -0.026 |  | 0 | 37.443 | 31.917 | 37.269 | 33.362 |  | 168.421 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.1152 | 0.0009 | -0.0006 | 0.0032 | 4.14 | 0.003726 |  | 62.069 | 100
19980506203000 | 1998-05-06 20:30 | 0 |  | 0 | 36.904 | 31.676 | 36.878 | 32.88 |  | 171.922 | 0 |  | 0.004 | 0.0085 | 0.004 | 0.0055 | 4.1528 | 0.0017 | 0.0002 | 0.0024 | 4.1791 | 0.0037612 |  | 62.069 | 100
19980506210000 | 1998-05-06 21:00 | 0 |  | 0 | 36.613 | 31.752 | 36.598 | 32.955 |  | 168.088 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.165 | 0.0017 | -0.0006 | 0.0032 | 4.1898 | 0.0037708 |  | 62.069 | 100
19980506213000 | 1998-05-06 21:30 | -0.026 |  | 0.09 | 36.148 | 30.979 | 36.249 | 32.905 |  | 168.672 | -0.25 |  | 0.0032 | 0.0078 | 0.0047 | 0.0047 | 4.2017 | 0.0009 | -0.0006 | 0.0032 | 4.2256 | 0.003803 |  | 62.069 | 100
19980506220000 | 1998-05-06 22:00 | -0.052 |  | 0.09 | 35.72 | 30.739 | 35.932 | 32.664 |  | 168.505 | -0.25 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | 4.197 | 0.0009 | -0.0006 | 0.004 | 4.2225 | 0.0038002 |  | 62.069 | 100
19980506223000 | 1998-05-06 22:30 | 0 |  | 0 | 35.467 | 30.764 | 35.656 | 31.967 |  | 170.505 | -0.083 |  | 0.0024 | 0.007 | 0.0055 | 0.0055 | 4.2039 | 0.0002 | -0.0006 | 0.0032 | 4.2271 | 0.0038044 |  | 62.069 | 100
19980506230000 | 1998-05-06 23:00 | 0 |  | 0 | 35.279 | 31.005 | 35.436 | 32.208 |  | 169.422 | -0.25 |  | 0.004 | 0.0078 | 0.004 | 0.0063 | 4.2183 | 0.0009 | -0.0006 | 0.0032 | 4.2439 | 0.0038195 |  | 62.069 | 100
19980506233000 | 1998-05-06 23:30 | 0 |  | 0 | 35.187 | 30.689 | 35.259 | 32.133 |  | 170.838 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.2505 | 0.0017 | -0.0006 | 0.004 | 4.2768 | 0.0038491 |  | 62.069 | 100
19980507000000 | 1998-05-07 | 0 |  | 0 | 35.024 | 29.867 | 35.031 | 31.069 |  | 170.255 | -0.167 |  | 0.0024 | 0.0078 | 0.0047 | 0.007 | 4.2412 | 0.0009 | 0.0009 | 0.0047 | 4.2696 | 0.0038426 |  | 62.069 | 100
19980507003000 | 1998-05-07 00:30 | 0 |  | 0 | 34.833 | 30.513 | 34.839 | 31.716 |  | 171.422 | -0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.2466 | 0.0009 | -0.0006 | 0.004 | 4.2714 | 0.0038443 |  | 62.069 | 100
19980507010000 | 1998-05-07 01:00 | 0 |  | 0 | 34.66 | 29.917 | 34.654 | 31.12 |  | 170.838 | -0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.2458 | 0.0002 | -0.0006 | 0.0047 | 4.2721 | 0.0038449 |  | 62.069 | 100
19980507013000 | 1998-05-07 01:30 | 0 |  | 0 | 34.404 | 29.536 | 34.432 | 30.739 |  | 169.755 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.252 | 0.0009 | -0.0006 | 0.0032 | 4.2789 | 0.003851 |  | 62.069 | 100
19980507020000 | 1998-05-07 02:00 | 0 |  | 0 | 34.051 | 29.346 | 34.154 | 30.789 |  | 168.588 | -0.083 |  | 0.0032 | 0.0093 | 0.004 | 0.0055 | 4.2505 | 0.0017 | -0.0006 | 0.004 | 4.2776 | 0.0038498 |  | 62.069 | 100
19980507023000 | 1998-05-07 02:30 | 0 |  | 0 | 33.743 | 29.221 | 33.923 | 30.663 |  | 170.922 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2512 | 0.0009 | -0.0021 | 0.0017 | 4.2737 | 0.0038463 |  | 62.069 | 100
19980507030000 | 1998-05-07 03:00 | 0.026 |  | 20.53 | 33.473 | 28.74 | 33.664 | 29.942 |  | 169.422 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.2542 | 0.0009 | 0.0002 | 0.0024 | 4.2774 | 0.0038497 |  | 62.069 | 100
19980507033000 | 1998-05-07 03:30 | 0 |  | 0 | 33.028 | 28.109 | 33.401 | 29.551 |  | 170.255 | -0.083 |  | 0.0047 | 0.0085 | 0.004 | 0.0055 | 4.2458 | 0.0009 | -0.0006 | 0.0047 | 4.2735 | 0.0038461 |  | 62.069 | 100
19980507040000 | 1998-05-07 04:00 | 0 |  | 15.763 | 32.735 | 28.069 | 33.098 | 29.03 |  | 169.172 | 0 |  | 0.0032 | 0.0078 | 0.0032 | 0.0047 | 4.2412 | 0.0002 | -0.0014 | 0.0032 | 4.2621 | 0.0038359 |  | 62.069 | 100
19980507043000 | 1998-05-07 04:30 | 0 |  | 0.097 | 32.369 | 27.464 | 32.818 | 29.386 |  | 169.505 | -0.083 |  | 0.0047 | 0.007 | 0.0063 | 0.0063 | 4.2275 | 0.0009 | -0.0006 | 0.0032 | 4.2553 | 0.0038298 |  | 62.069 | 100
19980507050000 | 1998-05-07 05:00 | -0.026 |  | 0.096 | 32.029 | 27.714 | 32.591 | 29.156 |  | 170.338 | -0.25 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.2007 | 0.0002 | -0.0006 | 0.004 | 4.2248 | 0.0038023 |  | 62.069 | 100
19980507053000 | 1998-05-07 05:30 | 0 |  | 0.096 | 31.746 | 27.234 | 32.388 | 28.916 |  | 169.838 | 0 |  | 0.0024 | 0.007 | 0.004 | 0.0055 | 4.1909 | 0.0002 | -0.0006 | 0.0032 | 4.2126 | 0.0037913 |  | 62.069 | 100
19980507060000 | 1998-05-07 06:00 | 0 |  | 0.097 | 31.525 | 27.134 | 32.108 | 28.815 |  | 168.338 | -0.25 |  | 0.0047 | 0.0063 | 0.004 | 0.0063 | 4.1848 | 0.0024 | 0.0009 | 0.0032 | 4.2126 | 0.0037913 |  | 62.069 | 100
19980507063000 | 1998-05-07 06:30 | -0.026 |  | 0.097 | 31.377 | 26.944 | 31.962 | 29.346 |  | 170.088 | -0.25 |  | 0.004 | 0.007 | 0.0047 | 0.007 | 4.1963 | 0.0009 | -0.0006 | 0.0024 | 4.2217 | 0.0037995 |  | 62.069 | 100
19980507070000 | 1998-05-07 07:00 | 0 |  | 0.098 | 31.191 | 27.184 | 31.859 | 28.385 |  | 169.338 | -0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.1833 | 0.0009 | -0.0006 | 0.004 | 4.2081 | 0.0037873 |  | 62.069 | 100
19980507073000 | 1998-05-07 07:30 | 0 |  | 0.094 | 31.174 | 27.033 | 31.65 | 28.715 |  | 169.422 | -0.083 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | 4.1763 | 0.0009 | -0.0014 | 0.0017 | 4.1987 | 0.0037788 |  | 62.069 | 100
19980507080000 | 1998-05-07 08:00 | -0.026 |  | 0.097 | 31.172 | 27.234 | 31.612 | 28.675 |  | 169.672 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.0055 | 4.1794 | 0.0009 | -0.0006 | 0.0085 | 4.2102 | 0.0037892 |  | 62.069 | 100
19980507083000 | 1998-05-07 08:30 | 0 |  | 0 | 31.173 | 27.664 | 31.611 | 28.865 |  | 170.172 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.168 | 0.0017 | 0.0002 | 0.004 | 4.1944 | 0.003775 |  | 62.069 | 100
19980507090000 | 1998-05-07 09:00 | -0.079 |  | 0 | 31.174 | 27.299 | 31.529 | 28.74 |  | 169.505 | -0.083 |  | 0.004 | 0.007 | 0.0047 | 0.007 | 4.1802 | 0.0002 | 0.0009 | 0.004 | 4.208 | 0.0037872 |  | 62.069 | 100
19980507093000 | 1998-05-07 09:30 | -0.026 |  | 0 | 31.099 | 27.184 | 31.378 | 28.625 |  | 169.088 | -0.25 |  | 0.0024 | 0.0093 | 0.0032 | 0.007 | 4.1809 | 0.0002 | 0.0002 | 0.0032 | 4.2064 | 0.0037858 |  | 62.069 | 100
19980507100000 | 1998-05-07 10:00 | 0 |  | 0 | 30.954 | 27.184 | 31.375 | 28.145 |  | 167.505 | 0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0085 | 4.2007 | 0.0002 | -0.0014 | 0.0024 | 4.2253 | 0.0038028 |  | 62.069 | 100
19980507103000 | 1998-05-07 10:30 | -0.026 |  | 0 | 30.817 | 27.134 | 31.133 | 28.335 |  | 169.422 | -0.083 |  | 0.004 | 0.007 | 0.004 | 0.0063 | 4.1931 | 0.0009 | -0.0006 | 0.0024 | 4.2171 | 0.0037954 |  | 62.069 | 100
19980507110000 | 1998-05-07 11:00 | 0 |  | 0 | 30.721 | 27.159 | 31.132 | 28.36 |  | 169.338 | -0.25 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.21 | 0.0009 | 0.0002 | 0.0024 | 4.2355 | 0.0038119 |  | 62.069 | 100
19980507113000 | 1998-05-07 11:30 | -0.026 |  | 0.098 | 30.791 | 27.209 | 31.133 | 28.65 |  | 169.505 | -0.25 |  | 0.0032 | 0.0085 | 0.004 | 0.0055 | 4.2007 | 0.0009 | -0.0006 | 0.0032 | 4.2254 | 0.0038029 |  | 62.069 | 100
19980507120000 | 1998-05-07 12:00 | 0 |  | 0 | 30.956 | 27.664 | 31.132 | 29.106 |  | 169.838 | -0.083 |  | 0.004 | 0.0078 | 0.004 | 0.0047 | 4.1985 | 0.0024 | -0.0006 | 0.0032 | 4.224 | 0.0038016 |  | 62.069 | 100
19980507123000 | 1998-05-07 12:30 | -0.026 |  | 0 | 31.182 | 32.664 | 31.346 | 33.387 |  | 164.921 | -0.083 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.187 | 0.0017 | -0.0006 | 0.0024 | 4.2117 | 0.0037905 |  | 62.069 | 100
19980507130000 | 1998-05-07 13:00 | -0.026 |  | 0 | 32.657 | 33.261 | 32.473 | 34.225 |  | 164.088 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1604 | 0.0024 | -0.0014 | 0.0024 | 4.1858 | 0.0037672 |  | 62.069 | 100
19980507133000 | 1998-05-07 13:30 | -0.026 |  | 0 | 33.744 | 33.487 | 33.662 | 34.451 |  | 164.755 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.1252 | 0.0009 | -0.0006 | 0.0047 | 4.1521 | 0.0037369 |  | 62.069 | 100
19980507140000 | 1998-05-07 14:00 | 0.026 |  | 0 | 34.292 | 33.829 | 34.385 | 34.552 |  | 163.755 | -0.083 |  | 0.0032 | 0.007 | 0.0032 | 0.007 | 4.0986 | 0.0009 | -0.0006 | 0.0032 | 4.1225 | 0.0037102 |  | 62.069 | 100
19980507143000 | 1998-05-07 14:30 | 0.026 |  | 0 | 34.58 | 33.412 | 34.745 | 33.894 |  | 163.005 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.0735 | 0.0009 | 0.0002 | 0.0032 | 4.0991 | 0.0036892 |  | 62.069 | 100
19980507150000 | 1998-05-07 15:00 | -0.026 |  | 0 | 34.722 | 33.668 | 34.787 | 34.149 |  | 161.671 | -0.167 |  | 0.0032 | 0.007 | 0.0047 | 0.0047 | 4.0559 | 0.0009 | -0.0014 | 0.0032 | 4.0782 | 0.0036704 |  | 62.069 | 100
19980507153000 | 1998-05-07 15:30 | 0 |  | 0 | 34.951 | 33.552 | 34.787 | 34.034 |  | 162.421 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.0444 | 0.0002 | -0.0006 | 0.0032 | 4.0699 | 0.0036629 |  | 62.069 | 100
19980507160000 | 1998-05-07 16:00 | -0.026 |  | 0 | 35.156 | 34.225 | 34.974 | 34.225 |  | 160.838 | -0.083 |  | 0.004 | 0.0085 | 0.0047 | 0.0055 | 4.0674 | 0.0009 | -0.0006 | 0.004 | 4.0944 | 0.003685 |  | 62.069 | 100
19980507163000 | 1998-05-07 16:30 | -0.026 |  | 0 | 35.4 | 35.049 | 35.025 | 34.567 |  | 162.005 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.071 | 0.0002 | -0.0006 | 0.0032 | 4.095 | 0.0036855 |  | 62.069 | 100
19980507170000 | 1998-05-07 17:00 | -0.026 |  | 0 | 35.707 | 34.883 | 35.265 | 34.16 |  | 160.171 | -0.25 |  | 0.0032 | 0.007 | 0.004 | 0.0063 | 4.0757 | 0.0017 | -0.0006 | 0.0032 | 4.1005 | 0.0036904 |  | 62.069 | 100
19980507173000 | 1998-05-07 17:30 | 0 |  | 20.623 | 36.096 | 35.873 | 35.387 | 34.426 |  | 160.921 | -0.167 |  | 0.004 | 0.007 | 0.0047 | 0.0063 | 4.0513 | 0.0009 | -0.0006 | 0.004 | 4.0776 | 0.0036698 |  | 62.069 | 100
19980507180000 | 1998-05-07 18:00 | 0 |  | 0.099 | 36.523 | 35.963 | 35.59 | 34.757 |  | 160.338 | -0.25 |  | 0.0032 | 0.007 | 0.0032 | 0.0047 | 4.0513 | 0.0017 | -0.0006 | 0.004 | 4.0745 | 0.003667 |  | 62.069 | 100
19980507183000 | 1998-05-07 18:30 | -0.026 |  | 15.522 | 36.93 | 36.445 | 35.759 | 35.481 |  | 161.505 | -0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.0308 | 0.0009 | -0.0006 | 0.0032 | 4.0548 | 0.0036493 |  | 62.069 | 100
19980507190000 | 1998-05-07 19:00 | 0 |  | 0 | 37.402 | 37.195 | 35.98 | 35.265 |  | 160.171 | 0.083 |  | 0.0032 | 0.0093 | 0.0032 | 0.0063 | 4.0237 | 0.0024 | -0.0029 | 0.0032 | 4.0484 | 0.0036436 |  | 62.069 | 100
19980507193000 | 1998-05-07 19:30 | 0 |  | 0 | 37.732 | 37.396 | 36.32 | 36.672 |  | 159.421 | -0.25 |  | 0.0055 | 0.0078 | 0.0047 | 0.007 | 4.0254 | 0.0002 | -0.0006 | 0.0063 | 4.0563 | 0.0036507 |  | 62.069 | 100
19980507200000 | 1998-05-07 20:00 | 0 |  | 0 | 37.991 | 37.537 | 36.872 | 36.33 |  | 158.921 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.0269 | 0.0017 | -0.0006 | 0.0032 | 4.0546 | 0.0036491 |  | 62.069 | 100
19980507203000 | 1998-05-07 20:30 | -0.026 |  | 0 | 38.287 | 37.512 | 37.147 | 36.064 |  | 159.505 | 0 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.0291 | 0.0009 | -0.0006 | 0.0032 | 4.0546 | 0.0036491 |  | 62.069 | 100
19980507210000 | 1998-05-07 21:00 | -0.026 |  | 0 | 38.485 | 37.652 | 37.023 | 35.722 |  | 160.005 | -0.083 |  | 0.0024 | 0.0085 | 0.004 | 0.0047 | 4.033 | 0.0009 | -0.0014 | 0.0024 | 4.0545 | 0.003649 |  | 62.069 | 100
19980507213000 | 1998-05-07 21:30 | -0.026 |  | 0 | 38.623 | 37.753 | 36.753 | 34.617 |  | 157.921 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.033 | 0.0017 | -0.0006 | 0.004 | 4.0593 | 0.0036534 |  | 62.069 | 100
19980507220000 | 1998-05-07 22:00 | -0.052 |  | 0 | 38.642 | 37.637 | 36.245 | 34.261 |  | 158.838 | -0.167 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.0444 | 0.0009 | -0.0014 | 0.0047 | 4.0713 | 0.0036642 |  | 62.069 | 100
19980507223000 | 1998-05-07 22:30 | 0.026 |  | 0 | 38.58 | 37.562 | 35.595 | 33.221 |  | 160.505 | -0.333 |  | 0.0032 | 0.0085 | 0.004 | 0.0055 | 4.0376 | 0.0017 | -0.0006 | 0.0032 | 4.0631 | 0.0036568 |  | 62.069 | 100
19980507230000 | 1998-05-07 23:00 | 0 |  | 0 | 38.482 | 37.22 | 34.917 | 32.639 |  | 159.421 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.0444 | 0.0017 | -0.0006 | 0.0032 | 4.0692 | 0.0036623 |  | 62.069 | 100
19980507233000 | 1998-05-07 23:30 | 0.026 |  | 0 | 38.29 | 37.562 | 34.262 | 32.258 |  | 158.588 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.007 | 4.0603 | 0.0009 | -0.0006 | 0.0032 | 4.0857 | 0.0036771 |  | 62.069 | 100
19980508000000 | 1998-05-08 | -0.026 |  | 0 | 38.294 | 37.295 | 33.658 | 31.511 |  | 158.171 | 0 |  | 0.004 | 0.0085 | 0.0032 | 0.0055 | 4.0405 | 0.0009 | -0.0014 | 0.0032 | 4.0644 | 0.003658 |  | 62.069 | 100
19980508003000 | 1998-05-08 00:30 | 0 |  | 0 | 38.293 | 37.22 | 33.159 | 31.195 |  | 159.588 | 0 |  | 0.0032 | 0.0085 | 0.0032 | 0.0047 | 4.0247 | 0.0002 | -0.0006 | 0.0032 | 4.0471 | 0.0036424 |  | 62.069 | 100
19980508010000 | 1998-05-08 01:00 | -0.026 |  | 0.099 | 38.293 | 37.155 | 32.721 | 31.13 |  | 158.588 | 0 |  | 0.0047 | 0.0078 | 0.0047 | 0.007 | 4.0186 | 0.0002 | -0.0006 | 0.004 | 4.0464 | 0.0036418 |  | 62.069 | 100
19980508013000 | 1998-05-08 01:30 | -0.026 |  | 0.1 | 38.118 | 36.471 | 32.385 | 30.448 |  | 158.338 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.033 | 0.0009 | -0.0014 | 0.004 | 4.0584 | 0.0036526 |  | 62.069 | 100
19980508020000 | 1998-05-08 02:00 | 0 |  | 0.099 | 37.877 | 37.13 | 32.075 | 30.624 |  | 158.005 | 0 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.071 | 0.0017 | 0.0002 | 0.0032 | 4.0981 | 0.0036883 |  | 62.069 | 100
19980508023000 | 1998-05-08 02:30 | 0 |  | 0.098 | 37.74 | 36.813 | 31.866 | 30.789 |  | 158.005 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.0725 | 0.0009 | -0.0006 | 0.004 | 4.0981 | 0.0036883 |  | 62.069 | 100
19980508030000 | 1998-05-08 03:00 | 0 |  | 0 | 37.611 | 36.496 | 31.631 | 30.473 |  | 158.171 | 0.167 |  | 0.0047 | 0.0093 | 0.0047 | 0.0055 | 4.0725 | 0.0009 | -0.0006 | 0.0017 | 4.0987 | 0.0036888 |  | 62.069 | 100
19980508033000 | 1998-05-08 03:30 | -0.052 |  | 0 | 37.466 | 36.305 | 31.519 | 30.283 |  | 158.005 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.0847 | 0.0017 | -0.0021 | 0.0017 | 4.1065 | 0.0036958 |  | 62.069 | 100
19980508040000 | 1998-05-08 04:00 | 0 |  | 0 | 37.292 | 36.471 | 31.387 | 29.967 |  | 157.921 | -0.083 |  | 0.004 | 0.0085 | 0.0024 | 0.004 | 4.1199 | 0.0017 | -0.0006 | 0.0017 | 4.1416 | 0.0037274 |  | 62.069 | 100
19980508043000 | 1998-05-08 04:30 | 0.026 |  | 0 | 37.292 | 36.064 | 31.256 | 29.802 |  | 157.921 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0055 | 4.1321 | 0.0002 | -0.0006 | 0.0017 | 4.1538 | 0.0037384 |  | 62.069 | 100
19980508050000 | 1998-05-08 05:00 | 0 |  | 0 | 37.1 | 35.747 | 31.139 | 29.486 |  | 157.921 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.1382 | 0.0002 | -0.0014 | 0.0032 | 4.1607 | 0.0037446 |  | 62.069 | 100
19980508053000 | 1998-05-08 05:30 | 0 |  | 0 | 36.946 | 36.19 | 31.033 | 29.927 |  | 157.505 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.1458 | 0.0009 | -0.0006 | 0.0032 | 4.1727 | 0.0037554 |  | 62.069 | 100
19980508060000 | 1998-05-08 06:00 | 0 |  | 0 | 36.946 | 35.873 | 30.9 | 29.612 |  | 157.838 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1345 | 0.0009 | 0.0002 | 0.0024 | 4.16 | 0.003744 |  | 62.069 | 100
19980508063000 | 1998-05-08 06:30 | 0 |  | 0 | 36.864 | 35.822 | 30.9 | 29.561 |  | 159.338 | -0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.1389 | 0.0009 | -0.0014 | 0.004 | 4.1644 | 0.003748 |  | 62.069 | 100
19980508070000 | 1998-05-08 07:00 | -0.052 |  | 0 | 36.729 | 35.315 | 30.729 | 29.536 |  | 157.921 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1306 | 0.0009 | -0.0006 | 0.0047 | 4.1576 | 0.0037418 |  | 62.069 | 100
19980508073000 | 1998-05-08 07:30 | -0.026 |  | 0 | 36.729 | 35.632 | 30.65 | 29.371 |  | 157.171 | -0.083 |  | 0.0032 | 0.0101 | 0.0047 | 0.0063 | 4.1191 | 0.0009 | 0.0009 | 0.0032 | 4.1484 | 0.0037336 |  | 62.069 | 100
19980508080000 | 1998-05-08 08:00 | 0 |  | 20.529 | 36.515 | 34.743 | 30.552 | 28.725 |  | 156.838 | -0.25 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.1284 | 0.0009 | -0.0014 | 0.0032 | 4.1538 | 0.0037384 |  | 62.069 | 100
19980508083000 | 1998-05-08 08:30 | 0 |  | 0.091 | 36.011 | 33.919 | 29.892 | 28.385 |  | 156.588 | 0 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.126 | 0.0009 | -0.0014 | 0.0032 | 4.1499 | 0.0037349 |  | 62.069 | 100
19980508090000 | 1998-05-08 09:00 | -0.026 |  | 20.889 | 35.479 | 33.412 | 29.386 | 27.639 |  | 156.004 | -0.25 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.1274 | 0.0009 | -0.0006 | 0.004 | 4.1537 | 0.0037383 |  | 62.069 | 100
19980508093000 | 1998-05-08 09:30 | -0.026 |  | 0 | 35.105 | 32.905 | 29.094 | 27.374 |  | 154.671 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.007 | 4.1396 | 0.0002 | 0.0002 | 0.004 | 4.1667 | 0.00375 |  | 62.069 | 100
19980508100000 | 1998-05-08 10:00 | -0.026 |  | 0.091 | 34.771 | 32.715 | 28.85 | 27.184 |  | 154.588 | -0.167 |  | 0.0032 | 0.0078 | 0.0024 | 0.0078 | 4.1345 | 0.0002 | -0.0014 | 0.0032 | 4.1577 | 0.0037419 |  | 62.069 | 100
19980508103000 | 1998-05-08 10:30 | -0.026 |  | 0.09 | 34.382 | 32.258 | 28.495 | 27.209 |  | 154.421 | -0.333 |  | 0.0032 | 0.0085 | 0.004 | 0.007 | 4.1345 | 0.0002 | -0.0006 | 0.0032 | 4.16 | 0.003744 |  | 62.069 | 100
19980508110000 | 1998-05-08 11:00 | -0.026 |  | 0.092 | 33.943 | 32.981 | 28.465 | 27.209 |  | 153.254 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.1389 | 0.0017 | -0.0006 | 0.0032 | 4.1652 | 0.0037487 |  | 62.069 | 100
19980508113000 | 1998-05-08 11:30 | -0.026 |  | 0.091 | 33.845 | 33.513 | 28.217 | 27.979 |  | 152.338 | 0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | 4.1421 | 0.0017 | -0.0006 | 0.0032 | 4.1668 | 0.0037501 |  | 62.069 | 100
19980508120000 | 1998-05-08 12:00 | 0 |  | 0 | 34.214 | 33.768 | 28.531 | 27.754 |  | 147.754 | -0.167 |  | 0.0024 | 0.0085 | 0.004 | 0.0047 | 4.1565 | 0.0009 | -0.0006 | 0.0032 | 4.1796 | 0.0037616 |  | 62.069 | 100
19980508123000 | 1998-05-08 12:30 | 0.026 |  | 0 | 34.544 | 34.095 | 28.862 | 28.08 |  | 151.671 | -0.083 |  | 0.0055 | 0.0078 | 0.004 | 0.0063 | 4.1802 | 0.0009 | -0.0014 | 0.0032 | 4.2065 | 0.0037858 |  | 62.069 | 100
19980508130000 | 1998-05-08 13:00 | -0.026 |  | 0 | 34.742 | 33.969 | 29.101 | 28.435 |  | 147.254 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2024 | 0.0009 | -0.0014 | 0.0032 | 4.2271 | 0.0038044 |  | 62.069 | 100
19980508133000 | 1998-05-08 13:30 | -0.026 |  | 0 | 34.881 | 34.491 | 29.312 | 27.754 |  | 147.588 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.007 | 4.2297 | 0.0017 | -0.0006 | 0.0024 | 4.2552 | 0.0038297 |  | 62.069 | 100
19980508140000 | 1998-05-08 14:00 | 0.026 |  | 0.095 | 35.09 | 35.441 | 29.512 | 28.46 |  | 145.338 | 0 |  | 0.0047 | 0.0085 | 0.0032 | 0.0063 | 4.2214 | 0.0002 | -0.0014 | 0.0032 | 4.2461 | 0.0038215 |  | 62.069 | 100
19980508143000 | 1998-05-08 14:30 | -0.052 |  | 0 | 35.441 | 34.617 | 29.702 | 28.6 |  | 146.838 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2383 | 0.0009 | -0.0006 | 0.0024 | 4.263 | 0.0038367 |  | 62.069 | 100
19980508150000 | 1998-05-08 15:00 | 0 |  | 0 | 35.279 | 34.617 | 29.924 | 28.6 |  | 145.171 | -0.167 |  | 0.0024 | 0.0085 | 0.0032 | 0.0063 | 4.2505 | 0.0002 | -0.0006 | 0.004 | 4.2745 | 0.003847 |  | 62.069 | 100
19980508153000 | 1998-05-08 15:30 | -0.026 |  | 0 | 35.262 | 33.071 | 29.928 | 28.98 |  | 144.421 | -0.167 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | 4.2649 | 0.0032 | -0.0006 | 0.0024 | 4.2927 | 0.0038634 |  | 62.069 | 100
19980508160000 | 1998-05-08 16:00 | -0.026 |  | 0 | 34.888 | 32.474 | 29.928 | 29.106 |  | 144.254 | 0 |  | 0.0024 | 0.0101 | 0.0032 | 0.0063 | 4.2756 | 0.0002 | -0.0014 | 0.0063 | 4.3027 | 0.0038724 |  | 62.069 | 100
19980508163000 | 1998-05-08 16:30 | -0.026 |  | 0 | 34.482 | 32.574 | 30.021 | 29.687 |  | 143.587 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.2793 | 0.0009 | -0.0006 | 0.0032 | 4.3025 | 0.0038722 |  | 62.069 | 100
19980508170000 | 1998-05-08 17:00 | 0 |  | 0 | 34.1 | 32.614 | 30.174 | 29.486 |  | 143.671 | 0 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.2854 | 0.0009 | -0.0006 | 0.0032 | 4.3094 | 0.0038785 |  | 62.069 | 100
19980508173000 | 1998-05-08 17:30 | -0.052 |  | 0 | 33.899 | 32.398 | 30.413 | 29.511 |  | 142.671 | -0.25 |  | 0.004 | 0.0085 | 0.004 | 0.0063 | 4.29 | 0.0009 | 0.0002 | 0.0047 | 4.3186 | 0.0038867 |  | 62.069 | 100
19980508180000 | 1998-05-08 18:00 | -0.026 |  | 0 | 33.828 | 32.639 | 30.59 | 29.511 |  | 141.504 | 0 |  | 0.0032 | 0.0085 | 0.0032 | 0.007 | 4.2878 | 0.0032 | -0.0006 | 0.0032 | 4.3155 | 0.0038839 |  | 62.069 | 100
19980508183000 | 1998-05-08 18:30 | -0.026 |  | 0 | 33.826 | 32.865 | 30.749 | 29.978 |  | 142.171 | 0 |  | 0.0024 | 0.007 | 0.0032 | 0.0055 | 4.29 | 0.0024 | -0.0014 | 0.0055 | 4.3146 | 0.0038831 |  | 62.069 | 100
19980508190000 | 1998-05-08 19:00 | -0.052 |  | 0 | 33.827 | 32.981 | 30.929 | 29.852 |  | 140.171 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.007 | 4.2954 | 0.0009 | -0.0006 | 0.0047 | 4.3224 | 0.0038902 |  | 62.069 | 100
19980508193000 | 1998-05-08 19:30 | -0.026 |  | 0.092 | 33.826 | 32.88 | 31.136 | 30.714 |  | 139.921 | -0.25 |  | 0.0047 | 0.007 | 0.004 | 0.0063 | 4.29 | 0.0009 | -0.0021 | 0.0017 | 4.3125 | 0.0038812 |  | 62.069 | 100
19980508200000 | 1998-05-08 20:00 | -0.026 |  | 0.095 | 33.826 | 32.779 | 31.37 | 30.613 |  | 140.754 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 4.2764 | 0.0009 | -0.0021 | 0.0032 | 4.2996 | 0.0038696 |  | 62.069 | 100
19980508203000 | 1998-05-08 20:30 | 0 |  | 0.094 | 33.902 | 32.981 | 31.568 | 30.574 |  | 142.837 | -0.25 |  | 0.0047 | 0.0078 | 0.0032 | 0.0055 | 4.2732 | 0.0002 | -0.0006 | 0.0024 | 4.2964 | 0.0038668 |  | 62.069 | 100
19980508210000 | 1998-05-08 21:00 | 0 |  | 0.095 | 33.943 | 33.056 | 31.757 | 31.371 |  | 140.837 | -0.083 |  | 0.0047 | 0.0078 | 0.0047 | 0.0055 | 4.2627 | 0.0017 | -0.0014 | 0.0032 | 4.2889 | 0.00386 |  | 62.069 | 100
19980508213000 | 1998-05-08 21:30 | -0.026 |  | 0 | 33.839 | 32.614 | 31.901 | 30.929 |  | 140.504 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.007 | 4.2556 | 0.0009 | -0.0006 | 0.004 | 4.2826 | 0.0038543 |  | 62.069 | 100
19980508220000 | 1998-05-08 22:00 | -0.026 |  | 0 | 33.826 | 33.196 | 32.093 | 31.27 |  | 139.587 | -0.167 |  | 0.0047 | 0.007 | 0.0047 | 0.0063 | 4.2512 | 0.0002 | -0.0014 | 0.0032 | 4.2759 | 0.0038483 |  | 62.069 | 100
19980508223000 | 1998-05-08 22:30 | -0.026 |  | 20.523 | 33.825 | 32.79 | 32.267 | 31.346 |  | 140.754 | -0.333 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.2412 | 0.0017 | -0.0006 | 0.004 | 4.2676 | 0.0038408 |  | 62.069 | 100
19980508230000 | 1998-05-08 23:00 | 0 |  | 0 | 33.825 | 32.664 | 32.352 | 30.979 |  | 141.087 | -0.083 |  | 0.004 | 0.007 | 0.0047 | 0.0063 | 4.2434 | 0.0002 | 0.0009 | 0.0047 | 4.2712 | 0.0038441 |  | 62.069 | 100
19980508233000 | 1998-05-08 23:30 | 0 |  | 0 | 33.827 | 32.564 | 32.49 | 31.601 |  | 140.254 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.2275 | 0.0009 | 0.0002 | 0.004 | 4.2553 | 0.0038298 |  | 62.069 | 100
19980509000000 | 1998-05-09 | 0 |  | 0 | 33.832 | 32.574 | 32.593 | 31.611 |  | 141.671 | -0.167 |  | 0.0047 | 0.0078 | 0.0047 | 0.007 | 4.2236 | 0.0002 | -0.0006 | 0.0032 | 4.2506 | 0.0038255 |  | 62.069 | 100
19980509003000 | 1998-05-09 00:30 | 0 |  | 0 | 33.83 | 32.449 | 32.593 | 31.726 |  | 140.837 | 0.083 |  | 0.0024 | 0.0085 | 0.0032 | 0.0032 | 4.22 | 0.0009 | -0.0006 | 0.0009 | 4.2385 | 0.0038146 |  | 62.069 | 100
19980509010000 | 1998-05-09 01:00 | 0 |  | 0 | 33.662 | 32.158 | 32.637 | 31.676 |  | 141.921 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.0063 | 4.2139 | 0.0009 | -0.0006 | 0.0032 | 4.2402 | 0.0038162 |  | 62.069 | 100
19980509013000 | 1998-05-09 01:30 | -0.026 |  | 0 | 33.597 | 32.574 | 32.813 | 31.852 |  | 143.254 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.007 | 4.2085 | 0.0002 | -0.0006 | 0.0024 | 4.2325 | 0.0038092 |  | 62.069 | 100
19980509020000 | 1998-05-09 02:00 | 0 |  | 0.095 | 33.598 | 32.524 | 32.844 | 31.32 |  | 143.421 | -0.083 |  | 0.004 | 0.0078 | 0.0047 | 0.007 | 4.1963 | 0.0009 | -0.0006 | 0.0024 | 4.2225 | 0.0038002 |  | 62.069 | 100
19980509023000 | 1998-05-09 02:30 | 0 |  | 0.097 | 33.599 | 32.74 | 32.843 | 32.017 |  | 145.421 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.1895 | 0.0009 | -0.0021 | 0.0032 | 4.2112 | 0.0037901 |  | 62.069 | 100
19980509030000 | 1998-05-09 03:00 | -0.026 |  | 0.095 | 33.598 | 32.625 | 32.843 | 32.143 |  | 145.421 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.187 | 0.0009 | -0.0006 | 0.0032 | 4.2125 | 0.0037912 |  | 62.069 | 100
19980509033000 | 1998-05-09 03:30 | 0 |  | 0.093 | 33.598 | 32.524 | 32.844 | 32.043 |  | 145.087 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1833 | 0.0002 | -0.0006 | 0.004 | 4.2089 | 0.003788 |  | 62.069 | 100
19980509040000 | 1998-05-09 04:00 | -0.026 |  | 0.098 | 33.598 | 32.675 | 32.844 | 31.953 |  | 147.088 | -0.25 |  | 0.0047 | 0.007 | 0.0047 | 0.0055 | 4.1726 | 0.0002 | -0.0006 | 0.0024 | 4.1965 | 0.0037768 |  | 62.069 | 100
19980509043000 | 1998-05-09 04:30 | 0 |  | 0.098 | 33.599 | 32.158 | 32.834 | 31.436 |  | 146.671 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.1917 | 0.0009 | -0.0014 | 0.0009 | 4.2118 | 0.0037906 |  | 62.069 | 100
19980509050000 | 1998-05-09 05:00 | -0.026 |  | 0.097 | 33.595 | 32.725 | 32.705 | 32.244 |  | 146.838 | 0.167 |  | 0.0047 | 0.007 | 0.004 | 0.0063 | 4.1909 | 0.0009 | -0.0006 | 0.0055 | 4.2187 | 0.0037968 |  | 62.069 | 100
19980509053000 | 1998-05-09 05:30 | 0 |  | 0.094 | 33.569 | 32.449 | 32.587 | 31.726 |  | 148.254 | -0.167 |  | 0.004 | 0.0078 | 0.004 | 0.0063 | 4.1763 | 0.0017 | -0.0006 | 0.0047 | 4.2042 | 0.0037838 |  | 62.069 | 100
19980509060000 | 1998-05-09 06:00 | -0.026 |  | 0 | 33.418 | 32.093 | 32.586 | 32.093 |  | 147.171 | -0.167 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.1909 | 0.0017 | -0.0006 | 0.0032 | 4.2171 | 0.0037954 |  | 62.069 | 100
19980509063000 | 1998-05-09 06:30 | -0.026 |  | 0 | 33.411 | 32.283 | 32.585 | 31.561 |  | 151.588 | -0.083 |  | 0.0047 | 0.0085 | 0.0047 | 0.007 | 4.2053 | 0.0002 | 0.0002 | 0.0032 | 4.2338 | 0.0038104 |  | 62.069 | 100
19980509070000 | 1998-05-09 07:00 | -0.026 |  | 0 | 33.452 | 32.258 | 32.583 | 31.295 |  | 150.754 | 0 |  | 0.0032 | 0.0093 | 0.0047 | 0.0063 | 4.1802 | 0.0002 | -0.0006 | 0.004 | 4.2073 | 0.0037866 |  | 62.069 | 100
19980509073000 | 1998-05-09 07:30 | 0 |  | 0 | 33.499 | 32.093 | 32.584 | 32.093 |  | 151.338 | 0.083 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.1741 | 0.0017 | -0.0006 | 0.004 | 4.2004 | 0.0037804 |  | 62.069 | 100
19980509080000 | 1998-05-09 08:00 | 0 |  | 0 | 33.575 | 32.017 | 32.739 | 31.536 |  | 152.088 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.1565 | 0.0009 | -0.0006 | 0.0063 | 4.1836 | 0.0037652 |  | 62.069 | 100
19980509083000 | 1998-05-09 08:30 | -0.026 |  | 0 | 33.59 | 32.168 | 32.835 | 31.927 |  | 151.838 | 0.083 |  | 0.0024 | 0.0078 | 0.004 | 0.007 | 4.1589 | 0.0017 | -0.0006 | 0.0024 | 4.1836 | 0.0037652 |  | 62.069 | 100
19980509090000 | 1998-05-09 09:00 | -0.026 |  | 0 | 33.591 | 31.917 | 32.835 | 32.398 |  | 146.838 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.1565 | 0.0002 | -0.0021 | 0.0032 | 4.179 | 0.0037611 |  | 62.069 | 100
19980509093000 | 1998-05-09 09:30 | -0.052 |  | 0 | 33.591 | 32.484 | 32.909 | 32.003 |  | 145.671 | -0.083 |  | 0.0024 | 0.0078 | 0.0032 | 0.0055 | 4.1604 | 0.0002 | -0.0014 | 0.004 | 4.1821 | 0.0037639 |  | 62.069 | 100
19980509100000 | 1998-05-09 10:00 | 0 |  | 0 | 33.59 | 32.373 | 33.067 | 31.892 |  | 145.921 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.1611 | 0.0017 | -0.0006 | 0.0032 | 4.1874 | 0.0037687 |  | 62.069 | 100
19980509103000 | 1998-05-09 10:30 | 0 |  | 0 | 33.588 | 32.79 | 33.066 | 32.068 |  | 146.588 | 0 |  | 0.0032 | 0.0093 | 0.004 | 0.0055 | 4.1611 | 0.0017 | 0.0017 | 0.0032 | 4.1897 | 0.0037707 |  | 62.069 | 100
19980509110000 | 1998-05-09 11:00 | 0 |  | 0 | 33.591 | 32.549 | 33.218 | 32.549 |  | 145.754 | -0.083 |  | 0.004 | 0.0093 | 0.0032 | 0.0063 | 4.1719 | 0.0009 | -0.0006 | 0.0032 | 4.1982 | 0.0037784 |  | 62.069 | 100
19980509113000 | 1998-05-09 11:30 | 0.026 |  | 0.218 | 33.59 | 32.183 | 33.331 | 31.942 |  | 142.921 | -0.083 |  | 0.0032 | 0.0078 | 0.0055 | 0.0055 | 4.1748 | 0.0009 | -0.0006 | 0.0032 | 4.2003 | 0.0037803 |  | 62.069 | 100
19980509120000 | 1998-05-09 12:00 | 0 |  | 7.038 | 33.592 | 32.334 | 33.33 | 32.093 |  | 140.337 | -0.25 |  | 0.004 | 0.0078 | 0.0047 | 0.0047 | 4.1741 | 0.0009 | -0.0006 | 0.0032 | 4.1988 | 0.0037789 |  | 62.069 | 100
19980509123000 | 1998-05-09 12:30 | 0 |  | 5.325 | 33.59 | 32.689 | 33.498 | 32.689 |  | 141.421 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.1763 | 0.0009 | -0.0006 | 0.0047 | 4.2033 | 0.003783 |  | 62.069 | 100
19980509130000 | 1998-05-09 13:00 | 0 |  | 23.184 | 33.592 | 32.398 | 33.561 | 32.639 |  | 139.921 | -0.167 |  | 0.0032 | 0.0085 | 0.0047 | 0.007 | 4.187 | 0.0009 | -0.0014 | 0.004 | 4.2139 | 0.0037925 |  | 62.069 | 100
19980509133000 | 1998-05-09 13:30 | -0.026 |  | 7.407 | 33.592 | 32.715 | 33.563 | 32.715 |  | 138.254 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.0055 | 4.197 | 0.0002 | -0.0006 | 0.0047 | 4.2225 | 0.0038002 |  | 62.069 | 100
19980509140000 | 1998-05-09 14:00 | 0 |  | 10.733 | 33.591 | 32.524 | 33.562 | 33.006 |  | 137.837 | -0.167 |  | 0.0047 | 0.0078 | 0.0032 | 0.007 | 4.2039 | 0.0002 | 0.0009 | 0.0024 | 4.2301 | 0.0038071 |  | 62.069 | 100
19980509143000 | 1998-05-09 14:30 | 0 |  | 5.817 | 33.593 | 32.689 | 33.563 | 32.93 |  | 139.171 | -0.167 |  | 0.0032 | 0.0093 | 0.0032 | 0.0063 | 4.2214 | 0.0017 | -0.0006 | 0.0032 | 4.2477 | 0.0038229 |  | 62.069 | 100
19980509150000 | 1998-05-09 15:00 | 0 |  | 3.001 | 33.59 | 32.398 | 33.562 | 32.398 |  | 137.504 | 0 |  | 0.0032 | 0.0093 | 0.0047 | 0.0055 | 4.2261 | 0.0009 | -0.0006 | 0.0055 | 4.2546 | 0.0038291 |  | 62.069 | 100
19980509153000 | 1998-05-09 15:30 | 0 |  | 1.66 | 33.592 | 32.308 | 33.564 | 32.549 |  | 135.921 | -0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0055 | 4.2649 | 0.0002 | 0.0002 | 0.0047 | 4.2897 | 0.0038607 |  | 62.069 | 100
19980509160000 | 1998-05-09 16:00 | 0 |  | 15.725 | 33.591 | 32.599 | 33.563 | 32.599 |  | 136.004 | -0.25 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.29 | 0.0009 | -0.0006 | 0.004 | 4.314 | 0.0038826 |  | 62.069 | 100
19980509163000 | 1998-05-09 16:30 | 0 |  | 0.675 | 33.593 | 32.449 | 33.564 | 32.449 |  | 136.171 | -0.25 |  | 0.0032 | 0.0085 | 0.0032 | 0.0055 | 4.2954 | 0.0002 | -0.0006 | 0.0032 | 4.3186 | 0.0038867 |  | 62.069 | 100
19980509170000 | 1998-05-09 17:00 | 0 |  | 0.794 | 33.593 | 32.158 | 33.56 | 32.158 |  | 134.504 | -0.167 |  | 0.0032 | 0.0078 | 0.0024 | 0.0063 | 4.3145 | 0.0017 | -0.0014 | 0.0032 | 4.3377 | 0.0039039 |  | 62.069 | 100
19980509173000 | 1998-05-09 17:30 | -0.026 |  | 0.551 | 33.591 | 32.258 | 33.4 | 32.017 |  | 132.504 | -0.25 |  | 0.0032 | 0.007 | 0.004 | 0.0063 | 4.3206 | 0.0002 | 0.0009 | 0.0047 | 4.3469 | 0.0039122 |  | 62.069 | 100
19980509180000 | 1998-05-09 18:00 | -0.026 |  | 0.217 | 33.489 | 32.283 | 33.334 | 32.283 |  | 131.42 | -0.167 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.3281 | 0.0017 | -0.0006 | 0.004 | 4.3537 | 0.0039183 |  | 62.069 | 100
19980509183000 | 1998-05-09 18:30 | 0 |  | 0 | 33.38 | 32.043 | 33.332 | 31.08 |  | 132.504 | 0 |  | 0.0032 | 0.0085 | 0.004 | 0.0055 | 4.3396 | 0.0009 | 0.0002 | 0.0024 | 4.3643 | 0.0039279 |  | 62.069 | 100
19980509190000 | 1998-05-09 19:00 | 0 |  | 0 | 33.376 | 32.017 | 33.331 | 31.295 |  | 131.254 | -0.083 |  | 0.0055 | 0.0085 | 0.0032 | 0.0063 | 4.3594 | 0.0009 | -0.0006 | 0.0032 | 4.3864 | 0.0039478 |  | 62.069 | 100
19980509193000 | 1998-05-09 19:30 | 0 |  | 0 | 33.376 | 31.877 | 33.241 | 31.636 |  | 130.254 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0078 | 4.3647 | 0.0002 | -0.0006 | 0.0032 | 4.3902 | 0.0039512 |  | 62.069 | 100
19980509200000 | 1998-05-09 20:00 | 0 |  | 0 | 33.377 | 31.992 | 33.069 | 31.27 |  | 130.587 | 0 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.3572 | 0.0009 | 0.0002 | 0.0055 | 4.3858 | 0.0039472 |  | 62.069 | 100
19980509203000 | 1998-05-09 20:30 | -0.026 |  | 0.096 | 33.376 | 31.992 | 33.068 | 31.752 |  | 132.67 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 4.3564 | 0.0002 | 0.0002 | 0.0032 | 4.3812 | 0.0039431 |  | 62.069 | 100
19980509210000 | 1998-05-09 21:00 | -0.026 |  | 0 | 33.376 | 31.586 | 32.912 | 31.827 |  | 132.837 | -0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0055 | 4.3464 | 0.0009 | 0.0009 | 0.0032 | 4.3718 | 0.0039346 |  | 62.069 | 100
19980509213000 | 1998-05-09 21:30 | -0.079 |  | 0 | 33.376 | 32.208 | 32.836 | 31.245 |  | 131.837 | -0.083 |  | 0.0024 | 0.007 | 0.0032 | 0.0047 | 4.3435 | 0.0002 | 0.0002 | 0.0032 | 4.3644 | 0.003928 |  | 62.069 | 100
19980509220000 | 1998-05-09 22:00 | -0.026 |  | 0.093 | 33.375 | 31.651 | 32.772 | 30.689 |  | 133.837 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.3281 | 0.0002 | -0.0006 | 0.0047 | 4.3537 | 0.0039183 |  | 62.069 | 100
19980509223000 | 1998-05-09 22:30 | -0.052 |  | 0 | 33.364 | 31.691 | 32.584 | 30.969 |  | 135.337 | 0 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | 4.3289 | 0.0002 | -0.0006 | 0.0024 | 4.3521 | 0.0039169 |  | 62.069 | 100
19980509230000 | 1998-05-09 23:00 | -0.026 |  | 0 | 33.351 | 31.17 | 32.582 | 30.929 |  | 135.171 | -0.083 |  | 0.0024 | 0.0078 | 0.0047 | 0.0055 | 4.313 | 0.0009 | -0.0006 | 0.0017 | 4.3354 | 0.0039019 |  | 62.069 | 100
19980509233000 | 1998-05-09 23:30 | 0 |  | 0 | 33.117 | 31.942 | 32.408 | 30.979 |  | 136.671 | -0.083 |  | 0.0032 | 0.007 | 0.004 | 0.0047 | 4.313 | 0.0002 | -0.0014 | 0.0032 | 4.3339 | 0.0039005 |  | 62.069 | 100
19980510000000 | 1998-05-10 | 0 |  | 0 | 33.049 | 31.496 | 32.361 | 31.256 |  | 136.337 | -0.25 |  | 0.0032 | 0.007 | 0.0032 | 0.0055 | 4.3 | 0.0009 | -0.0006 | 0.0063 | 4.3255 | 0.0038929 |  | 62.069 | 100
19980510003000 | 1998-05-10 00:30 | 0 |  | 0 | 33.048 | 31.371 | 32.345 | 31.13 |  | 138.087 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 4.2939 | 0.0002 | -0.0014 | 0.0024 | 4.3178 | 0.003886 |  | 62.069 | 100
19980510010000 | 1998-05-10 01:00 | 0 |  | 0 | 32.927 | 31.536 | 32.135 | 30.814 |  | 138.671 | 0 |  | 0.0032 | 0.0063 | 0.0055 | 0.0047 | 4.2832 | 0.0009 | -0.0006 | 0.004 | 4.3072 | 0.0038765 |  | 62.069 | 100
19980510013000 | 1998-05-10 01:30 | 0 |  | 0 | 32.835 | 31.12 | 32.101 | 31.12 |  | 137.087 | 0 |  | 0.0032 | 0.007 | 0.0032 | 0.0055 | 4.2764 | 0.0009 | -0.0006 | 0.0032 | 4.2988 | 0.0038689 |  | 62.069 | 100
19980510020000 | 1998-05-10 02:00 | 0 |  | 0 | 32.835 | 31.295 | 32.102 | 31.055 |  | 136.921 | -0.083 |  | 0.004 | 0.0078 | 0.0032 | 0.0063 | 4.2695 | 0.0002 | -0.0006 | 0.004 | 4.2944 | 0.003865 |  | 62.069 | 100
19980510023000 | 1998-05-10 02:30 | 0.026 |  | 0 | 32.834 | 31.636 | 32.101 | 30.674 |  | 135.921 | -0.25 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.2688 | 0.0009 | -0.0006 | 0.0024 | 4.2927 | 0.0038634 |  | 62.069 | 100
19980510030000 | 1998-05-10 03:00 | 0 |  | 0 | 32.739 | 31.32 | 32.101 | 31.32 |  | 136.337 | 0 |  | 0.0032 | 0.007 | 0.0032 | 0.0047 | 4.2664 | 0.0002 | -0.0006 | 0.0032 | 4.2873 | 0.0038586 |  | 62.069 | 100
19980510033000 | 1998-05-10 03:30 | 0 |  | 0 | 32.601 | 31.295 | 32.101 | 30.814 |  | 136.587 | -0.25 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.2603 | 0.0002 | -0.0006 | 0.0032 | 4.2844 | 0.003856 |  | 62.069 | 100
19980510040000 | 1998-05-10 04:00 | 0 |  | 0 | 32.6 | 31.385 | 32.101 | 30.663 |  | 135.004 | 0 |  | 0.0032 | 0.007 | 0.0032 | 0.0063 | 4.2581 | 0.0009 | 0.0002 | 0.004 | 4.2829 | 0.0038546 |  | 62.069 | 100
19980510043000 | 1998-05-10 04:30 | -0.026 |  | 0 | 32.6 | 31.27 | 32.1 | 30.548 |  | 134.171 | -0.083 |  | 0.0047 | 0.007 | 0.004 | 0.0055 | 4.2542 | 0.0002 | -0.0014 | 0.0032 | 4.2774 | 0.0038497 |  | 62.069 | 100
19980510050000 | 1998-05-10 05:00 | 0 |  | 0 | 32.597 | 31.396 | 32.098 | 30.674 |  | 133.671 | -0.083 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.2573 | 0.0009 | -0.0006 | 0.0032 | 4.2813 | 0.0038532 |  | 62.069 | 100
19980510053000 | 1998-05-10 05:30 | -0.052 |  | 0.095 | 32.593 | 31.155 | 32.093 | 30.915 |  | 134.254 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2649 | 0.0009 | -0.0006 | 0.004 | 4.2912 | 0.0038621 |  | 62.069 | 100
19980510060000 | 1998-05-10 06:00 | -0.026 |  | 0 | 32.594 | 30.954 | 32.092 | 30.954 |  | 134.254 | -0.25 |  | 0.0055 | 0.0078 | 0.004 | 0.0063 | 4.2627 | 0.0009 | 0.0002 | 0.0017 | 4.2891 | 0.0038602 |  | 62.069 | 100
19980510063000 | 1998-05-10 06:30 | -0.026 |  | 15.516 | 32.59 | 31.105 | 32.008 | 31.105 |  | 136.087 | -0.083 |  | 0.0032 | 0.0085 | 0.004 | 0.0063 | 4.2717 | 0.0009 | 0.0002 | 0.0032 | 4.298 | 0.0038682 |  | 62.069 | 100
19980510070000 | 1998-05-10 07:00 | 0 |  | 0 | 32.46 | 31.055 | 31.86 | 30.574 |  | 135.254 | -0.083 |  | 0.0032 | 0.0063 | 0.004 | 0.0055 | 4.2725 | 0.0002 | -0.0014 | 0.004 | 4.2943 | 0.0038649 |  | 62.069 | 100
19980510073000 | 1998-05-10 07:30 | -0.052 |  | 0 | 32.376 | 31.396 | 31.861 | 30.915 |  | 132.17 | -0.167 |  | 0.0032 | 0.007 | 0.0047 | 0.007 | 4.2778 | 0.0009 | -0.0006 | 0.007 | 4.307 | 0.0038763 |  | 62.069 | 100
19980510080000 | 1998-05-10 08:00 | -0.026 |  | 0 | 32.376 | 30.979 | 31.86 | 30.739 |  | 134.087 | -0.083 |  | 0.0024 | 0.0078 | 0.004 | 0.0055 | 4.2756 | 0.0002 | -0.0014 | 0.0024 | 4.2965 | 0.0038668 |  | 62.069 | 100
19980510083000 | 1998-05-10 08:30 | 0 |  | 0 | 32.378 | 30.523 | 31.861 | 30.283 |  | 135.754 | -0.083 |  | 0.0032 | 0.007 | 0.0032 | 0.0055 | 4.2778 | 0.0017 | -0.0006 | 0.0047 | 4.3025 | 0.0038722 |  | 62.069 | 100
19980510090000 | 1998-05-10 09:00 | -0.026 |  | 0.096 | 32.38 | 30.689 | 31.864 | 30.929 |  | 134.337 | -0.083 |  | 0.0032 | 0.007 | 0.004 | 0.0032 | 4.2832 | 0.0017 | -0.0014 | 0.0032 | 4.3041 | 0.0038737 |  | 62.069 | 100
19980510093000 | 1998-05-10 09:30 | 0 |  | 0 | 32.361 | 30.839 | 31.86 | 30.358 |  | 133.754 | -0.167 |  | 0.0047 | 0.007 | 0.004 | 0.0063 | 4.29 | 0.0009 | -0.0006 | 0.004 | 4.3163 | 0.0038847 |  | 62.069 | 100
19980510100000 | 1998-05-10 10:00 | -0.026 |  | 0 | 32.103 | 30.915 | 31.707 | 30.433 |  | 132.504 | -0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.2947 | 0.0009 | -0.0006 | 0.0032 | 4.3202 | 0.0038882 |  | 62.069 | 100
19980510103000 | 1998-05-10 10:30 | 0 |  | 0 | 32.042 | 30.94 | 31.614 | 30.459 |  | 133.504 | -0.25 |  | 0.0032 | 0.0085 | 0.004 | 0.007 | 4.2976 | 0.0009 | -0.0006 | 0.0032 | 4.3238 | 0.0038914 |  | 62.069 | 100
19980510110000 | 1998-05-10 11:00 | -0.026 |  | 0 | 32.042 | 30.839 | 31.611 | 30.358 |  | 134.087 | 0.167 |  | 0.0032 | 0.007 | 0.0032 | 0.0055 | 4.3022 | 0.0009 | 0.0002 | 0.004 | 4.3262 | 0.0038936 |  | 62.069 | 100
19980510113000 | 1998-05-10 11:30 | 0 |  | 0 | 32.042 | 31.195 | 31.611 | 30.714 |  | 132.004 | -0.25 |  | 0.004 | 0.007 | 0.0032 | 0.0063 | 4.3123 | 0.0009 | -0.0006 | 0.004 | 4.3371 | 0.0039034 |  | 62.069 | 100
19980510120000 | 1998-05-10 12:00 | 0 |  | 0 | 32.043 | 30.473 | 31.612 | 29.992 |  | 131.42 | -0.25 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.3167 | 0.0002 | 0.0002 | 0.0047 | 4.3438 | 0.0039094 |  | 62.069 | 100
19980510123000 | 1998-05-10 12:30 | 0 |  | 0 | 32.043 | 30.473 | 31.61 | 30.473 |  | 132.754 | -0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0055 | 4.3281 | 0.0009 | 0.0002 | 0.0055 | 4.3544 | 0.003919 |  | 62.069 | 100
19980510130000 | 1998-05-10 13:00 | -0.026 |  | 0 | 32.043 | 31.005 | 31.612 | 30.764 |  | 131.337 | -0.25 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | 4.3281 | 0.0009 | -0.0006 | 0.004 | 4.3529 | 0.0039176 |  | 62.069 | 100
19980510133000 | 1998-05-10 13:30 | -0.026 |  | 0 | 32.025 | 30.904 | 31.61 | 30.182 |  | 130.087 | 0 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.3435 | 0.0009 | 0.0002 | 0.0032 | 4.3691 | 0.0039322 |  | 62.069 | 100
19980510140000 | 1998-05-10 14:00 | -0.026 |  | 0 | 31.893 | 30.764 | 31.611 | 30.523 |  | 130.754 | -0.167 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.3411 | 0.0017 | -0.0006 | 0.004 | 4.3682 | 0.0039314 |  | 62.069 | 100
19980510143000 | 1998-05-10 14:30 | 0 |  | 0 | 31.829 | 30.839 | 31.612 | 30.599 |  | 130.504 | -0.083 |  | 0.0032 | 0.0085 | 0.0032 | 0.0047 | 4.3489 | 0.0009 | -0.0006 | 0.0024 | 4.3712 | 0.0039341 |  | 62.069 | 100
19980510150000 | 1998-05-10 15:00 | -0.026 |  | 0 | 31.828 | 30.523 | 31.61 | 30.042 |  | 130.337 | -0.083 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.3518 | 0.0002 | 0.0009 | 0.004 | 4.3782 | 0.0039404 |  | 62.069 | 100
19980510153000 | 1998-05-10 15:30 | -0.026 |  | 0 | 31.827 | 30.689 | 31.61 | 30.208 |  | 127.92 | -0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0055 | 4.3655 | 0.0009 | -0.0006 | 0.0032 | 4.3895 | 0.0039505 |  | 62.069 | 100
19980510160000 | 1998-05-10 16:00 | -0.026 |  | 0 | 31.829 | 30.789 | 31.61 | 30.548 |  | 126.837 | -0.167 |  | 0.0047 | 0.0085 | 0.0047 | 0.007 | 4.3708 | 0.0009 | 0.0017 | 0.0017 | 4.4 | 0.00396 |  | 62.069 | 100
19980510163000 | 1998-05-10 16:30 | 0 |  | 0 | 31.829 | 30.448 | 31.611 | 29.967 |  | 128.17 | 0.083 |  | 0.0047 | 0.007 | 0.0032 | 0.0055 | 4.3823 | 0.0002 | 0.0002 | 0.0032 | 4.4063 | 0.0039657 |  | 62.069 | 100
19980510170000 | 1998-05-10 17:00 | -0.026 |  | 6.668 | 32.222 | 42.269 | 32.212 | 45.416 |  | 130.087 | 355.177 |  | 0.004 | 0.0085 | 0.0032 | 0.0047 | 4.4106 | 0.0017 | 0.0002 | 0.0032 | 4.4361 | 0.0039925 |  | 62.069 | 100
19980510173000 | 1998-05-10 17:30 | -0.026 |  | 0.217 | 46.766 | 69.54 | 48.328 | 75.167 |  | 125.337 | 332.926 |  | 0.0047 | 0.0078 | 0.004 | 0.0055 | 4.4236 | 0.0009 | 0.0002 | 0.004 | 4.4507 | 0.0040056 |  | 62.069 | 100
19980510180000 | 1998-05-10 18:00 | -0.026 |  | 0.34 | 66.597 | 83.205 | 68.629 | 83.942 |  | 123.004 | 325.259 |  | 0.0024 | 0.0078 | 0.004 | 0.007 | 4.4351 | 0.0009 | 0.0002 | 0.0047 | 4.4621 | 0.0040159 |  | 62.069 | 100
19980510183000 | 1998-05-10 18:30 | 0 |  | 0.547 | 78.686 | 90.937 | 80.92 | 90.446 |  | 125.337 | 323.843 |  | 0.0032 | 0.0078 | 0.0047 | 0.0055 | 4.4502 | 0.0017 | 0.0002 | 0.0024 | 4.4757 | 0.0040281 |  | 62.069 | 100
19980510190000 | 1998-05-10 19:00 | 0 |  | 0.3 | 86.961 | 97.529 | 89.159 | 96.298 |  | 124.254 | 322.593 |  | 0.0047 | 0.0085 | 0.0032 | 0.0063 | 4.4624 | 0.0009 | 0.0002 | 0.004 | 4.4902 | 0.0040412 |  | 62.069 | 100
19980510193000 | 1998-05-10 19:30 | 0 |  | 0.084 | 93.628 | 102.311 | 95.209 | 101.08 |  | 124.42 | 327.926 |  | 0.0024 | 0.0078 | 0.0047 | 0.0047 | 4.4617 | 0.0009 | 0.0009 | 0.0032 | 4.4863 | 0.0040377 |  | 62.069 | 100
19980510200000 | 1998-05-10 20:00 | 0 |  | 0.207 | 99.226 | 106.579 | 99.792 | 103.621 |  | 123.504 | 394.345 |  | 0.0024 | 0.0085 | 0.0024 | 0.0055 | 4.4595 | 0.0017 | 0.0009 | 0.0032 | 4.4841 | 0.0040357 |  | 62.069 | 100
19980510203000 | 1998-05-10 20:30 | 0 |  | 0.176 | 103.24 | 108.188 | 102.088 | 103.503 |  | 126.92 | 391.845 |  | 0.004 | 0.007 | 0.0032 | 0.0055 | 4.4509 | 0.0024 | 0.0002 | 0.0009 | 4.4741 | 0.0040267 |  | 62.069 | 100
19980510210000 | 1998-05-10 21:00 | 0 |  | 15.836 | 105.021 | 93.653 | 101.776 | 89.473 |  | 578.35 | 246.59 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.4495 | 0.0009 | 0.0009 | 0.0032 | 4.4764 | 0.0040288 |  | 62.069 | 100
19980510213000 | 1998-05-10 21:30 | -0.026 |  | 1.282 | 88.44 | 65.784 | 85.858 | 66.516 |  | 789.939 | 638.602 |  | 0.0032 | 0.0085 | 0.0032 | 0.0063 | 4.4351 | 0.0002 | 0.0002 | 0.0032 | 4.4599 | 0.0040139 |  | 62.069 | 100
19980510220000 | 1998-05-10 22:00 | -0.026 |  | 7.281 | 71.489 | 67.366 | 71.061 | 68.343 |  | 914.526 | 872.192 |  | 0.0055 | 0.0078 | 0.0047 | 0.0063 | 4.4045 | 0.0009 | 0.0002 | 0.004 | 4.4339 | 0.0039905 |  | 62.069 | 100
19980510223000 | 1998-05-10 22:30 | 0 |  | 2.511 | 66.662 | 67.315 | 66.594 | 67.315 |  | 550.516 | 370.177 |  | 0.0047 | 0.0078 | 0.0024 | 0.0063 | 4.3655 | 0.0009 | 0.0009 | 0.0032 | 4.3917 | 0.0039525 |  | 62.069 | 100
19980510230000 | 1998-05-10 23:00 | -0.026 |  | 1.16 | 70.839 | 78.055 | 71.171 | 78.546 |  | 672.769 | 274.425 |  | 0.0024 | 0.007 | 0.0032 | 0.0055 | 4.3489 | 0.0009 | -0.0006 | 0.0024 | 4.3697 | 0.0039327 |  | 62.069 | 100
19980510233000 | 1998-05-10 23:30 | 0 |  | 6.915 | 84.969 | 115.411 | 84.926 | 111.708 |  | 709.77 | 404.928 |  | 0.0024 | 0.0085 | 0.0047 | 0.0063 | 4.3489 | 0.0002 | 0.0002 | 0.004 | 4.3752 | 0.0039377 |  | 62.069 | 100
19980511000000 | 1998-05-11 | 0 |  | 0.424 | 112.204 | 131.083 | 110.932 | 127.374 |  | 660.852 | 514.598 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 4.3367 | 0.0002 | 0.0009 | 0.0017 | 4.3608 | 0.0039247 |  | 62.069 | 100
19980511003000 | 1998-05-11 00:30 | 0 |  | 0.426 | 130.629 | 145.185 | 128.846 | 141.473 |  | 710.354 | 520.515 |  | 0.0032 | 0.0085 | 0.0047 | 0.0055 | 4.3306 | 0.0002 | 0.0009 | 0.0024 | 4.356 | 0.0039204 |  | 62.069 | 100
19980511010000 | 1998-05-11 01:00 | 0 |  | 0.666 | 143.746 | 153.276 | 141.642 | 149.315 |  | 709.937 | 592.767 |  | 0.0047 | 0.007 | 0.004 | 0.0063 | 4.3274 | 0.0009 | -0.0014 | 0.0032 | 4.3521 | 0.0039169 |  | 62.069 | 100
19980511013000 | 1998-05-11 01:30 | 0 |  | 0.791 | 150.822 | 152.038 | 149.191 | 150.553 |  | 719.521 | 590.1 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 4.3137 | 0.0009 | 0.0017 | 0.0032 | 4.3415 | 0.0039073 |  | 62.069 | 100
19980511020000 | 1998-05-11 02:00 | 49.283 |  | 0.544 | 151.02 | 151.037 | 151.24 | 153.265 |  | 654.019 | 530.849 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | 4.3015 | 0.0002 | 0.0009 | 0.0032 | 4.3262 | 0.0038936 |  | 62.069 | 100
19980511023000 | 1998-05-11 02:30 | 97.91 |  | 0.546 | 150.162 | 150.8 | 152.149 | 149.81 |  | 629.601 | 539.099 |  | 0.0032 | 0.0078 | 0.0047 | 0.004 | 4.3069 | 0.0017 | 0.0002 | 0.0032 | 4.3317 | 0.0038985 |  | 62.069 | 100
19980511030000 | 1998-05-11 03:00 | 149.474 |  | 0.666 | 150.344 | 151.986 | 150.957 | 152.729 |  | 664.436 | 704.52 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 4.3213 | 0.0002 | 0.0009 | 0.0017 | 4.3438 | 0.0039094 |  | 62.069 | 100
19980511033000 | 1998-05-11 03:30 | 168.479 |  | 0.667 | 150.985 | 151.909 | 152.078 | 151.414 |  | 647.352 | 795.523 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | 4.3213 | 0.0009 | -0.0006 | 0.0024 | 4.3452 | 0.0039107 |  | 62.069 | 100
19980511040000 | 1998-05-11 04:00 | 195.218 |  | 0.543 | 151.326 | 151.924 | 151.888 | 151.181 |  | 575.35 | 729.521 |  | 0.004 | 0.0078 | 0.004 | 0.0063 | 4.3259 | 0.0009 | -0.0014 | 0.0032 | 4.3507 | 0.0039156 |  | 62.069 | 100
19980511043000 | 1998-05-11 04:30 | 271.37 |  | 0.787 | 151.131 | 150.97 | 152.114 | 150.97 |  | 784.273 | 811.357 |  | 0.0047 | 0.0078 | 0.004 | 0.0063 | 4.3313 | 0.0017 | -0.0014 | 0.0032 | 4.3576 | 0.0039218 |  | 62.069 | 100
19980511050000 | 1998-05-11 05:00 | 326.158 |  | 13.546 | 151.506 | 151.96 | 151.809 | 150.228 |  | 1089.698 | 1151.866 |  | 0.0032 | 0.007 | 0.0047 | 0.0047 | 0.0024 | 0.0009 | 0.0009 | 0.0017 | 0.0255 | 2.295e-05 |  | 62.069 | 100
19980511053000 | 1998-05-11 05:30 | 348.807 |  | 0.424 | 152.352 | 152.548 | 153.321 | 153.786 |  | 1023.196 | 1071.281 |  | 0.0032 | 0.0093 | 0.0032 | 0.0063 | -0.0006 | 3.1876 | 0.5907 | 0.004 | 3.8037 | 0.0034233 |  | 62.069 | 100
19980511060000 | 1998-05-11 06:00 | 340.419 |  | 1.28 | 151.869 | 151.155 | 153.553 | 150.165 |  | 865.275 | 913.193 |  | 0.0032 | 0.0085 | 0.0047 | 4.1665 | 5.812 | 5.3796 | 5.3818 | 5.0171 | 25.7734 | 0.023196 |  | 62.069 | 100
19980511063000 | 1998-05-11 06:30 | 381.732 |  | 0.662 | 151.434 | 151.975 | 152.28 | 151.233 |  | 920.61 | 981.528 |  | 0.0032 | 0.0078 | 6.3767 | 6.6826 | 6.012 | 5.761 | 5.6802 | 5.5459 | 36.0694 | 0.032462 |  | 62.069 | 100
19980511070000 | 1998-05-11 07:00 | 467.846 |  | 5.191 | 151.459 | 153.956 | 152.168 | 152.223 |  | 1187.867 | 1264.703 |  | 0.0055 | 2.5002 | 7.1968 | 7.5234 | 6.7681 | 6.437 | 6.3462 | 6.2698 | 43.047 | 0.038742 |  | 62.069 | 100
19980511073000 | 1998-05-11 07:30 | 607.542 |  | 15.125 | 153.432 | 154.92 | 154.403 | 154.673 |  | 1420.874 | 1519.377 |  | 6.6528 | 7.3303 | 7.1138 | 7.4517 | 6.6787 | 6.3965 | 6.3164 | 6.1975 | 54.1377 | 0.048724 |  | 62.069 | 100
19980511080000 | 1998-05-11 08:00 | 610.819 |  | 8.868 | 152.219 | 150.944 | 153.501 | 150.202 |  | 1431.708 | 1527.794 |  | 6.7239 | 7.4951 | 7.2136 | 7.563 | 6.7529 | 6.4966 | 6.3979 | 6.3064 | 54.9494 | 0.049454 |  | 62.069 | 100
19980511083000 | 1998-05-11 08:30 | 630.218 |  | 2.669 | 150.853 | 151.805 | 151.593 | 150.815 |  | 1462.375 | 1562.878 |  | 6.8367 | 7.6318 | 7.3501 | 7.6667 | 6.8704 | 6.6079 | 6.4995 | 6.4119 | 55.875 | 0.050287 |  | 62.069 | 100
19980511090000 | 1998-05-11 09:00 | 631.188 |  | 5.444 | 150.713 | 152.145 | 151.925 | 150.165 |  | 1469.125 | 1569.628 |  | 6.8718 | 7.7102 | 7.4312 | 7.769 | 6.9321 | 6.6772 | 6.5515 | 6.4934 | 56.4364 | 0.050793 |  | 62.069 | 100
19980511093000 | 1998-05-11 09:30 | 633.232 |  | 3.122 | 150.833 | 151.218 | 152.273 | 150.228 |  | 1475.959 | 1579.962 |  | 6.9504 | 7.7493 | 7.4944 | 7.8193 | 6.9771 | 6.7239 | 6.5911 | 6.5347 | 56.8402 | 0.051156 |  | 62.069 | 100
19980511100000 | 1998-05-11 10:00 | 627.727 |  | 2.508 | 150.634 | 151.089 | 152.315 | 150.594 |  | 1433.208 | 1531.627 |  | 6.7253 | 7.5417 | 7.2183 | 7.5608 | 6.7544 | 6.4773 | 6.3599 | 6.3179 | 54.9556 | 0.04946 |  | 62.069 | 100
19980511103000 | 1998-05-11 10:30 | 538.625 |  | 0.296 | 149.243 | 148.743 | 150.568 | 148 |  | 1225.285 | 1296.454 |  | 5.7808 | 6.7131 | 6.1516 | 6.4583 | 5.9014 | 5.5908 | 5.5139 | 5.4695 | 47.5794 | 0.042821 |  | 62.069 | 100
19980511110000 | 1998-05-11 11:00 | 529.581 |  | 5.683 | 148.972 | 150.454 | 149.635 | 148.968 |  | 1232.702 | 1303.871 |  | 5.7632 | 6.7483 | 6.1311 | 6.4683 | 5.9434 | 5.6465 | 5.5374 | 5.4802 | 47.7184 | 0.042947 |  | 62.069 | 100
19980511113000 | 1998-05-11 11:30 | 473.718 |  | 16.198 | 150.303 | 150.908 | 150.941 | 149.67 |  | 1101.782 | 1158.95 |  | 5.1819 | 6.2356 | 5.4788 | 5.7556 | 5.4199 | 5.0896 | 5.0049 | 4.9187 | 43.085 | 0.038776 |  | 62.069 | 100
19980511120000 | 1998-05-11 12:00 | 471.569 |  | 2.261 | 150.102 | 149.866 | 150.985 | 149.371 |  | 1118.199 | 1177.784 |  | 5.375 | 6.4438 | 5.7229 | 6.0571 | 5.6543 | 3.743 | 5.2537 | 5.1277 | 43.3775 | 0.03904 |  | 62.069 | 100
19980511123000 | 1998-05-11 12:30 | 520.93 |  | 0.667 | 149.948 | 152.341 | 150.76 | 150.856 |  | 1257.286 | 1339.372 |  | 5.8503 | 6.8489 | 6.26 | 6.5811 | 6.0845 | 5.8091 | 5.6726 | 5.5664 | 48.6729 | 0.043806 |  | 62.069 | 100
19980511130000 | 1998-05-11 13:00 | 607.07 |  | 4.216 | 152.265 | 152.578 | 153.664 | 151.835 |  | 1456.542 | 1552.628 |  | 6.7834 | 7.6553 | 7.2998 | 7.666 | 6.9177 | 6.6826 | 6.5193 | 6.4302 | 55.9543 | 0.050359 |  | 62.069 | 100
19980511133000 | 1998-05-11 13:30 | 621.488 |  | 1.768 | 151.712 | 151.975 | 153.613 | 152.47 |  | 1484.793 | 1584.212 |  | 6.9045 | 7.7583 | 7.4639 | 7.8027 | 7.0183 | 6.7627 | 6.6116 | 6.5293 | 56.8513 | 0.051166 |  | 62.069 | 100
19980511140000 | 1998-05-11 14:00 | 624.896 |  | 2.381 | 150.651 | 149.737 | 153.659 | 149.984 |  | 1449.375 | 1545.878 |  | 6.9084 | 7.7493 | 7.4563 | 7.8027 | 7.0122 | 6.7681 | 6.6155 | 6.5225 | 56.835 | 0.051151 |  | 62.069 | 100
19980511143000 | 1998-05-11 14:30 | 641.437 |  | 1.278 | 150.23 | 152.589 | 152.644 | 151.846 |  | 1488.043 | 1589.379 |  | 7.0825 | 7.9094 | 7.6492 | 7.9949 | 7.1748 | 6.929 | 6.7712 | 6.697 | 58.208 | 0.052387 |  | 62.069 | 100
19980511150000 | 1998-05-11 15:00 | 643.954 |  | 3.119 | 151.159 | 152.548 | 153.714 | 153.538 |  | 1490.959 | 1590.379 |  | 7.0815 | 7.8843 | 7.644 | 7.9536 | 7.1504 | 6.9001 | 6.7458 | 6.6658 | 58.0255 | 0.052223 |  | 62.069 | 100
19980511153000 | 1998-05-11 15:30 | 642.565 |  | 1.402 | 151.185 | 151.366 | 154.407 | 153.346 |  | 1491.626 | 1591.962 |  | 7.0657 | 7.8828 | 7.6248 | 7.9431 | 7.1389 | 6.9016 | 6.7322 | 6.6621 | 57.9512 | 0.052156 |  | 62.069 | 100
19980511160000 | 1998-05-11 16:00 | 641.306 |  | 3.239 | 151.288 | 152.341 | 154.646 | 154.074 |  | 1490.626 | 1592.212 |  | 7.0962 | 7.8987 | 7.6523 | 7.9849 | 7.158 | 6.9167 | 6.7551 | 6.6758 | 58.1377 | 0.052324 |  | 62.069 | 100
19980511163000 | 1998-05-11 16:30 | 642.617 |  | 1.52 | 151.652 | 153.161 | 155.179 | 154.399 |  | 1491.043 | 1588.546 |  | 7.0405 | 7.8455 | 7.6042 | 7.9263 | 7.1069 | 6.8628 | 6.6948 | 6.623 | 57.704 | 0.051934 |  | 62.069 | 100
19980511170000 | 1998-05-11 17:00 | 642.512 |  | 2.384 | 152.362 | 154.27 | 155.936 | 155.508 |  | 1500.793 | 1599.379 |  | 7.0144 | 7.814 | 7.554 | 7.8789 | 7.071 | 6.8284 | 6.6675 | 6.5881 | 57.4163 | 0.051675 |  | 62.069 | 100
19980511173000 | 1998-05-11 17:30 | 639.76 |  | 1.763 | 153.232 | 154.192 | 156.727 | 154.44 |  | 1505.46 | 1604.129 |  | 7.0305 | 7.8462 | 7.5881 | 7.9216 | 7.1099 | 6.8542 | 6.6963 | 6.6216 | 57.6684 | 0.051902 |  | 62.069 | 100
19980511180000 | 1998-05-11 18:00 | 642.119 |  | 3.361 | 152.493 | 152.733 | 155.802 | 153.971 |  | 1499.543 | 1601.296 |  | 6.9978 | 7.8096 | 7.5515 | 7.8721 | 7.0732 | 6.8208 | 6.6575 | 6.5933 | 57.3758 | 0.051638 |  | 62.069 | 100
19980511183000 | 1998-05-11 18:30 | 638.423 |  | 1.892 | 151.436 | 151.429 | 154.858 | 152.914 |  | 1488.626 | 1587.962 |  | 6.968 | 7.8088 | 7.5356 | 7.8713 | 7.0679 | 6.8215 | 6.6499 | 6.5842 | 57.3072 | 0.051576 |  | 62.069 | 100
19980511190000 | 1998-05-11 19:00 | 639.235 |  | 2.749 | 150.811 | 151.831 | 154.272 | 153.564 |  | 1500.46 | 1601.879 |  | 7.0168 | 7.8354 | 7.5662 | 7.9255 | 7.1052 | 6.8542 | 6.6895 | 6.6108 | 57.6036 | 0.051843 |  | 62.069 | 100
19980511193000 | 1998-05-11 19:30 | 639.707 |  | 1.52 | 150.787 | 150.269 | 154.34 | 152.744 |  | 1492.209 | 1590.129 |  | 6.9771 | 7.7974 | 7.5364 | 7.8811 | 7.0664 | 6.813 | 6.6499 | 6.5835 | 57.3048 | 0.051574 |  | 62.069 | 100
19980511200000 | 1998-05-11 20:00 | 639.707 |  | 2.626 | 150.268 | 150.712 | 153.672 | 151.95 |  | 1491.376 | 1587.712 |  | 6.9817 | 7.8118 | 7.5325 | 7.8843 | 7.0632 | 6.8176 | 6.6453 | 6.582 | 57.3184 | 0.051587 |  | 62.069 | 100
19980511203000 | 1998-05-11 20:30 | 639.078 |  | 1.768 | 150.076 | 150.634 | 153.233 | 152.12 |  | 1489.876 | 1587.296 |  | 6.9749 | 7.8064 | 7.5227 | 7.8821 | 7.0649 | 6.7986 | 6.6453 | 6.595 | 57.2899 | 0.051561 |  | 62.069 | 100
19980511210000 | 1998-05-11 21:00 | 641.097 |  | 3.486 | 150.049 | 149.711 | 152.43 | 149.216 |  | 1479.126 | 1577.045 |  | 7.0054 | 7.8416 | 7.5615 | 7.9163 | 7.0947 | 6.8452 | 6.6743 | 6.623 | 57.562 | 0.051806 |  | 62.069 | 100
19980511213000 | 1998-05-11 21:30 | 584.5 |  | 1.764 | 149.251 | 150.428 | 150.257 | 148.695 |  | 1370.956 | 1456.792 |  | 6.4331 | 7.312 | 6.9443 | 7.2144 | 6.5498 | 6.2866 | 6.1257 | 6.0654 | 52.9313 | 0.047638 |  | 62.069 | 100
19980511220000 | 1998-05-11 22:00 | 582.01 |  | 1.642 | 150.581 | 150.83 | 151.146 | 151.078 |  | 1358.956 | 1449.375 |  | 6.3333 | 7.2449 | 6.804 | 7.1008 | 6.4851 | 6.2058 | 6.0608 | 5.9792 | 52.2139 | 0.046993 |  | 62.069 | 100
19980511223000 | 1998-05-11 22:30 | 579.676 |  | 1.276 | 150.441 | 150.531 | 151.422 | 149.293 |  | 1364.706 | 1453.292 |  | 6.3599 | 7.2456 | 6.842 | 7.1152 | 6.4934 | 6.2219 | 6.0662 | 5.9846 | 52.3288 | 0.047096 |  | 62.069 | 100
19980511230000 | 1998-05-11 23:00 | 577.789 |  | 2.787 | 150.067 | 151.455 | 150.812 | 150.712 |  | 1364.039 | 1454.625 |  | 6.3477 | 7.238 | 6.8176 | 7.1084 | 6.4912 | 6.2043 | 6.0579 | 5.9778 | 52.2429 | 0.047019 |  | 62.069 | 100
19980511233000 | 1998-05-11 23:30 | 578.287 |  | 1.154 | 150.631 | 151.495 | 151.532 | 150.753 |  | 1363.206 | 1451.125 |  | 6.3423 | 7.2427 | 6.8176 | 7.0977 | 6.4819 | 6.2148 | 6.0586 | 5.9814 | 52.237 | 0.047013 |  | 62.069 | 100
19980512000000 | 1998-05-12 | 584.657 |  | 3.966 | 150.104 | 149.748 | 150.843 | 149.5 |  | 1336.955 | 1427.791 |  | 6.3857 | 7.2617 | 6.8696 | 7.1389 | 6.5149 | 6.2363 | 6.0906 | 5.9951 | 52.4928 | 0.047244 |  | 62.069 | 100
19980512003000 | 1998-05-12 00:30 | 487.612 |  | 0.785 | 149.714 | 148.943 | 150.415 | 148.448 |  | 1087.281 | 1170.45 |  | 5.1865 | 6.2112 | 5.5215 | 5.7397 | 5.4131 | 5.095 | 4.9934 | 4.9072 | 43.0676 | 0.038761 |  | 62.069 | 100
19980512010000 | 1998-05-12 01:00 | 453.638 |  | 1.889 | 148.791 | 149.855 | 149.28 | 148.123 |  | 993.279 | 1075.614 |  | 4.7905 | 5.8411 | 5.043 | 5.2705 | 5.0461 | 4.7432 | 4.6411 | 4.5234 | 39.8989 | 0.035909 |  | 62.069 | 100
19980512013000 | 1998-05-12 01:30 | 423.046 |  | 0.415 | 149.532 | 149.293 | 150.187 | 149.046 |  | 970.778 | 1047.28 |  | 4.6257 | 5.7595 | 4.8738 | 5.1406 | 4.9697 | 4.7144 | 4.5959 | 4.406 | 39.0856 | 0.035177 |  | 62.069 | 100
19980512020000 | 1998-05-12 02:00 | 423.675 |  | 16.316 | 149.736 | 150.568 | 150.62 | 150.568 |  | 975.945 | 1055.28 |  | 4.686 | 5.7632 | 4.9531 | 5.1833 | 4.9568 | 4.7058 | 4.6167 | 4.4243 | 39.2892 | 0.03536 |  | 62.069 | 100
19980512023000 | 1998-05-12 02:30 | 423.046 |  | 0.171 | 150.676 | 150.475 | 151.304 | 150.228 |  | 974.111 | 1046.28 |  | 4.6982 | 5.7534 | 4.9531 | 5.1865 | 4.9302 | 4.6838 | 4.615 | 4.4221 | 39.2423 | 0.035318 |  | 62.069 | 100
19980512030000 | 1998-05-12 03:00 | 424.226 |  | 3.72 | 150.58 | 150.383 | 151.695 | 150.383 |  | 970.195 | 1045.78 |  | 4.6821 | 5.7434 | 4.9629 | 5.2095 | 4.9202 | 4.6516 | 4.5984 | 4.4265 | 39.1946 | 0.035275 |  | 62.069 | 100
19980512033000 | 1998-05-12 03:30 | 425.903 |  | 0.291 | 150.689 | 150.785 | 151.444 | 150.043 |  | 964.278 | 1037.53 |  | 4.7866 | 5.8213 | 5.272 | 4.6028 | 4.9866 | 4.7083 | 4.6655 | 4.5144 | 39.3575 | 0.035422 |  | 62.069 | 100
19980512040000 | 1998-05-12 04:00 | 423.754 |  | 2.869 | 150.637 | 150.471 | 151.318 | 149.976 |  | 970.278 | 1048.28 |  | 4.6746 | 5.729 | 5.2246 | 5.2498 | 4.9104 | 4.574 | 4.5723 | 4.387 | 39.3217 | 0.03539 |  | 62.069 | 100
19980512043000 | 1998-05-12 04:30 | 419.9 |  | 0.412 | 150.361 | 149.677 | 151.071 | 148.934 |  | 965.778 | 1043.28 |  | 4.6602 | 5.7205 | 5.1995 | 5.2705 | 4.8982 | 4.5647 | 4.5747 | 4.3945 | 39.2828 | 0.035355 |  | 62.069 | 100
19980512050000 | 1998-05-12 05:00 | 426.428 |  | 2.132 | 149.962 | 151.265 | 150.783 | 150.275 |  | 955.194 | 1032.53 |  | 4.6418 | 5.6892 | 5.1667 | 5.2322 | 4.8691 | 4.5251 | 4.5327 | 4.3801 | 39.0369 | 0.035133 |  | 62.069 | 100
19980512053000 | 1998-05-12 05:30 | 427.66 |  | 0.784 | 150.62 | 149.858 | 151.654 | 149.858 |  | 965.778 | 1044.363 |  | 4.6357 | 5.6863 | 5.1804 | 5.2078 | 4.8684 | 4.5068 | 4.5273 | 4.3625 | 38.9752 | 0.035078 |  | 62.069 | 100
19980512060000 | 1998-05-12 06:00 | 472.565 |  | 2.746 | 150.899 | 152.88 | 151.863 | 151.147 |  | 1118.865 | 1198.034 |  | 5.2993 | 6.2959 | 5.9624 | 6.0859 | 5.4773 | 5.1675 | 5.1377 | 5.0073 | 44.4333 | 0.03999 |  | 62.069 | 100
19980512063000 | 1998-05-12 06:30 | 551.155 |  | 2.503 | 151.853 | 152.385 | 152.586 | 151.394 |  | 1314.371 | 1405.457 |  | 6.0967 | 7.0679 | 7.01 | 7.1138 | 6.2722 | 6.0029 | 5.8975 | 5.8091 | 51.2701 | 0.046143 |  | 62.069 | 100
19980512070000 | 1998-05-12 07:00 | 629.615 |  | 3.725 | 152.72 | 153.338 | 153.879 | 152.348 |  | 1484.626 | 1582.712 |  | 6.8643 | 7.7134 | 7.875 | 7.9766 | 6.9275 | 6.6934 | 6.5308 | 6.4736 | 57.0546 | 0.051349 |  | 62.069 | 100
19980512073000 | 1998-05-12 07:30 | 629.72 |  | 1.885 | 151.681 | 150.553 | 153.78 | 152.038 |  | 1477.459 | 1574.795 |  | 6.8933 | 7.7058 | 7.9629 | 7.9568 | 6.9961 | 6.6826 | 6.5759 | 6.4736 | 57.247 | 0.051522 |  | 62.069 | 100
19980512080000 | 1998-05-12 08:00 | 635.172 |  | 3.602 | 150.604 | 150.047 | 153.596 | 152.027 |  | 1474.542 | 1567.295 |  | 6.9177 | 7.7332 | 7.9841 | 7.9841 | 7.0259 | 6.7041 | 6.5918 | 6.5088 | 57.4497 | 0.051705 |  | 62.069 | 100
19980512083000 | 1998-05-12 08:30 | 637.479 |  | 14.974 | 150.292 | 151.222 | 153.165 | 151.47 |  | 1477.542 | 1574.462 |  | 6.9497 | 7.7385 | 8.0063 | 8.0049 | 7.0398 | 6.7085 | 6.5942 | 6.5088 | 57.5507 | 0.051796 |  | 62.069 | 100
19980512090000 | 1998-05-12 09:00 | 636.273 |  | 3.844 | 150.566 | 151.805 | 152.853 | 151.805 |  | 1481.792 | 1577.379 |  | 6.939 | 7.7546 | 8.0107 | 8.0132 | 7.0474 | 6.7139 | 6.6011 | 6.5178 | 57.5977 | 0.051838 |  | 62.069 | 100
19980512093000 | 1998-05-12 09:30 | 636.273 |  | 3.602 | 150.854 | 151.274 | 153.292 | 152.264 |  | 1479.542 | 1580.629 |  | 6.9473 | 7.7651 | 8.0171 | 8.0488 | 7.0603 | 6.7231 | 6.6125 | 6.5354 | 57.7096 | 0.051939 |  | 62.069 | 100
19980512100000 | 1998-05-12 10:00 | 636.168 |  | 1.885 | 150.635 | 151.48 | 153.691 | 152.718 |  | 1471.959 | 1570.378 |  | 6.9458 | 7.7683 | 8.0063 | 8.0391 | 7.0435 | 6.7124 | 6.604 | 6.5308 | 57.6502 | 0.051885 |  | 62.069 | 100
19980512103000 | 1998-05-12 10:30 | 639.524 |  | 1.762 | 150.715 | 151.924 | 154.167 | 153.657 |  | 1471.126 | 1567.045 |  | 6.9382 | 7.7439 | 7.9805 | 8.0054 | 7.0244 | 6.6873 | 6.5759 | 6.5078 | 57.4634 | 0.051717 |  | 62.069 | 100
19980512110000 | 1998-05-12 11:00 | 638.79 |  | 1.881 | 151.412 | 151.846 | 155.021 | 153.579 |  | 1470.042 | 1567.378 |  | 6.9214 | 7.7493 | 7.9941 | 8.0063 | 7.0266 | 6.6987 | 6.5781 | 6.5042 | 57.4787 | 0.051731 |  | 62.069 | 100
19980512113000 | 1998-05-12 11:30 | 639.996 |  | 2.129 | 151.704 | 153.254 | 155.395 | 153.749 |  | 1473.876 | 1570.462 |  | 6.9185 | 7.7263 | 7.9697 | 7.9858 | 7.0176 | 6.6858 | 6.5645 | 6.4949 | 57.3631 | 0.051627 |  | 62.069 | 100
19980512120000 | 1998-05-12 12:00 | 640.467 |  | 2.129 | 151.901 | 153.398 | 155.675 | 153.398 |  | 1470.209 | 1565.878 |  | 6.9199 | 7.7439 | 7.9797 | 7.9971 | 7.0413 | 6.7017 | 6.5835 | 6.511 | 57.4781 | 0.05173 |  | 62.069 | 100
19980512123000 | 1998-05-12 12:30 | 646.208 |  | 2.251 | 151.973 | 153.176 | 155.614 | 153.919 |  | 1471.209 | 1564.295 |  | 6.9092 | 7.7363 | 7.9858 | 7.9949 | 7.0251 | 6.6873 | 6.5759 | 6.4941 | 57.4086 | 0.051668 |  | 62.069 | 100
19980512130000 | 1998-05-12 13:00 | 642.302 |  | 2.373 | 152.234 | 153.372 | 155.928 | 153.62 |  | 1474.876 | 1569.962 |  | 6.9055 | 7.7439 | 7.9849 | 7.9963 | 7.0298 | 6.6934 | 6.582 | 6.4988 | 57.4346 | 0.051691 |  | 62.069 | 100
19980512133000 | 1998-05-12 13:30 | 639.655 |  | 21.792 | 152.893 | 154.636 | 156.586 | 156.121 |  | 1481.126 | 1574.129 |  | 6.9124 | 7.7371 | 7.9919 | 7.9934 | 7.0237 | 6.6941 | 6.5759 | 6.5078 | 57.4363 | 0.051693 |  | 62.069 | 100
19980512140000 | 1998-05-12 14:00 | 637.898 |  | 3.596 | 153.612 | 153.971 | 157.337 | 155.456 |  | 1476.709 | 1573.129 |  | 6.9124 | 7.7468 | 7.991 | 7.9934 | 7.0388 | 6.7056 | 6.5828 | 6.511 | 57.4818 | 0.051734 |  | 62.069 | 100
19980512143000 | 1998-05-12 14:30 | 638.423 |  | 2.375 | 153.782 | 155.064 | 157.564 | 156.797 |  | 1481.209 | 1575.379 |  | 6.8833 | 7.7034 | 7.9507 | 7.9658 | 7.0007 | 6.6682 | 6.5483 | 6.4766 | 57.197 | 0.051477 |  | 62.069 | 100
19980512150000 | 1998-05-12 15:00 | 636.378 |  | 2.867 | 154.019 | 155.312 | 157.841 | 156.797 |  | 1478.792 | 1578.045 |  | 6.9077 | 7.7317 | 8.001 | 7.9773 | 7.0251 | 6.6858 | 6.5759 | 6.5002 | 57.4047 | 0.051664 |  | 62.069 | 100
19980512153000 | 1998-05-12 15:30 | 597.843 |  | 1.64 | 154.4 | 154.399 | 158.259 | 156.132 |  | 1339.538 | 1430.041 |  | 6.3362 | 7.1863 | 7.3213 | 7.2822 | 6.4636 | 6.0959 | 6.0288 | 5.9341 | 52.6484 | 0.047384 |  | 62.069 | 100
19980512160000 | 1998-05-12 16:00 | 588.773 |  | 2.13 | 152.078 | 150.568 | 155.594 | 152.053 |  | 1344.872 | 1433.208 |  | 6.2769 | 7.1504 | 7.2517 | 7.1914 | 6.4316 | 6.0715 | 5.9861 | 5.8931 | 52.2527 | 0.047027 |  | 62.069 | 100
19980512163000 | 1998-05-12 16:30 | 580.909 |  | 21.432 | 150.042 | 151.61 | 153.269 | 151.362 |  | 1325.621 | 1414.624 |  | 6.2148 | 7.1853 | 7.1755 | 7.2129 | 6.4102 | 6.1067 | 5.9617 | 5.8999 | 52.167 | 0.04695 |  | 62.069 | 100
19980512170000 | 1998-05-12 17:00 | 579.441 |  | 2.009 | 150.583 | 150.919 | 152.858 | 150.919 |  | 1340.038 | 1430.124 |  | 6.2234 | 7.2136 | 7.2075 | 7.2456 | 6.4446 | 6.1563 | 6.0037 | 5.9204 | 52.4151 | 0.047174 |  | 62.069 | 100
19980512173000 | 1998-05-12 17:30 | 633.547 |  | 2.133 | 152.337 | 156.091 | 154.979 | 157.081 |  | 1470.292 | 1568.795 |  | 6.8611 | 7.7454 | 7.9087 | 7.9858 | 6.99 | 6.7139 | 6.543 | 6.5002 | 57.2481 | 0.051523 |  | 62.069 | 100
19980512180000 | 1998-05-12 18:00 | 635.382 |  | 2.618 | 154.605 | 156.117 | 157.948 | 156.86 |  | 1468.375 | 1566.962 |  | 6.8718 | 7.7561 | 7.9209 | 8.0137 | 6.9932 | 6.7131 | 6.5498 | 6.5149 | 57.3335 | 0.0516 |  | 62.069 | 100
19980512183000 | 1998-05-12 18:30 | 627.308 |  | 2.005 | 155.171 | 156.039 | 158.732 | 157.277 |  | 1440.541 | 1538.377 |  | 7.0076 | 7.8933 | 8.0869 | 8.1787 | 7.1206 | 4.7754 | 6.6758 | 6.6582 | 56.3965 | 0.050757 |  | 62.069 | 100
19980512190000 | 1998-05-12 19:00 | 632.341 |  | 2.745 | 154.968 | 155.493 | 158.876 | 157.721 |  | 1457.792 | 1551.961 |  | 7.0337 | 7.9224 | 8.1123 | 8.2104 | 7.1497 | 4.8013 | 6.7024 | 6.6865 | 56.6187 | 0.050957 |  | 62.069 | 100
19980512193000 | 1998-05-12 19:30 | 634.543 |  | 2.375 | 154.588 | 156.132 | 158.642 | 157.865 |  | 1464.625 | 1559.211 |  | 7.0825 | 7.9583 | 8.165 | 8.251 | 7.1885 | 4.8203 | 6.7354 | 6.7261 | 56.9271 | 0.051234 |  | 62.069 | 100
19980512200000 | 1998-05-12 20:00 | 585.313 |  | 2.374 | 153.411 | 150.634 | 157.262 | 151.872 |  | 1343.539 | 1429.958 |  | 6.5232 | 7.438 | 7.5249 | 7.5637 | 6.6467 | 4.4365 | 6.2051 | 6.199 | 52.5371 | 0.047283 |  | 62.069 | 100
19980512203000 | 1998-05-12 20:30 | 578.811 |  | 1.764 | 150.353 | 151.274 | 153.751 | 151.769 |  | 1337.955 | 1428.041 |  | 6.4636 | 7.4243 | 7.46 | 7.5403 | 6.6299 | 4.4214 | 6.1875 | 6.1624 | 52.2894 | 0.04706 |  | 62.069 | 100
19980512210000 | 1998-05-12 21:00 | 564.761 |  | 2.009 | 151.085 | 151.521 | 154.085 | 153.006 |  | 1270.62 | 1363.622 |  | 6.2087 | 7.126 | 7.116 | 7.1526 | 6.3171 | 4.1938 | 5.8823 | 5.8601 | 49.8566 | 0.044871 |  | 62.069 | 100
19980512213000 | 1998-05-12 21:30 | 539.936 |  | 1.023 | 149.602 | 148.876 | 152.385 | 147.391 |  | 1236.619 | 1319.455 |  | 5.7488 | 6.739 | 6.5774 | 6.6101 | 5.929 | 5.6221 | 5.5107 | 5.4468 | 48.1839 | 0.043366 |  | 62.069 | 100
19980512220000 | 1998-05-12 22:00 | 580.673 |  | 2.005 | 149.731 | 153.852 | 149.487 | 150.139 |  | 1327.788 | 1418.374 |  | 6.2532 | 7.1748 | 7.1619 | 7.2334 | 6.4019 | 6.1096 | 5.9724 | 5.9097 | 52.2169 | 0.046995 |  | 62.069 | 100
19980512223000 | 1998-05-12 22:30 | 580.673 |  | 1.269 | 151.456 | 150.557 | 151.112 | 150.062 |  | 1329.038 | 1419.707 |  | 6.2783 | 7.2097 | 7.2212 | 7.2793 | 6.4385 | 6.1523 | 6.0066 | 5.9534 | 52.5393 | 0.047285 |  | 62.069 | 100
19980512230000 | 1998-05-12 23:00 | 581.616 |  | 1.516 | 150.414 | 150.479 | 151.335 | 149.984 |  | 1333.122 | 1421.791 |  | 6.2256 | 7.1892 | 7.187 | 7.2524 | 6.4111 | 6.1211 | 5.9761 | 5.9243 | 52.2868 | 0.047058 |  | 62.069 | 100
19980512233000 | 1998-05-12 23:30 | 578.444 |  | 1.27 | 150.049 | 150.546 | 151.048 | 149.556 |  | 1330.872 | 1419.124 |  | 6.2288 | 7.2 | 7.1853 | 7.2517 | 6.4202 | 6.1326 | 5.9822 | 5.9297 | 52.3305 | 0.047097 |  | 62.069 | 100
19980513000000 | 1998-05-13 | 487.795 |  | 0.78 | 149.879 | 148.381 | 150.128 | 145.411 |  | 1084.865 | 1167.533 |  | 5.166 | 6.2209 | 5.8923 | 5.8923 | 5.4009 | 5.0691 | 4.9607 | 4.8799 | 43.4821 | 0.039134 |  | 62.069 | 100
19980513003000 | 1998-05-13 00:30 | 483.155 |  | 0.29 | 148.441 | 149.371 | 145.703 | 141.451 |  | 1064.614 | 1143.949 |  | 5.0789 | 6.1738 | 5.761 | 5.8267 | 5.3994 | 5.0972 | 4.9768 | 4.8616 | 43.1754 | 0.038858 |  | 62.069 | 100
19980513010000 | 1998-05-13 01:00 | 481.609 |  | 0.657 | 149.753 | 150.83 | 143.402 | 142.168 |  | 1071.697 | 1151.533 |  | 5.2903 | 5.989 | 5.5168 | 6.1082 | 5.1667 | 5.3064 | 5.1865 | 4.8599 | 43.4238 | 0.039081 |  | 62.069 | 100
19980513013000 | 1998-05-13 01:30 | 450.099 |  | 0.411 | 150.649 | 150.387 | 143.551 | 142.219 |  | 992.279 | 1071.781 |  | 5.0408 | 5.6619 | 5.1284 | 4.8501 | 4.8096 | 4.9553 | 4.8645 | 4.5327 | 39.8433 | 0.035859 |  | 62.069 | 100
19980513020000 | 1998-05-13 02:00 | 416.912 |  | 0.655 | 150.091 | 150.243 | 143.698 | 142.818 |  | 972.195 | 1053.364 |  | 3.4883 | 5.6116 | 5.0476 | 4.8303 | 4.7661 | 4.9707 | 4.8623 | 4.5083 | 38.0852 | 0.034277 |  | 62.069 | 100
19980513023000 | 1998-05-13 02:30 | 424.147 |  | 0.291 | 150.523 | 150.671 | 143.488 | 140.276 |  | 972.445 | 1053.864 |  | 1.304 | 5.8853 | 5.4138 | 5.1934 | 4.9775 | 5.104 | 4.9919 | 4.7363 | 37.6062 | 0.033846 |  | 62.069 | 100
19980513030000 | 1998-05-13 03:00 | 420.136 |  | 0.657 | 150.029 | 149.016 | 142.717 | 141.096 |  | 967.028 | 1046.447 |  | 4.9768 | 5.5061 | 4.9004 | 4.7058 | 4.6357 | 4.8318 | 4.731 | 4.3823 | 38.6699 | 0.034803 |  | 62.069 | 100
19980513033000 | 1998-05-13 03:30 | 414.081 |  | 0.292 | 149.723 | 150.682 | 143.15 | 142.514 |  | 972.695 | 1049.78 |  | 5.0042 | 5.5208 | 4.96 | 4.7546 | 4.6616 | 4.8264 | 4.7334 | 4.4067 | 38.8677 | 0.034981 |  | 62.069 | 100
19980513040000 | 1998-05-13 04:00 | 418.406 |  | 20.954 | 150.492 | 148.872 | 143.72 | 140.457 |  | 948.611 | 1024.446 |  | 4.937 | 5.4978 | 4.8486 | 4.6846 | 4.5913 | 4.7859 | 4.6997 | 4.377 | 38.4219 | 0.03458 |  | 62.069 | 100
19980513043000 | 1998-05-13 04:30 | 420.425 |  | 0.415 | 149.377 | 150.564 | 142.153 | 141.406 |  | 950.777 | 1030.78 |  | 4.9646 | 5.4895 | 4.8875 | 4.6875 | 4.6218 | 4.792 | 4.7065 | 4.3794 | 38.5288 | 0.034676 |  | 62.069 | 100
19980513050000 | 1998-05-13 05:00 | 422.024 |  | 0.415 | 150.427 | 150.929 | 143.304 | 143.257 |  | 946.694 | 1027.78 |  | 4.9453 | 5.4788 | 4.863 | 4.6799 | 4.5959 | 4.7683 | 4.6807 | 4.3579 | 38.3698 | 0.034533 |  | 62.069 | 100
19980513053000 | 1998-05-13 05:30 | 420.897 |  | 0.166 | 151.042 | 150.068 | 144.232 | 142.149 |  | 952.777 | 1037.946 |  | 4.969 | 5.5222 | 4.9019 | 4.731 | 4.625 | 4.8059 | 4.731 | 4.4021 | 38.6881 | 0.034819 |  | 62.069 | 100
19980513060000 | 1998-05-13 06:00 | 418.537 |  | 0.539 | 150.636 | 150.12 | 143.61 | 142.943 |  | 958.278 | 1041.447 |  | 4.9622 | 5.5068 | 4.8928 | 4.7065 | 4.6311 | 4.783 | 4.7195 | 4.3909 | 38.5928 | 0.034734 |  | 62.069 | 100
19980513063000 | 1998-05-13 06:30 | 520.118 |  | 0.905 | 150.853 | 154.199 | 144.131 | 144.793 |  | 1188.701 | 1274.62 |  | 6.0249 | 6.5271 | 6.3171 | 6.1714 | 5.6816 | 5.7869 | 5.6633 | 5.4336 | 47.6059 | 0.042845 |  | 62.069 | 100
19980513070000 | 1998-05-13 07:00 | 522.87 |  | 21.086 | 152.25 | 150.553 | 146.054 | 144.612 |  | 1197.701 | 1280.37 |  | 5.9937 | 6.4934 | 6.2371 | 6.0967 | 5.6604 | 5.752 | 5.626 | 5.3901 | 47.2494 | 0.042524 |  | 62.069 | 100
19980513073000 | 1998-05-13 07:30 | 519.646 |  | 0.535 | 150.581 | 149.603 | 145.754 | 143.168 |  | 1172.867 | 1256.203 |  | 6.0134 | 6.53 | 6.2668 | 6.1365 | 5.6816 | 5.79 | 5.6604 | 5.4224 | 47.5011 | 0.042751 |  | 62.069 | 100
19980513080000 | 1998-05-13 08:00 | 523.158 |  | 0.782 | 149.905 | 150.583 | 144.881 | 143.405 |  | 1173.117 | 1256.703 |  | 6.0432 | 6.5354 | 6.2759 | 6.1074 | 5.7031 | 5.7808 | 5.6472 | 5.4192 | 47.5122 | 0.042761 |  | 62.069 | 100
19980513083000 | 1998-05-13 08:30 | 614.253 |  | 1.888 | 151.472 | 154.141 | 146.182 | 149.685 |  | 1406.707 | 1505.46 |  | 6.9558 | 7.4456 | 7.4829 | 7.4075 | 6.6467 | 6.7056 | 6.53 | 6.3667 | 55.5408 | 0.049987 |  | 62.069 | 100
19980513090000 | 1998-05-13 09:00 | 639.104 |  | 2.87 | 152.339 | 151.299 | 150.949 | 151.299 |  | 1467.625 | 1563.462 |  | 7.2869 | 7.7424 | 7.8721 | 7.782 | 6.9512 | 6.9885 | 6.8237 | 6.6597 | 58.1065 | 0.052296 |  | 62.069 | 100
19980513093000 | 1998-05-13 09:30 | 640.363 |  | 2.006 | 151.198 | 151.573 | 152.718 | 151.82 |  | 1468.375 | 1565.545 |  | 7.2571 | 7.7295 | 7.8394 | 7.7568 | 6.9307 | 6.9626 | 6.7957 | 6.6482 | 57.92 | 0.052128 |  | 62.069 | 100
19980513100000 | 1998-05-13 10:00 | 638.475 |  | 2.012 | 151.08 | 152.393 | 152.491 | 153.136 |  | 1470.542 | 1568.962 |  | 7.261 | 7.731 | 7.8416 | 7.7507 | 6.9321 | 6.9656 | 6.7878 | 6.6421 | 57.9119 | 0.052121 |  | 62.069 | 100
19980513103000 | 1998-05-13 10:30 | 638.134 |  | 1.885 | 151.566 | 152.315 | 154.354 | 153.553 |  | 1467.625 | 1568.878 |  | 7.2571 | 7.7202 | 7.843 | 7.7576 | 6.9336 | 6.9641 | 6.7939 | 6.6506 | 57.9201 | 0.052128 |  | 62.069 | 100
19980513110000 | 1998-05-13 11:00 | 639.288 |  | 2.007 | 151.881 | 153.461 | 155.049 | 154.203 |  | 1469.125 | 1568.295 |  | 7.2563 | 7.7058 | 7.8247 | 7.7295 | 6.9167 | 6.9429 | 6.7612 | 6.6353 | 57.7724 | 0.051995 |  | 62.069 | 100
19980513113000 | 1998-05-13 11:30 | 641.07 |  | 2.007 | 152.225 | 153.006 | 155.507 | 153.997 |  | 1465.625 | 1561.295 |  | 7.2678 | 7.7065 | 7.853 | 7.75 | 6.9207 | 6.9382 | 6.7581 | 6.627 | 57.8213 | 0.052039 |  | 62.069 | 100
19980513120000 | 1998-05-13 12:00 | 639.655 |  | 2.623 | 152.481 | 153.243 | 155.765 | 153.243 |  | 1464.375 | 1559.211 |  | 7.2488 | 7.699 | 7.8232 | 7.7209 | 6.9106 | 6.9351 | 6.7458 | 6.6162 | 57.6996 | 0.05193 |  | 62.069 | 100
19980513123000 | 1998-05-13 12:30 | 645.658 |  | 2.006 | 152.397 | 153.631 | 155.894 | 154.868 |  | 1456.375 | 1552.878 |  | 7.229 | 7.6807 | 7.8042 | 7.7041 | 6.8862 | 6.9146 | 6.7346 | 6.6011 | 57.5545 | 0.051799 |  | 62.069 | 100
19980513130000 | 1998-05-13 13:00 | 642.879 |  | 2.863 | 152.627 | 154.27 | 156.19 | 154.27 |  | 1470.792 | 1571.795 |  | 7.2617 | 7.7126 | 7.8567 | 7.7095 | 6.9229 | 6.9321 | 6.7529 | 6.6194 | 57.7678 | 0.051991 |  | 62.069 | 100
19980513133000 | 1998-05-13 13:30 | 638.895 |  | 2.614 | 153.405 | 154.037 | 156.74 | 155.028 |  | 1482.793 | 1578.795 |  | 7.2678 | 7.7095 | 7.8491 | 7.7263 | 6.9246 | 6.9443 | 6.7605 | 6.6316 | 57.8137 | 0.052032 |  | 62.069 | 100
19980513140000 | 1998-05-13 14:00 | 639.34 |  | 2.865 | 153.955 | 155.079 | 157.292 | 156.317 |  | 1474.792 | 1570.462 |  | 7.2646 | 7.7095 | 7.856 | 7.7324 | 6.9307 | 6.9421 | 6.7666 | 6.6392 | 57.8411 | 0.052057 |  | 62.069 | 100
19980513143000 | 1998-05-13 14:30 | 641.254 |  | 2.619 | 154.166 | 155.249 | 157.433 | 155.497 |  | 1471.709 | 1568.295 |  | 7.2571 | 7.6919 | 7.8254 | 7.7263 | 6.9055 | 6.9421 | 6.7444 | 6.6255 | 57.7182 | 0.051946 |  | 62.069 | 100
19980513150000 | 1998-05-13 15:00 | 637.505 |  | 3.111 | 154.109 | 154.063 | 157.445 | 154.311 |  | 1461.709 | 1559.045 |  | 7.2273 | 7.6631 | 7.8096 | 7.7004 | 6.8801 | 6.9116 | 6.7354 | 6.6018 | 57.5293 | 0.051776 |  | 62.069 | 100
19980513153000 | 1998-05-13 15:30 | 638.475 |  | 2.496 | 153.873 | 155.497 | 157.205 | 156.239 |  | 1469.875 | 1567.212 |  | 7.2488 | 7.6851 | 7.8271 | 7.7324 | 6.9045 | 6.926 | 6.772 | 6.6187 | 57.7146 | 0.051943 |  | 62.069 | 100
19980513160000 | 1998-05-13 16:00 | 640.363 |  | 3.355 | 154.431 | 156.265 | 157.85 | 157.255 |  | 1479.042 | 1575.879 |  | 7.2158 | 7.6516 | 7.8018 | 7.6545 | 6.875 | 6.8879 | 6.7224 | 6.5681 | 57.3771 | 0.051639 |  | 62.069 | 100
19980513163000 | 1998-05-13 16:30 | 637.269 |  | 2.74 | 155.333 | 156.343 | 158.755 | 157.085 |  | 1478.876 | 1575.879 |  | 7.2205 | 7.6545 | 7.8027 | 7.679 | 6.8811 | 6.9038 | 6.7397 | 6.5864 | 57.4677 | 0.051721 |  | 62.069 | 100
19980513170000 | 1998-05-13 17:00 | 636.194 |  | 3.97 | 154.836 | 155.105 | 158.222 | 155.105 |  | 1477.542 | 1573.712 |  | 7.2373 | 7.6646 | 7.8003 | 7.6624 | 6.8962 | 6.9023 | 6.7458 | 6.5864 | 57.4953 | 0.051746 |  | 62.069 | 100
19980513173000 | 1998-05-13 17:30 | 633.547 |  | 3.108 | 154.075 | 154.595 | 157.422 | 155.09 |  | 1478.792 | 1577.712 |  | 7.2036 | 7.6584 | 7.7844 | 7.6523 | 6.874 | 6.9023 | 6.7383 | 6.5789 | 57.3922 | 0.051653 |  | 62.069 | 100
19980513180000 | 1998-05-13 18:00 | 636.509 |  | 3.476 | 153.735 | 154.477 | 157.132 | 155.467 |  | 1474.792 | 1572.795 |  | 7.2229 | 7.6631 | 7.7888 | 7.6484 | 6.875 | 6.9016 | 6.7512 | 6.5811 | 57.4321 | 0.051689 |  | 62.069 | 100
19980513183000 | 1998-05-13 18:30 | 641.385 |  | 20.697 | 153.447 | 154.332 | 156.821 | 155.323 |  | 1473.209 | 1569.795 |  | 7.2007 | 7.6379 | 7.7766 | 7.6746 | 6.8582 | 6.8794 | 6.7214 | 6.5637 | 57.3125 | 0.051581 |  | 62.069 | 100
19980513190000 | 1998-05-13 19:00 | 633.809 |  | 3.113 | 153.159 | 153.446 | 156.459 | 154.683 |  | 1472.542 | 1567.295 |  | 7.1975 | 7.6501 | 7.7805 | 7.6492 | 6.865 | 6.8811 | 6.7231 | 6.5645 | 57.311 | 0.05158 |  | 62.069 | 100
19980513193000 | 1998-05-13 19:30 | 632.262 |  | 2.739 | 152.5 | 152.951 | 155.878 | 154.188 |  | 1472.709 | 1569.962 |  | 7.2388 | 7.6882 | 7.8103 | 7.689 | 6.9023 | 6.9282 | 6.7688 | 6.604 | 57.6296 | 0.051867 |  | 62.069 | 100
19980513200000 | 1998-05-13 20:00 | 638.161 |  | 3.237 | 151.755 | 151.909 | 155.029 | 153.146 |  | 1465.459 | 1562.795 |  | 7.2419 | 7.689 | 7.8254 | 7.7112 | 6.9001 | 6.9429 | 6.7825 | 6.6223 | 57.7153 | 0.051944 |  | 62.069 | 100
19980513203000 | 1998-05-13 20:30 | 637.846 |  | 2.738 | 151.403 | 152.275 | 154.644 | 153.017 |  | 1465.125 | 1558.545 |  | 7.2388 | 7.7034 | 7.7996 | 7.7371 | 6.8862 | 6.949 | 6.7856 | 6.6284 | 57.7281 | 0.051955 |  | 62.069 | 100
19980513210000 | 1998-05-13 21:00 | 638.161 |  | 3.602 | 151.619 | 152.537 | 154.738 | 152.785 |  | 1466.792 | 1560.961 |  | 7.2075 | 7.6729 | 7.7844 | 7.7034 | 6.8535 | 6.9092 | 6.7559 | 6.595 | 57.4818 | 0.051734 |  | 62.069 | 100
19980513213000 | 1998-05-13 21:30 | 573.385 |  | 1.303 | 151.515 | 150.232 | 154.651 | 150.479 |  | 1357.289 | 1443.458 |  | 6.6736 | 7.1587 | 7.1199 | 6.9917 | 6.3423 | 6.3867 | 6.2332 | 6.0632 | 52.9693 | 0.047672 |  | 62.069 | 100
19980513220000 | 1998-05-13 22:00 | 616.403 |  | 3.48 | 149.685 | 151.34 | 152.048 | 149.113 |  | 1477.209 | 1574.462 |  | 7.1328 | 7.6272 | 7.6858 | 7.6423 | 6.8123 | 6.8916 | 6.7063 | 6.5613 | 57.0596 | 0.051354 |  | 62.069 | 100
19980513223000 | 1998-05-13 22:30 | 630.218 |  | 2.373 | 151.549 | 152.341 | 153.062 | 152.341 |  | 1461.042 | 1557.461 |  | 7.1626 | 7.6248 | 7.7346 | 7.6492 | 6.8169 | 6.8779 | 6.7041 | 6.5522 | 57.1223 | 0.05141 |  | 62.069 | 100
19980513230000 | 1998-05-13 23:00 | 631.686 |  | 2.865 | 151.552 | 152.275 | 154.149 | 152.77 |  | 1469.292 | 1565.045 |  | 7.1619 | 7.6135 | 7.7324 | 7.6104 | 6.8384 | 6.8535 | 6.6858 | 6.5225 | 57.0184 | 0.051317 |  | 62.069 | 100
19980513233000 | 1998-05-13 23:30 | 532.098 |  | 1.024 | 149.976 | 146.478 | 152.074 | 143.261 |  | 1225.702 | 1308.038 |  | 6.2219 | 6.7185 | 6.5332 | 6.3423 | 5.8984 | 5.9441 | 5.8159 | 5.626 | 49.1003 | 0.04419 |  | 62.069 | 100
19980514000000 | 1998-05-14 | 478.358 |  | 1.027 | 148.054 | 148.396 | 145.151 | 139.487 |  | 1089.448 | 1165.95 |  | 5.6572 | 6.1958 | 5.7793 | 5.5603 | 5.3359 | 5.4543 | 5.3237 | 5.0842 | 44.3907 | 0.039952 |  | 62.069 | 100
19980514003000 | 1998-05-14 00:30 | 425.038 |  | 0.293 | 149.248 | 150.243 | 142.692 | 139.848 |  | 937.944 | 1010.779 |  | 4.9751 | 5.4932 | 4.8767 | 4.5769 | 4.6326 | 4.8013 | 4.7119 | 4.3953 | 38.463 | 0.034617 |  | 62.069 | 100
19980514010000 | 1998-05-14 01:00 | 422.732 |  | 2.864 | 149.273 | 149.969 | 142.184 | 141.802 |  | 959.778 | 1037.113 |  | 5.0896 | 5.6299 | 5.0483 | 4.8486 | 4.7676 | 4.9783 | 4.863 | 4.5144 | 39.7397 | 0.035766 |  | 62.069 | 100
19980514013000 | 1998-05-14 01:30 | 418.642 |  | 0.168 | 150.075 | 150.439 | 143.08 | 141.776 |  | 951.277 | 1035.53 |  | 5.0537 | 5.5671 | 4.9722 | 4.8074 | 4.7065 | 4.8896 | 4.7966 | 4.4663 | 39.2594 | 0.035333 |  | 62.069 | 100
19980514020000 | 1998-05-14 02:00 | 423.597 |  | 0.662 | 150.775 | 151.114 | 143.67 | 142.699 |  | 953.111 | 1037.113 |  | 5.0515 | 5.5984 | 5.0049 | 4.8455 | 4.7288 | 4.9072 | 4.8181 | 4.4885 | 39.4429 | 0.035499 |  | 62.069 | 100
19980514023000 | 1998-05-14 02:30 | 403.097 |  | 0.537 | 150.676 | 150.867 | 143.817 | 142.699 |  | 899.276 | 986.195 |  | 4.908 | 5.4224 | 4.821 | 4.5837 | 4.551 | 4.6929 | 3.2014 | 4.3062 | 36.4866 | 0.032838 |  | 62.069 | 100
19980514030000 | 1998-05-14 03:00 | 369.7 |  | 0.538 | 149.852 | 148.783 | 142.888 | 139.874 |  | 857.525 | 943.61 |  | 4.7639 | 5.2673 | 4.667 | 4.3953 | 4.4053 | 4.5974 | 3.2465 | 4.1626 | 35.5053 | 0.031955 |  | 62.069 | 100
19980514033000 | 1998-05-14 03:30 | 370.434 |  | 0.292 | 149.902 | 150.279 | 142.945 | 143.102 |  | 851.191 | 931.943 |  | 4.512 | 5.0698 | 4.3167 | 4.0886 | 4.1946 | 4.4121 | 4.4763 | 3.9689 | 35.039 | 0.031535 |  | 62.069 | 100
19980514040000 | 1998-05-14 04:00 | 372.348 |  | 1.89 | 150.445 | 150.383 | 143.435 | 141.473 |  | 849.524 | 924.693 |  | 4.5015 | 5.0522 | 4.2793 | 4.0857 | 4.1633 | 4.3611 | 4.457 | 3.9597 | 34.8598 | 0.031374 |  | 62.069 | 100
19980514043000 | 1998-05-14 04:30 | 373.894 |  | 0.293 | 150.715 | 149.888 | 143.517 | 142.215 |  | 854.691 | 931.86 |  | 4.5181 | 5.0522 | 4.332 | 4.0933 | 4.1802 | 4.3374 | 4.4465 | 3.962 | 34.9217 | 0.03143 |  | 62.069 | 100
19980514050000 | 1998-05-14 05:00 | 370.644 |  | 3.477 | 150.557 | 150.434 | 143.709 | 143.257 |  | 840.441 | 918.276 |  | 4.4893 | 5.0637 | 4.28 | 4.1145 | 4.1772 | 4.3289 | 4.4519 | 3.9559 | 34.8614 | 0.031375 |  | 62.069 | 100
19980514053000 | 1998-05-14 05:30 | 373.737 |  | 0.293 | 150.569 | 150.264 | 143.562 | 141.354 |  | 852.691 | 928.027 |  | 4.4656 | 5.011 | 4.271 | 4.0452 | 4.1306 | 4.2793 | 4.397 | 3.9414 | 34.5411 | 0.031087 |  | 62.069 | 100
19980514060000 | 1998-05-14 06:00 | 371.352 |  | 1.274 | 150.157 | 149.821 | 142.93 | 142.149 |  | 852.191 | 928.693 |  | 4.4915 | 5.072 | 4.2969 | 4.1428 | 4.1658 | 4.3245 | 4.4487 | 3.9926 | 34.9348 | 0.031441 |  | 62.069 | 100
19980514063000 | 1998-05-14 06:30 | 511.336 |  | 1.523 | 151.465 | 154.772 | 144.854 | 146.108 |  | 1199.534 | 1283.037 |  | 6.0586 | 6.543 | 6.3096 | 6.1975 | 5.7183 | 5.7869 | 5.9075 | 5.4695 | 47.9909 | 0.043192 |  | 62.069 | 100
19980514070000 | 1998-05-14 07:00 | 608.591 |  | 3.359 | 154.047 | 152.899 | 149.1 | 151.661 |  | 1419.707 | 1518.71 |  | 6.9749 | 7.4448 | 7.467 | 7.4233 | 6.6377 | 6.7163 | 6.781 | 6.395 | 55.84 | 0.050256 |  | 62.069 | 100
19980514073000 | 1998-05-14 07:30 | 634.045 |  | 2.375 | 152.571 | 153.006 | 152.838 | 152.511 |  | 1462.209 | 1562.212 |  | 7.1853 | 7.6309 | 7.7363 | 7.6638 | 6.8445 | 6.8855 | 6.9543 | 6.5742 | 57.4748 | 0.051727 |  | 62.069 | 100
19980514080000 | 1998-05-14 08:00 | 632.76 |  | 2.868 | 152.101 | 152.094 | 154.149 | 152.589 |  | 1467.125 | 1561.712 |  | 7.1396 | 7.592 | 7.6882 | 7.5981 | 6.8008 | 6.8459 | 6.9099 | 6.5437 | 57.1182 | 0.051406 |  | 62.069 | 100
19980514083000 | 1998-05-14 08:30 | 635.827 |  | 2.253 | 151.641 | 151.558 | 154.207 | 151.805 |  | 1456.042 | 1553.378 |  | 7.2007 | 7.6348 | 7.7881 | 7.6858 | 6.8635 | 6.8984 | 6.981 | 6.6169 | 57.6692 | 0.051902 |  | 62.069 | 100
19980514090000 | 1998-05-14 09:00 | 636.011 |  | 20.472 | 151.34 | 152.378 | 153.604 | 152.13 |  | 1464.709 | 1561.545 |  | 7.2419 | 7.6714 | 7.8308 | 7.7209 | 6.9146 | 6.9375 | 7.0154 | 6.6589 | 57.9914 | 0.052192 |  | 62.069 | 100
19980514093000 | 1998-05-14 09:30 | 637.977 |  | 2.498 | 151.036 | 151.975 | 153.583 | 151.975 |  | 1463.042 | 1561.712 |  | 7.1985 | 7.6125 | 7.7583 | 7.6858 | 6.8528 | 6.8772 | 6.9634 | 6.6072 | 57.5557 | 0.0518 |  | 62.069 | 100
19980514100000 | 1998-05-14 10:00 | 637.715 |  | 2.496 | 151.582 | 152.6 | 154.196 | 153.342 |  | 1456.208 | 1553.211 |  | 7.1687 | 7.5981 | 7.7173 | 7.6577 | 6.8269 | 6.8521 | 6.939 | 6.5986 | 57.3584 | 0.051623 |  | 62.069 | 100
19980514103000 | 1998-05-14 10:30 | 640.441 |  | 2.13 | 151.695 | 153.032 | 154.879 | 153.775 |  | 1454.875 | 1546.294 |  | 7.1626 | 7.5784 | 7.731 | 7.6279 | 6.8176 | 6.8398 | 6.9321 | 6.575 | 57.2644 | 0.051538 |  | 62.069 | 100
19980514110000 | 1998-05-14 11:00 | 639.235 |  | 2.867 | 151.95 | 152.759 | 155.365 | 154.492 |  | 1463.209 | 1560.545 |  | 7.1641 | 7.5974 | 7.7195 | 7.605 | 6.8359 | 6.8467 | 6.9404 | 6.5872 | 57.2962 | 0.051567 |  | 62.069 | 100
19980514113000 | 1998-05-14 11:30 | 638.239 |  | 2.372 | 152.483 | 153.435 | 156.076 | 154.425 |  | 1466.375 | 1561.295 |  | 7.2129 | 7.634 | 7.7905 | 7.6851 | 6.8879 | 6.8901 | 6.9749 | 6.6384 | 57.7138 | 0.051942 |  | 62.069 | 100
19980514120000 | 1998-05-14 12:00 | 637.505 |  | 2.618 | 152.931 | 154.27 | 156.405 | 154.765 |  | 1467.292 | 1564.462 |  | 7.1938 | 7.6042 | 7.7546 | 7.6394 | 6.8521 | 6.8528 | 6.949 | 6.5986 | 57.4445 | 0.0517 |  | 62.069 | 100
19980514123000 | 1998-05-14 12:30 | 638.029 |  | 2.616 | 153.435 | 154.806 | 156.835 | 155.548 |  | 1464.292 | 1560.545 |  | 7.209 | 7.5798 | 7.8003 | 7.6074 | 6.8855 | 6.8384 | 6.981 | 6.5872 | 57.4886 | 0.05174 |  | 62.069 | 100
19980514130000 | 1998-05-14 13:00 | 639.917 |  | 3.72 | 153.792 | 154.78 | 157.169 | 155.275 |  | 1459.375 | 1556.378 |  | 7.1831 | 7.554 | 7.7385 | 7.5759 | 6.8535 | 6.7971 | 6.929 | 6.5361 | 57.1672 | 0.05145 |  | 62.069 | 100
19980514133000 | 1998-05-14 13:30 | 627.989 |  | 2.622 | 153.504 | 155.807 | 156.974 | 157.045 |  | 1472.459 | 1567.962 |  | 7.1541 | 7.5249 | 7.7234 | 7.5027 | 6.833 | 6.7781 | 6.9099 | 6.5178 | 56.9439 | 0.05125 |  | 62.069 | 100
19980514140000 | 1998-05-14 14:00 | 625.027 |  | 17.778 | 154.921 | 156.72 | 158.296 | 157.462 |  | 1474.542 | 1568.295 |  | 7.1519 | 7.5051 | 7.6958 | 7.5088 | 6.8093 | 6.7581 | 6.8909 | 6.4912 | 56.8111 | 0.05113 |  | 62.069 | 100
19980514143000 | 1998-05-14 14:30 | 626.521 |  | 2.369 | 155.46 | 156.003 | 158.887 | 156.745 |  | 1460.542 | 1554.378 |  | 7.1191 | 7.4958 | 7.6753 | 7.499 | 6.7896 | 6.7537 | 6.8726 | 6.4797 | 56.6848 | 0.051016 |  | 62.069 | 100
19980514150000 | 1998-05-14 15:00 | 626.102 |  | 3.719 | 154.93 | 155.807 | 158.366 | 156.054 |  | 1470.459 | 1566.045 |  | 7.1084 | 7.4639 | 7.6599 | 7.4592 | 6.7749 | 6.7314 | 6.8535 | 6.4644 | 56.5156 | 0.050864 |  | 62.069 | 100
19980514153000 | 1998-05-14 15:30 | 619.837 |  | 2.249 | 154.569 | 154.322 | 158.106 | 155.559 |  | 1467.625 | 1561.795 |  | 7.0718 | 7.4631 | 7.6204 | 7.4707 | 6.7498 | 6.7253 | 6.8528 | 6.4529 | 56.4068 | 0.050766 |  | 62.069 | 100
19980514160000 | 1998-05-14 16:00 | 626.128 |  | 2.985 | 152.806 | 151.429 | 156.348 | 153.161 |  | 1447.792 | 1542.378 |  | 7.1106 | 7.4897 | 7.6797 | 7.4807 | 6.7849 | 6.7498 | 6.8862 | 6.4722 | 56.6538 | 0.050988 |  | 62.069 | 100
19980514163000 | 1998-05-14 16:30 | 627.491 |  | 2.614 | 151.524 | 153.146 | 155.097 | 153.889 |  | 1449.958 | 1539.961 |  | 7.1023 | 7.4868 | 7.6807 | 7.4502 | 6.7903 | 6.7498 | 6.8733 | 6.4661 | 56.5995 | 0.05094 |  | 62.069 | 100
19980514170000 | 1998-05-14 17:00 | 628.461 |  | 2.983 | 151.685 | 152.821 | 155.264 | 153.812 |  | 1449.792 | 1545.294 |  | 7.1558 | 7.5134 | 7.718 | 7.4875 | 6.8352 | 6.7756 | 6.9077 | 6.4934 | 56.8866 | 0.051198 |  | 62.069 | 100
19980514173000 | 1998-05-14 17:30 | 575.902 |  | 1.88 | 151.283 | 149.408 | 154.855 | 149.903 |  | 1351.372 | 1439.375 |  | 6.6467 | 7.0496 | 7.1084 | 6.8542 | 6.3354 | 6.3225 | 6.4377 | 6.0303 | 52.7848 | 0.047506 |  | 62.069 | 100
19980514180000 | 1998-05-14 18:00 | 627.465 |  | 3.108 | 150.858 | 153.616 | 153.32 | 154.606 |  | 1470.792 | 1569.378 |  | 7.2046 | 7.5715 | 7.7949 | 7.6125 | 6.8887 | 6.8679 | 6.9824 | 6.5767 | 57.4992 | 0.051749 |  | 62.069 | 100
19980514183000 | 1998-05-14 18:30 | 632.524 |  | 2.733 | 152.817 | 154.657 | 156.142 | 154.905 |  | 1469.542 | 1566.712 |  | 7.1755 | 7.5493 | 7.7546 | 7.5615 | 6.8611 | 6.8345 | 6.9688 | 6.5552 | 57.2605 | 0.051534 |  | 62.069 | 100
19980514190000 | 1998-05-14 19:00 | 631.948 |  | 3.107 | 153.853 | 154.58 | 157.474 | 156.313 |  | 1466.959 | 1564.045 |  | 7.1863 | 7.5698 | 7.7637 | 7.5942 | 6.8733 | 6.855 | 6.9885 | 6.5759 | 57.4067 | 0.051666 |  | 62.069 | 100
19980514193000 | 1998-05-14 19:30 | 636.09 |  | 2.855 | 154.323 | 155.869 | 157.935 | 157.355 |  | 1468.959 | 1563.795 |  | 7.1533 | 7.5364 | 7.7454 | 7.55 | 6.8406 | 6.8169 | 6.9465 | 6.5376 | 57.1267 | 0.051414 |  | 62.069 | 100
19980514200000 | 1998-05-14 20:00 | 581.302 |  | 2.125 | 154.538 | 153.59 | 158.08 | 154.332 |  | 1343.955 | 1432.041 |  | 6.7124 | 7.0876 | 7.187 | 6.8962 | 6.3972 | 6.3462 | 6.4751 | 6.0525 | 53.1542 | 0.047839 |  | 62.069 | 100
19980514203000 | 1998-05-14 20:30 | 586.754 |  | 2.245 | 151.651 | 150.619 | 155.137 | 152.352 |  | 1341.705 | 1427.041 |  | 6.5986 | 6.9795 | 7.0229 | 6.7947 | 6.283 | 6.2302 | 6.3774 | 5.9456 | 52.2319 | 0.047009 |  | 62.069 | 100
19980514210000 | 1998-05-14 21:00 | 531.94 |  | 1.268 | 149.491 | 148.768 | 152.505 | 147.531 |  | 1206.785 | 1285.037 |  | 6.0815 | 6.5071 | 6.3545 | 6.092 | 5.7717 | 5.7764 | 5.9106 | 5.4512 | 47.945 | 0.04315 |  | 62.069 | 100
19980514213000 | 1998-05-14 21:30 | 562.113 |  | 1.269 | 149.439 | 151.868 | 149.006 | 146.917 |  | 1326.955 | 1420.874 |  | 6.5149 | 6.9443 | 6.9619 | 6.6919 | 6.2295 | 6.2737 | 6.3767 | 5.9395 | 51.9324 | 0.046739 |  | 62.069 | 100
19980514220000 | 1998-05-14 22:00 | 611.553 |  | 3.108 | 152.15 | 153.312 | 150.959 | 154.055 |  | 1425.291 | 1519.627 |  | 6.9871 | 7.3745 | 7.5234 | 7.3579 | 6.6804 | 6.6826 | 6.7681 | 6.376 | 55.75 | 0.050175 |  | 62.069 | 100
19980514223000 | 1998-05-14 22:30 | 614.935 |  | 2.614 | 152.136 | 152.115 | 154.682 | 153.601 |  | 1428.374 | 1517.21 |  | 6.9282 | 7.3425 | 7.4463 | 7.325 | 6.5994 | 6.6377 | 6.7253 | 6.3447 | 55.3491 | 0.049814 |  | 62.069 | 100
19980514230000 | 1998-05-14 23:00 | 607.464 |  | 3.109 | 151.736 | 151.687 | 154.901 | 152.677 |  | 1399.54 | 1489.959 |  | 6.7856 | 7.2266 | 7.2991 | 7.1426 | 6.4805 | 6.4949 | 6.5706 | 6.2209 | 54.2208 | 0.048799 |  | 62.069 | 100
19980514233000 | 1998-05-14 23:30 | 535.217 |  | 19.479 | 149.935 | 148.469 | 152.868 | 147.232 |  | 1222.285 | 1300.287 |  | 6.0417 | 6.5156 | 6.2935 | 6.0959 | 5.7275 | 5.7847 | 5.8479 | 5.491 | 47.7978 | 0.043018 |  | 62.069 | 100
19980515000000 | 1998-05-15 | 524.522 |  | 1.024 | 149.11 | 149.537 | 148.309 | 144.339 |  | 1203.201 | 1283.12 |  | 6.0547 | 6.334 | 6.3264 | 6.1394 | 5.7449 | 5.8274 | 5.8992 | 5.4971 | 47.8231 | 0.043041 |  | 62.069 | 100
19980515003000 | 1998-05-15 00:30 | 523.971 |  | 0.778 | 150.105 | 151.151 | 146.516 | 145.211 |  | 1197.701 | 1281.37 |  | 5.9434 | 5.8608 | 6.4248 | 6.2288 | 5.8152 | 5.8906 | 5.9617 | 5.5505 | 47.6758 | 0.042908 |  | 62.069 | 100
19980515010000 | 1998-05-15 01:00 | 472.119 |  | 0.778 | 150.746 | 149.862 | 146.54 | 145.654 |  | 1114.365 | 1194.618 |  | 5.5024 | 5.3909 | 5.8547 | 5.6274 | 5.3933 | 5.4939 | 5.5488 | 5.1262 | 43.9376 | 0.039544 |  | 62.069 | 100
19980515013000 | 1998-05-15 01:30 | 419.009 |  | 0.287 | 149.853 | 148.923 | 146.336 | 143.478 |  | 980.612 | 1059.114 |  | 4.8989 | 4.7302 | 5.0745 | 4.7891 | 4.8066 | 4.989 | 5.0325 | 4.5356 | 38.8564 | 0.034971 |  | 62.069 | 100
19980515020000 | 1998-05-15 02:00 | 371.483 |  | 0.534 | 149.381 | 150.094 | 144.875 | 144.154 |  | 854.025 | 929.943 |  | 4.4792 | 4.3152 | 5.085 | 4.8752 | 3.4135 | 4.625 | 4.6785 | 2.8268 | 34.2984 | 0.030869 |  | 62.069 | 100
19980515023000 | 1998-05-15 02:30 | 370.591 |  | 0.412 | 149.228 | 150.781 | 145.77 | 147.811 |  | 878.609 | 953.777 |  | 4.3184 | 4.2261 | 4.9219 | 4.7134 | 4.2922 | 4.4624 | 4.5496 | 3.0946 | 34.5786 | 0.031121 |  | 62.069 | 100
19980515030000 | 1998-05-15 03:00 | 371.194 |  | 0.78 | 150.495 | 149.528 | 148.381 | 146.311 |  | 879.192 | 949.694 |  | 4.229 | 4.1213 | 4.7937 | 4.6311 | 4.1909 | 4.3496 | 4.4075 | 4.0696 | 34.7927 | 0.031313 |  | 62.069 | 100
19980515033000 | 1998-05-15 03:30 | 368.389 |  | 0.285 | 149.432 | 150.478 | 147.124 | 147.012 |  | 874.025 | 944.277 |  | 4.2244 | 4.0969 | 4.7798 | 4.5876 | 4.187 | 4.3115 | 4.3787 | 4.0481 | 34.614 | 0.031153 |  | 62.069 | 100
19980515040000 | 1998-05-15 04:00 | 367.472 |  | 0.9 | 150.507 | 151.283 | 148.124 | 148.312 |  | 865.692 | 941.194 |  | 4.2534 | 4.1091 | 4.8394 | 4.634 | 4.2251 | 4.3167 | 4.4136 | 4.0627 | 34.854 | 0.031369 |  | 62.069 | 100
19980515043000 | 1998-05-15 04:30 | 370.434 |  | 16.314 | 150.346 | 150.226 | 148.521 | 146.266 |  | 857.191 | 928.36 |  | 4.2473 | 4.0947 | 4.8157 | 4.5945 | 4.1985 | 4.2749 | 4.3984 | 4.0437 | 34.6677 | 0.031201 |  | 62.069 | 100
19980515050000 | 1998-05-15 05:00 | 373.239 |  | 1.27 | 150.332 | 151.789 | 147.955 | 147.333 |  | 867.442 | 939.444 |  | 4.2595 | 4.1274 | 4.8401 | 4.6401 | 4.21 | 4.2671 | 4.4106 | 4.0649 | 34.8197 | 0.031338 |  | 62.069 | 100
19980515053000 | 1998-05-15 05:30 | 369.805 |  | 0.079 | 150.795 | 150.118 | 148.344 | 147.396 |  | 865.192 | 934.527 |  | 4.2336 | 4.0955 | 4.8127 | 4.6243 | 4.1963 | 4.2466 | 4.3945 | 4.0574 | 34.6609 | 0.031195 |  | 62.069 | 100
19980515060000 | 1998-05-15 06:00 | 368.887 |  | 2.006 | 150.244 | 150.392 | 148.573 | 146.679 |  | 864.275 | 936.61 |  | 4.2351 | 4.1191 | 4.8074 | 4.6204 | 4.2175 | 4.2678 | 4.4045 | 4.0725 | 34.7443 | 0.03127 |  | 62.069 | 100
19980515063000 | 1998-05-15 06:30 | 476.785 |  | 0.657 | 151.45 | 154.548 | 149.064 | 149.845 |  | 1092.198 | 1164.7 |  | 5.4504 | 5.3689 | 5.8342 | 5.6274 | 5.3909 | 5.3665 | 5.4963 | 5.1912 | 43.7258 | 0.039353 |  | 62.069 | 100
19980515070000 | 1998-05-15 07:00 | 495.188 |  | 1.028 | 152.032 | 151.109 | 149.888 | 146.653 |  | 1166.95 | 1249.453 |  | 5.7678 | 5.7014 | 6.2058 | 6.0815 | 5.752 | 5.7664 | 5.845 | 5.5588 | 46.6787 | 0.042011 |  | 62.069 | 100
19980515073000 | 1998-05-15 07:30 | 619.627 |  | 2.006 | 151.96 | 154.682 | 149.983 | 150.969 |  | 1437.291 | 1540.294 |  | 6.949 | 6.8984 | 7.6868 | 7.5891 | 6.8923 | 6.8481 | 6.9153 | 6.6765 | 56.4555 | 0.05081 |  | 62.069 | 100
19980515080000 | 1998-05-15 08:00 | 641.464 |  | 2.618 | 152.65 | 151.845 | 152.953 | 152.587 |  | 1477.042 | 1571.795 |  | 7.1487 | 7.0693 | 7.9033 | 7.7751 | 7.0405 | 6.9749 | 7.0581 | 6.8262 | 57.7961 | 0.052016 |  | 62.069 | 100
19980515083000 | 1998-05-15 08:30 | 641.306 |  | 2.248 | 151.537 | 152.107 | 154.718 | 153.592 |  | 1482.959 | 1578.545 |  | 7.1121 | 7.0388 | 7.8567 | 7.7356 | 7.0154 | 6.9404 | 7.0244 | 6.7957 | 57.5191 | 0.051767 |  | 62.069 | 100
19980515090000 | 1998-05-15 09:00 | 642.853 |  | 2.617 | 151.452 | 151.941 | 155.408 | 153.426 |  | 1477.459 | 1571.545 |  | 7.1045 | 7.0527 | 7.8462 | 7.731 | 7.0083 | 6.9504 | 7.0276 | 6.804 | 57.5247 | 0.051772 |  | 62.069 | 100
19980515093000 | 1998-05-15 09:30 | 642.774 |  | 2.004 | 151.682 | 152.488 | 155.775 | 154.963 |  | 1475.709 | 1570.378 |  | 7.1008 | 7.0549 | 7.8394 | 7.7417 | 7.0068 | 6.9526 | 7.0337 | 6.8176 | 57.5475 | 0.051793 |  | 62.069 | 100
19980515100000 | 1998-05-15 10:00 | 641.044 |  | 2.735 | 152.066 | 153.401 | 156.255 | 155.133 |  | 1481.376 | 1577.129 |  | 7.0999 | 7.0427 | 7.8384 | 7.7278 | 6.9954 | 6.9397 | 7.0154 | 6.7925 | 57.4518 | 0.051707 |  | 62.069 | 100
19980515103000 | 1998-05-15 10:30 | 643.561 |  | 2.371 | 152.541 | 153.937 | 156.872 | 156.412 |  | 1483.709 | 1577.379 |  | 7.1206 | 7.0564 | 7.8674 | 7.75 | 7.019 | 6.9451 | 7.0183 | 6.8069 | 57.5837 | 0.051825 |  | 62.069 | 100
19980515110000 | 1998-05-15 11:00 | 640.153 |  | 2.619 | 153.051 | 154.225 | 157.359 | 156.205 |  | 1479.626 | 1572.629 |  | 7.0969 | 7.0427 | 7.834 | 7.74 | 6.9871 | 6.9146 | 7.0046 | 6.7932 | 57.4131 | 0.051672 |  | 62.069 | 100
19980515113000 | 1998-05-15 11:30 | 642.014 |  | 2.247 | 153.195 | 154.147 | 157.518 | 155.633 |  | 1474.792 | 1570.712 |  | 7.1289 | 7.0481 | 7.8599 | 7.7561 | 7.0237 | 6.9429 | 7.0259 | 6.8093 | 57.5948 | 0.051835 |  | 62.069 | 100
19980515120000 | 1998-05-15 12:00 | 641.49 |  | 3.104 | 153.427 | 154.838 | 157.834 | 156.571 |  | 1479.376 | 1573.129 |  | 7.1296 | 7.0305 | 7.8667 | 7.7263 | 7.0205 | 6.9275 | 7.0129 | 6.7834 | 57.4974 | 0.051748 |  | 62.069 | 100
19980515123000 | 1998-05-15 12:30 | 635.565 |  | 2 | 154.156 | 155.086 | 158.629 | 157.066 |  | 1479.459 | 1570.295 |  | 7.1084 | 7.0266 | 7.8538 | 7.7324 | 7.0032 | 6.9275 | 7.0129 | 6.7825 | 57.4473 | 0.051703 |  | 62.069 | 100
19980515130000 | 1998-05-15 13:00 | 633.783 |  | 2.857 | 154.468 | 155.958 | 158.887 | 156.948 |  | 1469.209 | 1564.462 |  | 7.0764 | 6.9727 | 7.8071 | 7.6782 | 6.9666 | 6.8726 | 6.9626 | 6.7336 | 57.0698 | 0.051363 |  | 62.069 | 100
19980515133000 | 1998-05-15 13:30 | 635.775 |  | 2.122 | 154.514 | 156.479 | 158.852 | 157.469 |  | 1470.459 | 1565.962 |  | 7.0488 | 6.9648 | 7.7844 | 7.6387 | 6.9465 | 6.8665 | 6.9595 | 6.72 | 56.9292 | 0.051236 |  | 62.069 | 100
19980515140000 | 1998-05-15 14:00 | 640.336 |  | 21.173 | 155.094 | 156.634 | 159.441 | 158.366 |  | 1471.126 | 1561.795 |  | 7.0596 | 6.9832 | 7.8018 | 7.6707 | 6.9612 | 6.8757 | 6.9666 | 6.7346 | 57.0534 | 0.051348 |  | 62.069 | 100
19980515143000 | 1998-05-15 14:30 | 644.006 |  | 2.243 | 155.507 | 157.609 | 159.857 | 159.094 |  | 1472.126 | 1566.878 |  | 7.0366 | 6.9727 | 7.76 | 7.6462 | 6.949 | 6.855 | 6.9534 | 6.7139 | 56.8868 | 0.051198 |  | 62.069 | 100
19980515150000 | 1998-05-15 15:00 | 580.882 |  | 2.244 | 154.014 | 150.962 | 158.283 | 153.19 |  | 1329.371 | 1412.624 |  | 6.4805 | 6.376 | 7.0947 | 6.8811 | 6.4119 | 6.3286 | 6.3989 | 6.1624 | 52.1341 | 0.046921 |  | 62.069 | 100
19980515153000 | 1998-05-15 15:30 | 576.164 |  | 1.509 | 150.621 | 150.674 | 154.718 | 151.911 |  | 1323.621 | 1409.54 |  | 6.4485 | 6.3584 | 7.0596 | 6.8779 | 6.3889 | 6.324 | 6.3911 | 6.1455 | 51.9939 | 0.046795 |  | 62.069 | 100
19980515160000 | 1998-05-15 16:00 | 613.991 |  | 2.859 | 150.307 | 153.5 | 154.119 | 153.995 |  | 1449.792 | 1546.211 |  | 6.9924 | 6.9207 | 7.6875 | 7.592 | 6.8977 | 6.8452 | 6.9167 | 6.6628 | 56.515 | 0.050863 |  | 62.069 | 100
19980515163000 | 1998-05-15 16:30 | 629.038 |  | 2.367 | 153.607 | 156.3 | 157.276 | 157.538 |  | 1458.375 | 1552.711 |  | 7.0183 | 6.9551 | 7.7217 | 7.6143 | 6.9246 | 6.8474 | 6.929 | 6.6941 | 56.7045 | 0.051034 |  | 62.069 | 100
19980515170000 | 1998-05-15 17:00 | 628.592 |  | 3.353 | 156.02 | 157.76 | 160.032 | 159.492 |  | 1461.209 | 1562.378 |  | 7.0449 | 6.9565 | 7.7644 | 7.6211 | 6.9519 | 6.8604 | 6.9421 | 6.7031 | 56.8444 | 0.05116 |  | 62.069 | 100
19980515173000 | 1998-05-15 17:30 | 631.135 |  | 2.611 | 156.553 | 157.46 | 160.762 | 158.946 |  | 1465.459 | 1561.712 |  | 7.0825 | 6.9763 | 7.8125 | 7.6699 | 6.9863 | 6.8757 | 6.9688 | 6.7253 | 57.0973 | 0.051388 |  | 62.069 | 100
19980515180000 | 1998-05-15 18:00 | 632.472 |  | 3.225 | 156.006 | 156.795 | 160.15 | 157.29 |  | 1475.626 | 1569.378 |  | 7.0449 | 6.9771 | 7.769 | 7.6523 | 6.9604 | 6.8733 | 6.9473 | 6.7214 | 56.9457 | 0.051251 |  | 62.069 | 100
19980515183000 | 1998-05-15 18:30 | 631.581 |  | 2.739 | 155.238 | 155.753 | 159.363 | 156.744 |  | 1464.625 | 1559.545 |  | 7.0442 | 6.9604 | 7.7454 | 7.637 | 6.9473 | 6.8481 | 6.9253 | 6.6926 | 56.8003 | 0.05112 |  | 62.069 | 100
19980515190000 | 1998-05-15 19:00 | 581.878 |  | 21.926 | 154.519 | 153.005 | 158.611 | 154.985 |  | 1337.705 | 1424.624 |  | 6.5139 | 6.4155 | 7.1167 | 6.916 | 6.4294 | 6.3469 | 6.4202 | 6.199 | 52.3576 | 0.047122 |  | 62.069 | 100
19980515193000 | 1998-05-15 19:30 | 582.219 |  | 1.754 | 151.403 | 150.777 | 155.245 | 151.519 |  | 1343.955 | 1428.124 |  | 6.5483 | 6.4392 | 7.168 | 6.9795 | 6.4766 | 6.3936 | 6.459 | 6.2202 | 52.6844 | 0.047416 |  | 62.069 | 100
19980515200000 | 1998-05-15 20:00 | 587.41 |  | 2.37 | 150.428 | 151.102 | 153.332 | 151.597 |  | 1346.705 | 1430.874 |  | 6.5117 | 6.4316 | 7.1274 | 6.9626 | 6.4392 | 6.3774 | 6.4417 | 6.2126 | 52.5042 | 0.047254 |  | 62.069 | 100
19980515203000 | 1998-05-15 20:30 | 533.277 |  | 1.02 | 149.215 | 148.823 | 151.368 | 145.852 |  | 1224.869 | 1305.454 |  | 6.0151 | 5.9089 | 6.5095 | 6.2959 | 5.9524 | 5.906 | 5.9692 | 5.7161 | 48.2731 | 0.043446 |  | 62.069 | 100
19980515210000 | 1998-05-15 21:00 | 525.36 |  | 1.265 | 149.585 | 150.906 | 148.164 | 144.966 |  | 1197.534 | 1279.12 |  | 5.9517 | 5.8633 | 6.4163 | 6.2471 | 5.9053 | 5.8914 | 5.9524 | 5.6855 | 47.913 | 0.043122 |  | 62.069 | 100
19980515213000 | 1998-05-15 21:30 | 529.345 |  | 0.773 | 150.354 | 150.999 | 147.809 | 146.791 |  | 1198.201 | 1281.453 |  | 5.9624 | 5.8389 | 6.4255 | 6.2119 | 5.9021 | 5.8701 | 5.9333 | 5.6565 | 47.8007 | 0.043021 |  | 62.069 | 100
19980515220000 | 1998-05-15 22:00 | 561.589 |  | 2.124 | 150.681 | 153.056 | 148.345 | 148.848 |  | 1348.539 | 1443.875 |  | 6.3989 | 6.3667 | 7.01 | 6.9063 | 6.3684 | 6.3706 | 6.4209 | 6.1685 | 52.0103 | 0.046809 |  | 62.069 | 100
19980515223000 | 1998-05-15 22:30 | 576.557 |  | 1.759 | 152.479 | 150.895 | 151.988 | 151.638 |  | 1339.372 | 1426.541 |  | 6.4819 | 6.4087 | 7.1008 | 6.9551 | 6.408 | 6.3667 | 6.4338 | 6.2043 | 52.3593 | 0.047123 |  | 62.069 | 100
19980515230000 | 1998-05-15 23:00 | 576.845 |  | 2.129 | 150.798 | 150.348 | 153.366 | 151.834 |  | 1337.122 | 1424.208 |  | 6.4485 | 6.3835 | 7.0596 | 6.9307 | 6.3674 | 6.3469 | 6.4094 | 6.1799 | 52.1259 | 0.046913 |  | 62.069 | 100
19980515233000 | 1998-05-15 23:30 | 580.122 |  | 1.514 | 149.936 | 150.364 | 152.793 | 150.364 |  | 1337.872 | 1426.374 |  | 6.4819 | 6.4072 | 7.0876 | 6.9626 | 6.4041 | 6.3545 | 6.4216 | 6.1951 | 52.3146 | 0.047083 |  | 62.069 | 100
19980516000000 | 1998-05-16 | 576.924 |  | 1.882 | 150.494 | 149.662 | 152.711 | 149.909 |  | 1347.289 | 1437.541 |  | 6.4988 | 6.4233 | 7.1243 | 6.9595 | 6.4355 | 6.3774 | 6.4424 | 6.2134 | 52.4746 | 0.047227 |  | 62.069 | 100
19980516003000 | 1998-05-16 00:30 | 576.033 |  | 1.51 | 149.969 | 150.574 | 151.971 | 149.089 |  | 1332.372 | 1425.624 |  | 6.4614 | 6.4058 | 7.0808 | 6.9534 | 6.3958 | 6.3584 | 6.4255 | 6.1897 | 52.2708 | 0.047044 |  | 62.069 | 100
19980516010000 | 1998-05-16 01:00 | 578.287 |  | 2.125 | 150.218 | 150.172 | 151.023 | 148.934 |  | 1334.955 | 1425.124 |  | 6.4675 | 6.4094 | 7.0923 | 6.9695 | 6.4019 | 6.3562 | 6.4255 | 6.1943 | 52.3166 | 0.047085 |  | 62.069 | 100
19980516013000 | 1998-05-16 01:30 | 525.649 |  | 0.777 | 149.909 | 149.233 | 150.047 | 144.778 |  | 1214.952 | 1301.704 |  | 5.9502 | 5.8625 | 6.4141 | 6.2378 | 5.8801 | 5.8655 | 5.9167 | 5.6885 | 47.8154 | 0.043034 |  | 62.069 | 100
19980516020000 | 1998-05-16 02:00 | 523.499 |  | 1.147 | 149.83 | 151.059 | 147.91 | 146.356 |  | 1214.202 | 1297.871 |  | 5.9319 | 5.8289 | 6.3745 | 6.2141 | 5.8633 | 5.8442 | 5.9121 | 5.6572 | 47.6262 | 0.042864 |  | 62.069 | 100
19980516023000 | 1998-05-16 02:30 | 532.019 |  | 0.086 | 150.655 | 149.104 | 148.228 | 144.649 |  | 1203.035 | 1291.704 |  | 6.3333 | 6.2769 | 6.9404 | 6.7727 | 6.2188 | 3.2815 | 6.2568 | 6.092 | 48.1724 | 0.043355 |  | 62.069 | 100
19980516030000 | 1998-05-16 03:00 | 478.411 |  | 0.777 | 148.918 | 149.285 | 146.736 | 145.325 |  | 1073.864 | 1150.366 |  | 5.3315 | 5.2192 | 5.6055 | 5.439 | 5.2781 | 5.3452 | 5.3779 | 5.0867 | 42.6831 | 0.038415 |  | 62.069 | 100
19980516033000 | 1998-05-16 03:30 | 470.546 |  | 0.409 | 149.703 | 150.523 | 147.29 | 146.315 |  | 1056.864 | 1131.116 |  | 5.3308 | 5.2246 | 5.6099 | 5.4268 | 5.2834 | 5.3542 | 5.3872 | 5.0896 | 42.7065 | 0.038436 |  | 62.069 | 100
19980516040000 | 1998-05-16 04:00 | 476.156 |  | 0.658 | 150.543 | 150.848 | 148.341 | 147.135 |  | 1064.447 | 1140.866 |  | 5.3308 | 5.2253 | 5.6177 | 5.4253 | 5.2781 | 5.333 | 5.3711 | 5.0728 | 42.6541 | 0.038389 |  | 62.069 | 100
19980516043000 | 1998-05-16 04:30 | 471.097 |  | 0.287 | 150.822 | 150.559 | 148.715 | 146.847 |  | 1053.947 | 1129.449 |  | 5.3391 | 5.2261 | 5.6321 | 5.4138 | 5.2993 | 5.3535 | 5.3933 | 5.0813 | 42.7385 | 0.038465 |  | 62.069 | 100
19980516050000 | 1998-05-16 05:00 | 425.641 |  | 0.654 | 150.309 | 150.312 | 148.255 | 146.352 |  | 946.777 | 1020.613 |  | 4.77 | 4.6135 | 4.918 | 4.635 | 4.7317 | 4.7905 | 4.844 | 4.5083 | 37.811 | 0.03403 |  | 62.069 | 100
19980516053000 | 1998-05-16 05:30 | 419.271 |  | 0.166 | 149.934 | 149.972 | 147.553 | 146.259 |  | 961.861 | 1039.697 |  | 4.8416 | 4.7058 | 5.0095 | 4.7571 | 4.7944 | 4.918 | 4.9324 | 4.6013 | 38.5601 | 0.034704 |  | 62.069 | 100
19980516060000 | 1998-05-16 06:00 | 473.535 |  | 0.9 | 150.853 | 151.73 | 148.845 | 149.008 |  | 1085.615 | 1164.117 |  | 5.4063 | 5.301 | 5.7344 | 5.519 | 5.3459 | 5.3833 | 5.4375 | 5.1223 | 43.2497 | 0.038925 |  | 62.069 | 100
19980516063000 | 1998-05-16 06:30 | 472.224 |  | 0.288 | 151.18 | 150.57 | 149.486 | 147.6 |  | 1072.864 | 1148.033 |  | 5.3757 | 5.2644 | 5.6855 | 5.4863 | 5.3201 | 5.3674 | 5.4001 | 5.1125 | 43.012 | 0.038711 |  | 62.069 | 100
19980516070000 | 1998-05-16 07:00 | 474.033 |  | 0.781 | 150.584 | 150.256 | 148.703 | 146.791 |  | 1081.531 | 1158.117 |  | 5.3689 | 5.2795 | 5.6863 | 5.4834 | 5.3018 | 5.3521 | 5.3894 | 5.1147 | 42.9761 | 0.038678 |  | 62.069 | 100
19980516073000 | 1998-05-16 07:30 | 523.237 |  | 0.901 | 150.497 | 152.159 | 148.494 | 148.446 |  | 1215.202 | 1298.121 |  | 5.9158 | 5.8694 | 6.3928 | 6.2737 | 5.8572 | 5.9014 | 5.9395 | 5.6863 | 47.8361 | 0.043052 |  | 62.069 | 100
19980516080000 | 1998-05-16 08:00 | 611.448 |  | 2.863 | 152.085 | 154.257 | 150.621 | 151.039 |  | 1437.375 | 1540.461 |  | 6.8428 | 6.7871 | 7.5027 | 7.4448 | 6.7429 | 6.7468 | 6.7979 | 6.5613 | 55.4263 | 0.049884 |  | 62.069 | 100
19980516083000 | 1998-05-16 08:30 | 625.997 |  | 1.762 | 151.985 | 151.679 | 153.406 | 152.916 |  | 1440.375 | 1536.044 |  | 6.9336 | 6.875 | 7.6257 | 7.5325 | 6.8428 | 6.8147 | 6.8635 | 6.6277 | 56.1155 | 0.050504 |  | 62.069 | 100
19980516090000 | 1998-05-16 09:00 | 625.814 |  | 2.619 | 150.628 | 151.42 | 154.357 | 152.41 |  | 1431.208 | 1525.46 |  | 6.9146 | 6.8679 | 7.5974 | 7.4814 | 6.8123 | 6.7925 | 6.8445 | 6.6255 | 55.9361 | 0.050342 |  | 62.069 | 100
19980516093000 | 1998-05-16 09:30 | 624.319 |  | 1.147 | 150.748 | 151.095 | 154.246 | 152.828 |  | 1430.458 | 1522.96 |  | 6.9146 | 6.8665 | 7.6057 | 7.5166 | 6.8147 | 6.7947 | 6.842 | 6.6277 | 55.9825 | 0.050384 |  | 62.069 | 100
19980516100000 | 1998-05-16 10:00 | 623.979 |  | 2.62 | 151.082 | 151.657 | 154.736 | 153.39 |  | 1431.458 | 1524.71 |  | 6.9131 | 6.8704 | 7.6143 | 7.5242 | 6.8154 | 6.791 | 6.842 | 6.6255 | 55.9959 | 0.050396 |  | 62.069 | 100
19980516103000 | 1998-05-16 10:30 | 627.78 |  | 1.637 | 151.18 | 152.049 | 155.266 | 154.029 |  | 1432.374 | 1526.294 |  | 6.9688 | 6.8977 | 7.6545 | 7.5454 | 6.8611 | 6.8018 | 6.8635 | 6.6482 | 56.241 | 0.050617 |  | 62.069 | 100
19980516110000 | 1998-05-16 11:00 | 627.072 |  | 2.499 | 151.576 | 153.168 | 155.779 | 154.901 |  | 1426.374 | 1518.377 |  | 6.9023 | 6.8435 | 7.592 | 7.4829 | 6.8108 | 6.7651 | 6.8054 | 6.5979 | 55.7999 | 0.05022 |  | 62.069 | 100
19980516113000 | 1998-05-16 11:30 | 629.903 |  | 1.882 | 152.166 | 153.756 | 156.331 | 154.993 |  | 1434.958 | 1526.294 |  | 6.9131 | 6.842 | 7.6035 | 7.5142 | 6.8215 | 6.772 | 6.8184 | 6.6201 | 55.9048 | 0.050314 |  | 62.069 | 100
19980516120000 | 1998-05-16 12:00 | 625.106 |  | 2.618 | 152.746 | 153.781 | 156.999 | 155.762 |  | 1436.875 | 1526.71 |  | 6.9253 | 6.855 | 7.6082 | 7.5173 | 6.833 | 6.7756 | 6.8262 | 6.6155 | 55.9561 | 0.05036 |  | 62.069 | 100
19980516123000 | 1998-05-16 12:30 | 626.888 |  | 2 | 153.166 | 154.328 | 157.292 | 156.061 |  | 1444.208 | 1535.877 |  | 6.968 | 6.8726 | 7.679 | 7.5173 | 6.8733 | 6.7886 | 6.8496 | 6.6284 | 56.1768 | 0.050559 |  | 62.069 | 100
19980516130000 | 1998-05-16 13:00 | 623.926 |  | 2.492 | 153.463 | 154.953 | 157.739 | 156.19 |  | 1438.458 | 1532.961 |  | 6.9351 | 6.8481 | 7.6523 | 7.4829 | 6.8391 | 6.7803 | 6.8337 | 6.6169 | 55.9884 | 0.05039 |  | 62.069 | 100
19980516133000 | 1998-05-16 13:30 | 626.888 |  | 1.874 | 153.828 | 155.278 | 158.039 | 156.515 |  | 1441.875 | 1536.044 |  | 6.9412 | 6.8542 | 7.6484 | 7.4937 | 6.842 | 6.7742 | 6.8352 | 6.6187 | 56.0076 | 0.050407 |  | 62.069 | 100
19980516140000 | 1998-05-16 14:00 | 622.72 |  | 2.859 | 154.363 | 155.643 | 158.538 | 157.376 |  | 1442.041 | 1536.044 |  | 6.9314 | 6.8542 | 7.6187 | 7.5166 | 6.8298 | 6.781 | 6.8323 | 6.6125 | 55.9765 | 0.050379 |  | 62.069 | 100
19980516143000 | 1998-05-16 14:30 | 623.376 |  | 2.123 | 154.626 | 156.464 | 158.87 | 157.454 |  | 1438.208 | 1532.544 |  | 6.9504 | 6.8489 | 7.6631 | 7.5264 | 6.8535 | 6.7756 | 6.8398 | 6.6133 | 56.071 | 0.050464 |  | 62.069 | 100
19980516150000 | 1998-05-16 15:00 | 628.252 |  | 2.616 | 155.102 | 156.567 | 159.229 | 158.3 |  | 1441.291 | 1532.211 |  | 6.939 | 6.8542 | 7.6477 | 7.5234 | 6.8435 | 6.7803 | 6.8359 | 6.6194 | 56.0434 | 0.050439 |  | 62.069 | 100
19980516153000 | 1998-05-16 15:30 | 622.38 |  | 1.877 | 155.479 | 156.541 | 159.573 | 158.521 |  | 1437.041 | 1529.377 |  | 6.9666 | 6.8765 | 7.679 | 7.5264 | 6.865 | 6.8101 | 6.8726 | 6.6431 | 56.2393 | 0.050615 |  | 62.069 | 100
19980516160000 | 1998-05-16 16:00 | 626.705 |  | 2.613 | 155.539 | 156.423 | 159.596 | 157.908 |  | 1445.292 | 1536.294 |  | 6.9741 | 6.8787 | 7.6919 | 7.5654 | 6.8772 | 6.8115 | 6.874 | 6.6431 | 56.3159 | 0.050684 |  | 62.069 | 100
19980516163000 | 1998-05-16 16:30 | 626.915 |  | 2.49 | 155.71 | 156.877 | 159.773 | 158.362 |  | 1441.541 | 1536.711 |  | 6.9351 | 6.8765 | 7.6401 | 7.5342 | 6.8496 | 6.8093 | 6.8801 | 6.637 | 56.1619 | 0.050546 |  | 62.069 | 100
19980516170000 | 1998-05-16 17:00 | 626.023 |  | 1.436 | 156.164 | 158.141 | 160.29 | 160.368 |  | 1443.625 | 1536.877 |  | 6.9612 | 6.9055 | 7.6523 | 7.5593 | 6.8635 | 6.8252 | 6.9009 | 6.6582 | 56.3261 | 0.050693 |  | 62.069 | 100
19980516173000 | 1998-05-16 17:30 | 622.642 |  | 2.614 | 156.882 | 158.646 | 160.947 | 159.389 |  | 1446.208 | 1541.128 |  | 6.9626 | 6.9167 | 7.6753 | 7.5769 | 6.8628 | 6.8323 | 6.9009 | 6.6704 | 56.3979 | 0.050758 |  | 62.069 | 100
19980516180000 | 1998-05-16 18:00 | 621.567 |  | 3.598 | 156.865 | 158.074 | 161.016 | 159.064 |  | 1442.625 | 1534.627 |  | 6.9849 | 6.9124 | 7.6814 | 7.5698 | 6.8801 | 6.8284 | 6.9009 | 6.6689 | 56.4268 | 0.050784 |  | 62.069 | 100
19980516183000 | 1998-05-16 18:30 | 622.668 |  | 2.611 | 156.808 | 158.92 | 160.958 | 159.662 |  | 1452.542 | 1544.628 |  | 6.9756 | 6.9131 | 7.6851 | 7.5662 | 6.874 | 6.8252 | 6.8977 | 6.6499 | 56.3868 | 0.050748 |  | 62.069 | 100
19980516190000 | 1998-05-16 19:00 | 621.934 |  | 3.719 | 157.821 | 159.714 | 161.947 | 161.199 |  | 1452.042 | 1546.128 |  | 6.9641 | 6.8855 | 7.6692 | 7.5447 | 6.8657 | 6.8086 | 6.8733 | 6.6399 | 56.251 | 0.050626 |  | 62.069 | 100
19980516193000 | 1998-05-16 19:30 | 622.38 |  | 3.107 | 158.426 | 159.271 | 162.5 | 160.261 |  | 1452.125 | 1542.378 |  | 6.9429 | 6.8718 | 7.6484 | 7.5195 | 6.8359 | 6.7939 | 6.8574 | 6.623 | 56.0928 | 0.050484 |  | 62.069 | 100
19980516200000 | 1998-05-16 20:00 | 611.212 |  | 3.594 | 157.706 | 158.384 | 161.902 | 159.869 |  | 1389.79 | 1479.292 |  | 6.7002 | 6.6162 | 7.3206 | 7.2021 | 6.5811 | 6.5193 | 6.5903 | 6.3728 | 53.9026 | 0.048512 |  | 62.069 | 100
19980516203000 | 1998-05-16 20:30 | 546.62 |  | 1.391 | 155.276 | 151.608 | 159.385 | 153.836 |  | 1252.119 | 1338.122 |  | 6.1218 | 6.0205 | 6.6309 | 6.4041 | 6.0693 | 6.0234 | 6.0852 | 5.8403 | 49.1955 | 0.044276 |  | 62.069 | 100
19980516210000 | 1998-05-16 21:00 | 542.033 |  | 1.635 | 150.593 | 149.783 | 154.737 | 150.773 |  | 1245.536 | 1327.371 |  | 6.0823 | 6.0151 | 6.5986 | 6.3843 | 6.0112 | 6.0159 | 6.0701 | 5.8191 | 48.9966 | 0.044097 |  | 62.069 | 100
19980516213000 | 1998-05-16 21:30 | 499.539 |  | 0.656 | 149.757 | 149.912 | 152.646 | 149.417 |  | 1130.866 | 1204.618 |  | 5.6641 | 5.5825 | 6.0723 | 5.8342 | 5.6343 | 5.6221 | 5.6777 | 5.4146 | 45.5018 | 0.040952 |  | 62.069 | 100
19980516220000 | 1998-05-16 22:00 | 548.377 |  | 2.618 | 149.491 | 151.969 | 150.233 | 148.009 |  | 1296.621 | 1387.373 |  | 6.2012 | 6.1692 | 6.7903 | 6.6208 | 6.1692 | 6.231 | 6.2424 | 5.9792 | 50.4033 | 0.045363 |  | 62.069 | 100
19980516223000 | 1998-05-16 22:30 | 579.362 |  | 1.878 | 151.678 | 151.319 | 151.476 | 151.072 |  | 1315.621 | 1404.374 |  | 6.4285 | 6.3569 | 7.0381 | 6.8894 | 6.353 | 6.3584 | 6.405 | 6.1599 | 51.9892 | 0.04679 |  | 62.069 | 100
19980516230000 | 1998-05-16 23:00 | 576.216 |  | 2.618 | 150.77 | 151.242 | 152.743 | 151.242 |  | 1312.454 | 1398.54 |  | 6.4004 | 6.3394 | 6.981 | 6.842 | 6.3186 | 6.3271 | 6.3789 | 6.1387 | 51.7261 | 0.046553 |  | 62.069 | 100
19980516233000 | 1998-05-16 23:30 | 576.242 |  | 2.126 | 150.465 | 150.618 | 152.975 | 152.35 |  | 1315.704 | 1402.79 |  | 6.4072 | 6.3552 | 7.0068 | 6.8557 | 6.3257 | 6.3293 | 6.3774 | 6.1501 | 51.8074 | 0.046627 |  | 62.069 | 100
19980517000000 | 1998-05-17 | 570.187 |  | 2.004 | 150.824 | 152.572 | 153.426 | 153.81 |  | 1338.122 | 1424.041 |  | 6.4026 | 6.3552 | 6.991 | 6.8604 | 6.321 | 6.3369 | 6.3806 | 6.1563 | 51.804 | 0.046624 |  | 62.069 | 100
19980517003000 | 1998-05-17 00:30 | 577.815 |  | 1.878 | 151.913 | 152.391 | 155.159 | 154.124 |  | 1332.038 | 1418.707 |  | 6.4033 | 6.3379 | 6.9985 | 6.8589 | 6.3171 | 6.3118 | 6.3584 | 6.1333 | 51.7192 | 0.046547 |  | 62.069 | 100
19980517010000 | 1998-05-17 01:00 | 526.724 |  | 1.636 | 150.747 | 149.07 | 154.081 | 149.07 |  | 1219.618 | 1300.287 |  | 5.9204 | 5.8259 | 6.3552 | 6.1799 | 5.8403 | 5.8403 | 5.8914 | 5.6497 | 47.5031 | 0.042753 |  | 62.069 | 100
19980517013000 | 1998-05-17 01:30 | 502.344 |  | 0.653 | 149.159 | 150.973 | 150.499 | 148.002 |  | 1136.116 | 1217.702 |  | 5.6184 | 5.5146 | 5.9814 | 5.7617 | 5.5276 | 5.5129 | 5.5657 | 5.3369 | 44.8192 | 0.040337 |  | 62.069 | 100
19980517020000 | 1998-05-17 02:00 | 464.36 |  | 16.556 | 149.711 | 148.652 | 148.428 | 142.96 |  | 1037.113 | 1115.532 |  | 5.0857 | 4.9661 | 5.3643 | 5.0332 | 5.0378 | 5.0508 | 5.0957 | 4.8425 | 40.4761 | 0.036428 |  | 62.069 | 100
19980517023000 | 1998-05-17 02:30 | 431.146 |  | 0.405 | 148.192 | 149.524 | 145.718 | 145.317 |  | 961.444 | 1028.196 |  | 4.8203 | 4.6868 | 4.9775 | 4.7104 | 4.802 | 4.9141 | 4.9355 | 4.5959 | 38.4425 | 0.034598 |  | 62.069 | 100
19980517030000 | 1998-05-17 03:00 | 423.964 |  | 0.776 | 149.542 | 151.634 | 147.505 | 148.416 |  | 975.195 | 1044.947 |  | 4.844 | 4.7151 | 5.0049 | 4.7805 | 4.8042 | 4.9255 | 4.9575 | 4.6174 | 38.6491 | 0.034784 |  | 62.069 | 100
19980517033000 | 1998-05-17 03:30 | 425.248 |  | 0.285 | 151.115 | 150.629 | 149.508 | 147.411 |  | 979.361 | 1048.197 |  | 4.8677 | 4.7532 | 5.0354 | 4.8364 | 4.8181 | 4.9446 | 4.9873 | 4.6455 | 38.8882 | 0.034999 |  | 62.069 | 100
19980517040000 | 1998-05-17 04:00 | 419.376 |  | 0.898 | 150.382 | 150.041 | 148.843 | 147.318 |  | 971.278 | 1049.113 |  | 4.8738 | 4.7622 | 5.0508 | 4.866 | 4.8196 | 4.9187 | 4.9714 | 4.6584 | 38.9209 | 0.035029 |  | 62.069 | 100
19980517043000 | 1998-05-17 04:30 | 422.181 |  | 0.284 | 150.144 | 150.964 | 148.298 | 147.499 |  | 970.528 | 1046.113 |  | 4.8645 | 4.7126 | 5.0317 | 4.7952 | 4.8049 | 4.8774 | 4.9158 | 4.6089 | 38.611 | 0.03475 |  | 62.069 | 100
19980517050000 | 1998-05-17 05:00 | 396.386 |  | 2.862 | 150.364 | 150.521 | 148.658 | 147.056 |  | 897.609 | 977.945 |  | 4.4624 | 4.3481 | 4.5129 | 4.28 | 4.406 | 4.4692 | 4.5137 | 4.2505 | 35.2428 | 0.031719 |  | 62.069 | 100
19980517053000 | 1998-05-17 05:30 | 356.96 |  | 0.41 | 149.753 | 148.969 | 147.984 | 145.009 |  | 810.607 | 882.942 |  | 1.9883 | 1.8579 | 5.1621 | 4.9683 | 4.4937 | 4.6602 | 4.6792 | 4.3435 | 32.1532 | 0.028938 |  | 62.069 | 100
19980517060000 | 1998-05-17 06:00 | 353.5 |  | 6.65 | 149.26 | 149.841 | 147.219 | 146.376 |  | 819.774 | 906.943 |  | 2.0166 | 1.8839 | 5.2881 | 5.0667 | 4.5801 | 4.7349 | 4.7622 | 4.4143 | 32.7468 | 0.029472 |  | 62.069 | 100
19980517063000 | 1998-05-17 06:30 | 343.643 |  | 0.075 | 150.414 | 149.826 | 148.512 | 148.588 |  | 807.357 | 896.359 |  | 2.0227 | 1.893 | 5.2979 | 5.0935 | 4.6035 | 4.7632 | 4.7966 | 4.4258 | 32.8962 | 0.029607 |  | 62.069 | 100
19980517070000 | 1998-05-17 07:00 | 350.039 |  | 1.022 | 149.955 | 151.27 | 148.35 | 147.557 |  | 800.523 | 884.359 |  | 2.0028 | 1.8747 | 5.2437 | 5.0134 | 4.541 | 4.6982 | 4.7463 | 4.3708 | 32.4909 | 0.029242 |  | 62.069 | 100
19980517073000 | 1998-05-17 07:30 | 351.743 |  | 0 | 150.641 | 150.683 | 148.647 | 148.207 |  | 807.523 | 888.526 |  | 2.0157 | 1.8839 | 5.2781 | 5.082 | 4.5791 | 4.7119 | 4.7708 | 4.4143 | 32.7358 | 0.029462 |  | 62.069 | 100
19980517080000 | 1998-05-17 08:00 | 481.478 |  | 2.125 | 151.087 | 155.267 | 149.502 | 152.049 |  | 1164.617 | 1249.203 |  | 4.7158 | 2.4247 | 7.1443 | 7.0825 | 6.4407 | 6.5027 | 6.5461 | 6.2798 | 47.1366 | 0.042423 |  | 62.069 | 100
19980517083000 | 1998-05-17 08:30 | 627.046 |  | 4.208 | 154.167 | 155.726 | 152.99 | 152.755 |  | 1472.042 | 1578.795 |  | 6.9666 | 6.9314 | 7.6523 | 7.5959 | 6.8557 | 6.8787 | 6.9368 | 6.6826 | 56.5 | 0.05085 |  | 62.069 | 100
19980517090000 | 1998-05-17 09:00 | 632.026 |  | 4.086 | 153.668 | 153.879 | 155.573 | 155.364 |  | 1485.376 | 1586.796 |  | 7.1572 | 7.0876 | 7.8987 | 7.8232 | 7.052 | 7.0198 | 7.0901 | 6.8452 | 57.9738 | 0.052176 |  | 62.069 | 100
19980517093000 | 1998-05-17 09:30 | 633.258 |  | 2.615 | 152.935 | 152.605 | 157.004 | 154.337 |  | 1470.876 | 1568.962 |  | 7.0664 | 7.0215 | 7.8018 | 7.7102 | 6.9695 | 6.9343 | 6.9932 | 6.7781 | 57.275 | 0.051547 |  | 62.069 | 100
19980517100000 | 1998-05-17 10:00 | 633.547 |  | 3.229 | 152.337 | 153.362 | 156.673 | 154.6 |  | 1470.792 | 1568.712 |  | 7.0657 | 7.0305 | 7.801 | 7.7156 | 6.9771 | 6.9504 | 7.0007 | 6.7871 | 57.3281 | 0.051595 |  | 62.069 | 100
19980517103000 | 1998-05-17 10:30 | 601.723 |  | 1.758 | 152.46 | 152.908 | 156.668 | 154.641 |  | 1356.289 | 1450.625 |  | 6.6108 | 6.5322 | 7.238 | 7.0955 | 6.5049 | 6.427 | 6.4858 | 6.3057 | 53.1999 | 0.04788 |  | 62.069 | 100
19980517110000 | 1998-05-17 11:00 | 585.706 |  | 2.246 | 150.577 | 149.886 | 154.409 | 149.391 |  | 1334.288 | 1423.874 |  | 6.4629 | 6.4026 | 7.0718 | 6.9106 | 6.3867 | 6.3333 | 6.3943 | 6.1897 | 52.1519 | 0.046937 |  | 62.069 | 100
19980517113000 | 1998-05-17 11:30 | 578.838 |  | 1.263 | 149.801 | 150.85 | 151.778 | 149.613 |  | 1324.038 | 1413.957 |  | 6.4424 | 6.3584 | 7.0459 | 6.8779 | 6.3516 | 6.3125 | 6.3569 | 6.1609 | 51.9065 | 0.046716 |  | 62.069 | 100
19980517120000 | 1998-05-17 12:00 | 574.879 |  | 1.386 | 151.201 | 151.644 | 152.411 | 152.14 |  | 1341.122 | 1432.708 |  | 6.4453 | 6.3796 | 7.0581 | 6.9038 | 6.3699 | 6.3225 | 6.3674 | 6.1807 | 52.0273 | 0.046825 |  | 62.069 | 100
19980517123000 | 1998-05-17 12:30 | 578.104 |  | 1.387 | 150.43 | 151.098 | 153.299 | 151.098 |  | 1342.289 | 1427.708 |  | 6.4431 | 6.3735 | 7.0442 | 6.9229 | 6.3821 | 6.3264 | 6.3843 | 6.1807 | 52.0572 | 0.046851 |  | 62.069 | 100
19980517130000 | 1998-05-17 13:00 | 576.295 |  | 1.878 | 150.624 | 150.706 | 153.455 | 151.696 |  | 1343.372 | 1432.625 |  | 6.46 | 6.3843 | 7.0833 | 6.9343 | 6.3875 | 6.3325 | 6.3896 | 6.1904 | 52.1619 | 0.046946 |  | 62.069 | 100
19980517133000 | 1998-05-17 13:30 | 618.841 |  | 2.364 | 150.229 | 152.934 | 153.505 | 153.676 |  | 1503.793 | 1609.796 |  | 7.0283 | 6.981 | 7.7751 | 7.6951 | 6.9497 | 6.9343 | 6.9788 | 6.7742 | 57.1165 | 0.051405 |  | 62.069 | 100
19980517140000 | 1998-05-17 14:00 | 630.742 |  | 2.86 | 152.521 | 151.84 | 156.32 | 153.078 |  | 1451.042 | 1547.461 |  | 7.051 | 6.9465 | 7.7773 | 7.6401 | 6.9443 | 6.8689 | 6.926 | 6.7239 | 56.878 | 0.05119 |  | 62.069 | 100
19980517143000 | 1998-05-17 14:30 | 599.259 |  | 1.872 | 151.498 | 151.319 | 155.402 | 152.31 |  | 1324.871 | 1419.041 |  | 6.5347 | 6.4438 | 7.1426 | 6.9961 | 6.45 | 6.3455 | 6.4172 | 6.2385 | 52.5684 | 0.047312 |  | 62.069 | 100
19980517150000 | 1998-05-17 15:00 | 564.289 |  | 1.877 | 149.27 | 149.69 | 152.415 | 147.957 |  | 1282.953 | 1369.873 |  | 6.241 | 6.1501 | 6.7979 | 6.6101 | 6.1699 | 6.1243 | 6.1746 | 5.9785 | 50.2464 | 0.045222 |  | 62.069 | 100
19980517153000 | 1998-05-17 15:30 | 557.211 |  | 1.143 | 149.867 | 150.979 | 149.622 | 148.009 |  | 1270.62 | 1356.706 |  | 6.2288 | 6.1501 | 6.7756 | 6.5994 | 6.1631 | 6.1523 | 6.1958 | 5.9731 | 50.2382 | 0.045214 |  | 62.069 | 100
19980517160000 | 1998-05-17 16:00 | 557.709 |  | 1.263 | 150.959 | 150.484 | 149.835 | 148.752 |  | 1269.37 | 1361.372 |  | 6.2546 | 6.1653 | 6.813 | 6.6675 | 6.1875 | 6.1609 | 6.2087 | 5.9907 | 50.4482 | 0.045403 |  | 62.069 | 100
19980517163000 | 1998-05-17 16:30 | 608.486 |  | 17.766 | 150.672 | 153.336 | 150.587 | 151.851 |  | 1419.041 | 1517.544 |  | 6.8345 | 6.7444 | 7.5159 | 7.4189 | 6.7322 | 6.7063 | 6.762 | 6.5437 | 55.2579 | 0.049732 |  | 62.069 | 100
19980517170000 | 1998-05-17 17:00 | 633.154 |  | 2.736 | 152.844 | 155.069 | 154.916 | 156.554 |  | 1452.958 | 1553.211 |  | 7.052 | 6.9727 | 7.8027 | 7.6501 | 6.9587 | 6.9016 | 6.9604 | 6.7476 | 57.0458 | 0.051341 |  | 62.069 | 100
19980517173000 | 1998-05-17 17:30 | 581.118 |  | 1.753 | 152.696 | 150.588 | 156.458 | 151.578 |  | 1338.122 | 1425.708 |  | 6.521 | 6.427 | 7.1418 | 6.9954 | 6.4478 | 6.3936 | 6.4492 | 6.2378 | 52.6136 | 0.047352 |  | 62.069 | 100
19980517180000 | 1998-05-17 18:00 | 576.19 |  | 1.877 | 149.984 | 151.681 | 153.654 | 151.434 |  | 1312.954 | 1398.707 |  | 6.3896 | 6.3271 | 6.9893 | 6.8323 | 6.3232 | 6.3096 | 6.3577 | 6.1462 | 51.675 | 0.046508 |  | 62.069 | 100
19980517183000 | 1998-05-17 18:30 | 573.909 |  | 1.509 | 150.708 | 151.016 | 153.49 | 152.254 |  | 1314.621 | 1402.124 |  | 6.4216 | 6.3569 | 7.0359 | 6.9199 | 6.353 | 6.3379 | 6.3943 | 6.1731 | 51.9926 | 0.046793 |  | 62.069 | 100
19980517190000 | 1998-05-17 19:00 | 578.077 |  | 1.757 | 150.307 | 151.042 | 153.75 | 151.784 |  | 1316.204 | 1401.957 |  | 6.418 | 6.3318 | 7.0229 | 6.8772 | 6.3491 | 6.3179 | 6.3767 | 6.1531 | 51.8467 | 0.046662 |  | 62.069 | 100
19980517193000 | 1998-05-17 19:30 | 573.936 |  | 1.387 | 150.65 | 152.135 | 154.03 | 152.383 |  | 1330.455 | 1416.624 |  | 6.4561 | 6.3652 | 7.0686 | 6.907 | 6.3867 | 6.3491 | 6.4087 | 6.176 | 52.1174 | 0.046906 |  | 62.069 | 100
19980517200000 | 1998-05-17 20:00 | 575.194 |  | 2 | 151.347 | 152.409 | 155.031 | 153.399 |  | 1323.788 | 1412.707 |  | 6.4363 | 6.3347 | 7.0466 | 6.8794 | 6.3674 | 6.3247 | 6.3835 | 6.1455 | 51.9181 | 0.046726 |  | 62.069 | 100
19980517203000 | 1998-05-17 20:30 | 575.351 |  | 1.632 | 151.559 | 152.187 | 155.529 | 154.167 |  | 1327.038 | 1413.291 |  | 6.4331 | 6.3545 | 7.0427 | 6.8542 | 6.3674 | 6.3301 | 6.3806 | 6.1563 | 51.9189 | 0.046727 |  | 62.069 | 100
19980517210000 | 1998-05-17 21:00 | 573.647 |  | 2.363 | 151.237 | 152.368 | 155.267 | 153.358 |  | 1327.705 | 1414.374 |  | 6.4529 | 6.3767 | 7.0625 | 6.9023 | 6.3796 | 6.353 | 6.3979 | 6.1829 | 52.1078 | 0.046897 |  | 62.069 | 100
19980517213000 | 1998-05-17 21:30 | 573.804 |  | 1.63 | 150.997 | 151.899 | 155.092 | 152.889 |  | 1327.705 | 1415.207 |  | 6.4529 | 6.3469 | 7.0632 | 6.884 | 6.3867 | 6.321 | 6.385 | 6.1616 | 52.0013 | 0.046801 |  | 62.069 | 100
19980517220000 | 1998-05-17 22:00 | 575.718 |  | 21.298 | 150.732 | 151.455 | 154.703 | 152.693 |  | 1319.788 | 1408.624 |  | 6.3958 | 6.3232 | 6.9788 | 6.8306 | 6.3247 | 6.2959 | 6.3423 | 6.144 | 51.6353 | 0.046472 |  | 62.069 | 100
19980517223000 | 1998-05-17 22:30 | 610.321 |  | 2.363 | 150.359 | 152.59 | 154.28 | 153.332 |  | 1434.625 | 1532.127 |  | 6.8435 | 6.7795 | 7.5378 | 7.4448 | 6.772 | 6.7544 | 6.8008 | 6.5803 | 55.5131 | 0.049962 |  | 62.069 | 100
19980517230000 | 1998-05-17 23:00 | 630.034 |  | 3.106 | 152.693 | 155.405 | 156.482 | 157.138 |  | 1454.208 | 1551.295 |  | 7.0679 | 6.9688 | 7.792 | 7.6484 | 6.9543 | 6.9001 | 6.9673 | 6.739 | 57.0378 | 0.051334 |  | 62.069 | 100
19980517233000 | 1998-05-17 23:30 | 630.034 |  | 2.611 | 154.344 | 156.096 | 158.182 | 157.581 |  | 1459.792 | 1552.795 |  | 7.0251 | 6.9253 | 7.7302 | 7.5752 | 6.9246 | 6.8557 | 6.9153 | 6.6987 | 56.6501 | 0.050985 |  | 62.069 | 100
19980518000000 | 1998-05-18 | 610.111 |  | 2.611 | 154.754 | 155.693 | 158.671 | 156.931 |  | 1379.873 | 1473.376 |  | 6.6711 | 6.5918 | 7.2998 | 7.1602 | 6.572 | 6.4927 | 6.5393 | 6.3691 | 53.696 | 0.048326 |  | 62.069 | 100
19980518003000 | 1998-05-18 00:30 | 578.549 |  | 1.879 | 152.448 | 149.974 | 156.405 | 151.459 |  | 1326.621 | 1413.124 |  | 6.3928 | 6.3081 | 6.9863 | 6.8489 | 6.3142 | 6.2715 | 6.3149 | 6.1279 | 51.5646 | 0.046408 |  | 62.069 | 100
19980518010000 | 1998-05-18 01:00 | 571.393 |  | 2.487 | 149.998 | 150.846 | 153.421 | 151.589 |  | 1316.954 | 1404.124 |  | 6.4041 | 6.334 | 6.9741 | 6.8413 | 6.3232 | 6.3049 | 6.3501 | 6.1555 | 51.6872 | 0.046518 |  | 62.069 | 100
19980518013000 | 1998-05-18 01:30 | 568.299 |  | 1.511 | 151.027 | 152.058 | 153.643 | 153.296 |  | 1312.121 | 1401.29 |  | 6.553 | 4.3267 | 7.1724 | 7.0649 | 6.4722 | 6.4363 | 6.4675 | 6.2759 | 50.7689 | 0.045692 |  | 62.069 | 100
19980518020000 | 1998-05-18 02:00 | 506.041 |  | 1.39 | 150.018 | 148.737 | 153.628 | 148.489 |  | 1192.201 | 1271.786 |  | 5.9822 | 4.1008 | 6.4783 | 6.2959 | 5.948 | 5.9326 | 5.9822 | 5.7488 | 46.4688 | 0.041822 |  | 62.069 | 100
19980518023000 | 1998-05-18 02:30 | 502.292 |  | 0.897 | 149.448 | 150.521 | 150.542 | 147.056 |  | 1176.284 | 1254.453 |  | 5.6702 | 5.6978 | 6.0669 | 5.8892 | 5.6228 | 5.6472 | 5.696 | 5.4451 | 45.7352 | 0.041162 |  | 62.069 | 100
19980518030000 | 1998-05-18 03:00 | 502.711 |  | 1.017 | 150.04 | 149.778 | 148.795 | 145.323 |  | 1165.367 | 1248.119 |  | 5.6953 | 5.7053 | 6.0913 | 5.9175 | 5.635 | 5.6533 | 5.7046 | 5.4475 | 45.8498 | 0.041265 |  | 62.069 | 100
19980518033000 | 1998-05-18 03:30 | 507.43 |  | 0.778 | 149.98 | 150.82 | 147.84 | 146.365 |  | 1170.117 | 1253.453 |  | 5.6709 | 5.6794 | 6.0776 | 5.8831 | 5.6221 | 5.6404 | 5.6892 | 5.4414 | 45.7041 | 0.041134 |  | 62.069 | 100
19980518040000 | 1998-05-18 04:00 | 504.677 |  | 1.145 | 150.137 | 150.846 | 148.283 | 146.638 |  | 1159.783 | 1241.952 |  | 5.6899 | 5.7046 | 6.1013 | 5.928 | 5.6375 | 5.6626 | 5.7136 | 5.4475 | 45.885 | 0.041296 |  | 62.069 | 100
19980518043000 | 1998-05-18 04:30 | 504.992 |  | 0.529 | 150.552 | 151.094 | 148.606 | 147.133 |  | 1165.45 | 1246.952 |  | 5.6985 | 5.6931 | 6.0884 | 5.8906 | 5.6458 | 5.6482 | 5.7075 | 5.4421 | 45.8142 | 0.041233 |  | 62.069 | 100
19980518050000 | 1998-05-18 05:00 | 502.895 |  | 1.141 | 150.643 | 151.212 | 148.742 | 148.242 |  | 1170.367 | 1251.119 |  | 5.6587 | 5.6885 | 6.0615 | 5.8884 | 5.6138 | 5.6497 | 5.6953 | 5.4292 | 45.6851 | 0.041117 |  | 62.069 | 100
19980518053000 | 1998-05-18 05:30 | 542.793 |  | 0.897 | 150.909 | 151.733 | 149.287 | 148.515 |  | 1298.121 | 1393.29 |  | 6.1477 | 6.2417 | 6.7146 | 6.5872 | 6.1135 | 6.1555 | 6.1868 | 5.9487 | 50.0957 | 0.045086 |  | 62.069 | 100
19980518060000 | 1998-05-18 06:00 | 634.543 |  | 3.106 | 151.595 | 153.311 | 150.399 | 151.825 |  | 1458.875 | 1563.545 |  | 7.0854 | 7.1641 | 7.8262 | 7.7295 | 7.0046 | 6.9871 | 7.0381 | 6.8062 | 57.6412 | 0.051877 |  | 62.069 | 100
19980518063000 | 1998-05-18 06:30 | 638.344 |  | 2.368 | 151.952 | 151.892 | 153.848 | 153.625 |  | 1464.542 | 1563.628 |  | 7.0488 | 7.1343 | 7.7751 | 7.6484 | 6.958 | 6.9229 | 6.9795 | 6.759 | 57.226 | 0.051503 |  | 62.069 | 100
19980518070000 | 1998-05-18 07:00 | 638.895 |  | 22.416 | 151.286 | 151.804 | 155.022 | 153.536 |  | 1470.625 | 1564.962 |  | 7.0405 | 7.1296 | 7.7668 | 7.6973 | 6.9473 | 6.9207 | 6.9788 | 6.762 | 57.243 | 0.051519 |  | 62.069 | 100
19980518073000 | 1998-05-18 07:30 | 639.34 |  | 2.489 | 151.351 | 151.623 | 155.45 | 152.86 |  | 1458.792 | 1556.545 |  | 7.0374 | 7.1274 | 7.76 | 7.6797 | 6.9482 | 6.9131 | 6.9695 | 6.7559 | 57.1912 | 0.051472 |  | 62.069 | 100
19980518080000 | 1998-05-18 08:00 | 635.172 |  | 2.858 | 151.611 | 153.526 | 155.801 | 154.763 |  | 1456.625 | 1551.628 |  | 7.0298 | 7.1016 | 7.7644 | 7.6577 | 6.9412 | 6.8833 | 6.9329 | 6.7383 | 57.0492 | 0.051344 |  | 62.069 | 100
19980518083000 | 1998-05-18 08:30 | 639.891 |  | 2.614 | 152.169 | 153.304 | 156.5 | 155.037 |  | 1475.542 | 1566.878 |  | 7.0657 | 7.1389 | 7.8096 | 7.7034 | 6.9839 | 6.8984 | 6.9565 | 6.7551 | 57.3115 | 0.05158 |  | 62.069 | 100
19980518090000 | 1998-05-18 09:00 | 638.082 |  | 3.348 | 152.529 | 154.32 | 156.779 | 155.31 |  | 1476.209 | 1571.712 |  | 7.0825 | 7.1479 | 7.8157 | 7.699 | 7.0046 | 6.9229 | 6.981 | 6.7749 | 57.4285 | 0.051686 |  | 62.069 | 100
19980518093000 | 1998-05-18 09:30 | 635.487 |  | 2.856 | 152.899 | 154.217 | 157.193 | 155.702 |  | 1473.876 | 1570.545 |  | 7.0359 | 7.1321 | 7.7798 | 7.6775 | 6.968 | 6.8984 | 6.9573 | 6.7551 | 57.2041 | 0.051484 |  | 62.069 | 100
19980518100000 | 1998-05-18 10:00 | 635.251 |  | 3.591 | 153.524 | 154.712 | 157.735 | 156.444 |  | 1478.042 | 1575.045 |  | 7.0779 | 7.1609 | 7.8384 | 7.7241 | 6.9985 | 6.9229 | 6.9839 | 6.7871 | 57.4937 | 0.051744 |  | 62.069 | 100
19980518103000 | 1998-05-18 10:30 | 637.4 |  | 2.979 | 154.028 | 156.001 | 158.267 | 157.239 |  | 1470.292 | 1571.295 |  | 7.061 | 7.1167 | 7.7888 | 7.6729 | 6.9673 | 6.8909 | 6.9565 | 6.7537 | 57.2078 | 0.051487 |  | 62.069 | 100
19980518110000 | 1998-05-18 11:00 | 632.105 |  | 3.834 | 154.301 | 156.012 | 158.458 | 157.25 |  | 1457.375 | 1551.045 |  | 6.9771 | 7.0352 | 7.7019 | 7.5295 | 6.8916 | 6.8184 | 6.8833 | 6.6682 | 56.5052 | 0.050855 |  | 62.069 | 100
19980518113000 | 1998-05-18 11:30 | 629.615 |  | 2.976 | 154.3 | 155.543 | 158.42 | 157.028 |  | 1458.042 | 1552.211 |  | 6.9695 | 7.0564 | 7.6929 | 7.5881 | 6.8923 | 6.8374 | 6.894 | 6.6873 | 56.6179 | 0.050956 |  | 62.069 | 100
19980518120000 | 1998-05-18 12:00 | 633.442 |  | 4.324 | 154.445 | 156.141 | 158.597 | 157.626 |  | 1463.375 | 1558.545 |  | 6.981 | 7.0664 | 7.7112 | 7.5959 | 6.9023 | 6.8435 | 6.9138 | 6.6941 | 56.7082 | 0.051037 |  | 62.069 | 100
19980518123000 | 1998-05-18 12:30 | 630.899 |  | 21.292 | 154.733 | 156.569 | 158.906 | 157.064 |  | 1459.125 | 1551.961 |  | 6.9727 | 7.0549 | 7.7004 | 7.5769 | 6.884 | 6.8323 | 6.9031 | 6.6719 | 56.5962 | 0.050937 |  | 62.069 | 100
19980518130000 | 1998-05-18 13:00 | 629.877 |  | 3.834 | 155.28 | 157.194 | 159.383 | 158.431 |  | 1459.208 | 1555.211 |  | 6.9871 | 7.0671 | 7.7217 | 7.5989 | 6.9116 | 6.8445 | 6.926 | 6.6895 | 56.7464 | 0.051072 |  | 62.069 | 100
19980518133000 | 1998-05-18 13:30 | 630.27 |  | 3.465 | 155.739 | 157.962 | 159.941 | 158.705 |  | 1456.042 | 1553.878 |  | 6.9824 | 7.051 | 7.7058 | 7.5867 | 6.8894 | 6.8374 | 6.9099 | 6.6772 | 56.6398 | 0.050976 |  | 62.069 | 100
19980518140000 | 1998-05-18 14:00 | 632.918 |  | 4.324 | 156.246 | 157.999 | 160.47 | 160.969 |  | 1465.459 | 1557.711 |  | 6.9641 | 7.0618 | 7.6875 | 7.5981 | 6.875 | 6.8521 | 6.9106 | 6.6812 | 56.6304 | 0.050967 |  | 62.069 | 100
19980518143000 | 1998-05-18 14:30 | 632.341 |  | 3.833 | 156.451 | 157.153 | 160.76 | 158.886 |  | 1454.208 | 1549.044 |  | 6.9734 | 7.0496 | 7.6936 | 7.5935 | 6.8916 | 6.8542 | 6.9268 | 6.6858 | 56.6685 | 0.051002 |  | 62.069 | 100
19980518150000 | 1998-05-18 15:00 | 628.854 |  | 4.321 | 156.648 | 158.948 | 160.96 | 160.433 |  | 1453.708 | 1548.461 |  | 6.9458 | 7.0054 | 7.6584 | 7.5486 | 6.8611 | 6.8176 | 6.8887 | 6.6377 | 56.3633 | 0.050727 |  | 62.069 | 100
19980518153000 | 1998-05-18 15:30 | 632.053 |  | 3.462 | 157.252 | 158.726 | 161.499 | 160.212 |  | 1458.792 | 1553.628 |  | 6.9863 | 7.0488 | 7.7051 | 7.6028 | 6.9077 | 6.8459 | 6.9238 | 6.6787 | 56.6991 | 0.051029 |  | 62.069 | 100
19980518160000 | 1998-05-18 16:00 | 630.034 |  | 4.201 | 157.576 | 159.454 | 161.973 | 160.692 |  | 1461.459 | 1557.128 |  | 6.9702 | 7.0474 | 7.7019 | 7.5891 | 6.8801 | 6.8452 | 6.9199 | 6.6675 | 56.6213 | 0.050959 |  | 62.069 | 100
19980518163000 | 1998-05-18 16:30 | 629.484 |  | 3.464 | 157.878 | 159.413 | 162.209 | 160.651 |  | 1449.208 | 1543.711 |  | 6.9382 | 6.9924 | 7.6423 | 7.5181 | 6.842 | 6.7957 | 6.8635 | 6.6223 | 56.2145 | 0.050593 |  | 62.069 | 100
19980518170000 | 1998-05-18 17:00 | 630.925 |  | 4.568 | 157.674 | 158.696 | 161.953 | 160.677 |  | 1454.792 | 1547.461 |  | 6.9299 | 6.9924 | 7.6362 | 7.5349 | 6.8506 | 6.7964 | 6.8635 | 6.6255 | 56.2294 | 0.050606 |  | 62.069 | 100
19980518173000 | 1998-05-18 17:30 | 626.285 |  | 3.83 | 157.959 | 159.439 | 162.102 | 161.172 |  | 1458.208 | 1553.295 |  | 6.9436 | 7.0366 | 7.6646 | 7.573 | 6.865 | 6.8169 | 6.8872 | 6.6567 | 56.4436 | 0.050799 |  | 62.069 | 100
19980518180000 | 1998-05-18 18:00 | 624.11 |  | 5.427 | 158.088 | 159.295 | 162.313 | 160.285 |  | 1453.792 | 1550.795 |  | 6.958 | 7.0366 | 7.6746 | 7.5547 | 6.8765 | 6.8162 | 6.8872 | 6.6482 | 56.452 | 0.050807 |  | 62.069 | 100
19980518183000 | 1998-05-18 18:30 | 628.487 |  | 4.198 | 158.233 | 159.893 | 162.462 | 160.883 |  | 1456.208 | 1551.628 |  | 6.9641 | 7.0313 | 7.7073 | 7.5623 | 6.8826 | 6.8291 | 6.9038 | 6.656 | 56.5365 | 0.050883 |  | 62.069 | 100
19980518190000 | 1998-05-18 19:00 | 625.945 |  | 4.813 | 158.323 | 159.646 | 162.56 | 161.378 |  | 1456.792 | 1555.878 |  | 6.9473 | 7.032 | 7.6624 | 7.5684 | 6.874 | 6.8313 | 6.9023 | 6.6514 | 56.4691 | 0.050822 |  | 62.069 | 100
19980518193000 | 1998-05-18 19:30 | 625.237 |  | 3.708 | 158.32 | 160.141 | 162.615 | 161.131 |  | 1454.375 | 1553.045 |  | 6.9612 | 7.0266 | 7.689 | 7.563 | 6.8765 | 6.8284 | 6.8933 | 6.6521 | 56.4901 | 0.050841 |  | 62.069 | 100
19980518200000 | 1998-05-18 20:00 | 625.289 |  | 4.69 | 158.797 | 160.584 | 163.045 | 161.574 |  | 1454.875 | 1550.211 |  | 6.9688 | 7.0215 | 7.679 | 7.5715 | 6.8726 | 6.8252 | 6.8977 | 6.6482 | 56.4845 | 0.050836 |  | 62.069 | 100
19980518203000 | 1998-05-18 20:30 | 568.955 |  | 2.853 | 157.924 | 154.917 | 162.106 | 156.154 |  | 1353.039 | 1437.708 |  | 6.4873 | 6.5476 | 7.1289 | 6.9573 | 6.4294 | 6.385 | 6.4417 | 6.2012 | 52.5784 | 0.047321 |  | 62.069 | 100
19980518210000 | 1998-05-18 21:00 | 571.55 |  | 3.589 | 154.314 | 154.396 | 158.285 | 154.891 |  | 1339.705 | 1421.291 |  | 6.4468 | 6.5322 | 7.0754 | 6.9282 | 6.4026 | 6.3674 | 6.4302 | 6.1951 | 52.3779 | 0.04714 |  | 62.069 | 100
19980518213000 | 1998-05-18 21:30 | 576.347 |  | 2.157 | 153.225 | 154.004 | 157.111 | 154.994 |  | 1333.372 | 1412.874 |  | 6.4988 | 6.543 | 7.1213 | 6.9497 | 6.4407 | 6.3928 | 6.4521 | 6.2004 | 52.5988 | 0.047339 |  | 62.069 | 100
19980518220000 | 1998-05-18 22:00 | 594.147 |  | 4.447 | 152.847 | 156.35 | 156.83 | 157.34 |  | 1410.374 | 1507.21 |  | 6.7102 | 6.7817 | 7.3784 | 7.2664 | 6.6438 | 6.6431 | 6.6865 | 6.4309 | 54.541 | 0.049087 |  | 62.069 | 100
19980518223000 | 1998-05-18 22:30 | 614.751 |  | 3.713 | 156.565 | 160.012 | 160.582 | 161.497 |  | 1442.625 | 1539.044 |  | 6.8704 | 6.9077 | 7.5623 | 7.4172 | 6.7856 | 6.7268 | 6.7903 | 6.5322 | 55.5925 | 0.050033 |  | 62.069 | 100
19980518230000 | 1998-05-18 23:00 | 618.107 |  | 4.203 | 158.8 | 159.687 | 162.875 | 161.172 |  | 1449.875 | 1542.294 |  | 6.8618 | 6.9436 | 7.5601 | 7.4563 | 6.7856 | 6.7476 | 6.813 | 6.5781 | 55.7461 | 0.050171 |  | 62.069 | 100
19980518233000 | 1998-05-18 23:30 | 617.976 |  | 3.956 | 158.463 | 159.557 | 162.585 | 160.795 |  | 1450.792 | 1546.211 |  | 6.8811 | 6.9543 | 7.5928 | 7.4792 | 6.7939 | 6.7537 | 6.8215 | 6.5903 | 55.8668 | 0.05028 |  | 62.069 | 100
19980519000000 | 1998-05-19 | 525.229 |  | 1.509 | 157.147 | 152.379 | 161.243 | 154.111 |  | 1239.119 | 1311.538 |  | 5.9861 | 6.0051 | 6.469 | 6.2759 | 5.9563 | 5.8992 | 5.9524 | 5.7258 | 48.2698 | 0.043443 |  | 62.069 | 100
19980519003000 | 1998-05-19 00:30 | 522.346 |  | 1.263 | 151.094 | 151.167 | 155.196 | 152.157 |  | 1233.785 | 1304.037 |  | 5.9341 | 5.9548 | 6.4102 | 6.2219 | 5.8945 | 5.8801 | 5.9211 | 5.6809 | 47.8976 | 0.043108 |  | 62.069 | 100
19980519010000 | 1998-05-19 01:00 | 525.282 |  | 1.753 | 150.672 | 150.842 | 153.755 | 151.337 |  | 1237.536 | 1305.537 |  | 5.928 | 5.929 | 6.3904 | 6.1799 | 5.873 | 5.8601 | 5.9075 | 5.6504 | 47.7183 | 0.042946 |  | 62.069 | 100
19980519013000 | 1998-05-19 01:30 | 474.531 |  | 0.527 | 150.223 | 148.392 | 152.824 | 148.887 |  | 1062.281 | 1115.782 |  | 5.249 | 5.2124 | 5.4688 | 5.2942 | 5.1704 | 5.1499 | 5.22 | 4.9492 | 41.7139 | 0.037543 |  | 62.069 | 100
19980519020000 | 1998-05-19 02:00 | 419.35 |  | 1.999 | 148.144 | 149.94 | 148.547 | 143.257 |  | 1012.279 | 1057.78 |  | 4.969 | 4.9219 | 5.146 | 4.9546 | 4.928 | 5.0354 | 5.0867 | 4.7524 | 39.794 | 0.035815 |  | 62.069 | 100
19980519023000 | 1998-05-19 02:30 | 417.436 |  | 0.198 | 149.629 | 150.42 | 146.943 | 146.955 |  | 1027.529 | 1066.781 |  | 4.9836 | 4.9492 | 5.1912 | 4.9873 | 4.9463 | 5.04 | 5.0813 | 4.7524 | 39.9313 | 0.035938 |  | 62.069 | 100
19980519030000 | 1998-05-19 03:00 | 421.866 |  | 19.597 | 149.469 | 149.26 | 147.62 | 145.795 |  | 1001.029 | 1034.613 |  | 4.9622 | 4.9087 | 5.1621 | 4.9683 | 4.9141 | 5.0002 | 5.0522 | 4.7349 | 39.7027 | 0.035732 |  | 62.069 | 100
19980519033000 | 1998-05-19 03:30 | 419.114 |  | 0.282 | 149.965 | 152.932 | 148.111 | 149.219 |  | 1021.779 | 1056.947 |  | 4.9729 | 4.9097 | 5.1721 | 4.9463 | 4.9255 | 4.9912 | 5.0469 | 4.7241 | 39.6887 | 0.03572 |  | 62.069 | 100
19980519040000 | 1998-05-19 04:00 | 417.672 |  | 3.955 | 151.307 | 150.586 | 149.672 | 147.368 |  | 1020.279 | 1061.447 |  | 4.9653 | 4.9697 | 5.1667 | 5.0325 | 4.9219 | 5.0256 | 5.0828 | 4.7615 | 39.926 | 0.035933 |  | 62.069 | 100
19980519043000 | 1998-05-19 04:30 | 426.27 |  | 0.286 | 149.882 | 150.117 | 148.111 | 146.651 |  | 1014.279 | 1049.363 |  | 4.9453 | 4.9255 | 5.1438 | 4.9561 | 4.895 | 4.9836 | 5.0325 | 4.731 | 39.6128 | 0.035652 |  | 62.069 | 100
19980519050000 | 1998-05-19 05:00 | 420.372 |  | 1.512 | 150.061 | 151.432 | 148.101 | 147.719 |  | 1015.362 | 1052.614 |  | 4.9478 | 4.9133 | 5.1423 | 4.9507 | 4.8965 | 4.9934 | 5.0447 | 4.7395 | 39.6282 | 0.035665 |  | 62.069 | 100
19980519053000 | 1998-05-19 05:30 | 427.896 |  | 0.285 | 150.886 | 150.272 | 149.228 | 147.797 |  | 1016.029 | 1048.363 |  | 4.9209 | 4.8936 | 5.105 | 4.9287 | 4.8669 | 4.9463 | 4.998 | 4.6997 | 39.3591 | 0.035423 |  | 62.069 | 100
19980519060000 | 1998-05-19 06:00 | 531.547 |  | 2.492 | 150.223 | 153.763 | 148.508 | 150.298 |  | 1244.952 | 1318.288 |  | 6.051 | 6.1211 | 6.5735 | 6.4355 | 5.9785 | 6.012 | 6.0669 | 5.8022 | 49.0407 | 0.044137 |  | 62.069 | 100
19980519063000 | 1998-05-19 06:30 | 626.102 |  | 4.942 | 153.115 | 154.288 | 151.67 | 152.06 |  | 1445.042 | 1550.045 |  | 6.9045 | 6.9985 | 7.6021 | 7.5417 | 6.8262 | 6.7971 | 6.8611 | 6.6194 | 56.1506 | 0.050536 |  | 62.069 | 100
19980519070000 | 1998-05-19 07:00 | 626.495 |  | 4.208 | 152.166 | 151.75 | 153.857 | 152.493 |  | 1456.375 | 1555.878 |  | 7.0215 | 7.1016 | 7.74 | 7.6768 | 6.9329 | 6.9092 | 6.968 | 6.7185 | 57.0685 | 0.051362 |  | 62.069 | 100
19980519073000 | 1998-05-19 07:30 | 635.198 |  | 3.224 | 151.236 | 152.198 | 154.777 | 153.683 |  | 1473.876 | 1571.712 |  | 7.1313 | 7.1885 | 7.8774 | 7.74 | 7.0405 | 6.9709 | 7.0352 | 6.813 | 57.7968 | 0.052017 |  | 62.069 | 100
19980519080000 | 1998-05-19 08:00 | 636.011 |  | 3.719 | 151.304 | 151.862 | 155.733 | 154.09 |  | 1474.042 | 1570.795 |  | 7.042 | 7.1304 | 7.7783 | 7.698 | 6.9626 | 6.9138 | 6.9717 | 6.7498 | 57.2466 | 0.051522 |  | 62.069 | 100
19980519083000 | 1998-05-19 08:30 | 635.513 |  | 3.106 | 151.349 | 152.32 | 156.108 | 154.548 |  | 1470.292 | 1566.128 |  | 7.0496 | 7.1267 | 7.782 | 7.6768 | 6.9666 | 6.9063 | 6.9702 | 6.7612 | 57.2394 | 0.051515 |  | 62.069 | 100
19980519090000 | 1998-05-19 09:00 | 636.09 |  | 3.966 | 151.58 | 152.985 | 156.552 | 154.966 |  | 1476.126 | 1572.295 |  | 7.0649 | 7.1519 | 7.8125 | 7.7241 | 6.9849 | 6.9214 | 6.981 | 6.7817 | 57.4224 | 0.05168 |  | 62.069 | 100
19980519093000 | 1998-05-19 09:30 | 633.494 |  | 3.349 | 151.912 | 153.351 | 156.982 | 155.332 |  | 1480.876 | 1577.295 |  | 7.1182 | 7.158 | 7.8857 | 7.7065 | 7.0442 | 6.9229 | 7.0366 | 6.7825 | 57.6546 | 0.051889 |  | 62.069 | 100
19980519100000 | 1998-05-19 10:00 | 633.73 |  | 3.843 | 152.059 | 152.856 | 157.18 | 155.579 |  | 1471.959 | 1567.378 |  | 7.093 | 7.1426 | 7.8384 | 7.6875 | 7.0122 | 6.9016 | 7.0039 | 6.7688 | 57.448 | 0.051703 |  | 62.069 | 100
19980519103000 | 1998-05-19 10:30 | 636.43 |  | 3.35 | 152.21 | 153.392 | 157.434 | 155.62 |  | 1480.542 | 1577.212 |  | 7.1191 | 7.1558 | 7.8674 | 7.731 | 7.0374 | 6.9023 | 7.0168 | 6.7742 | 57.604 | 0.051844 |  | 62.069 | 100
19980519110000 | 1998-05-19 11:00 | 634.884 |  | 4.088 | 152.654 | 154.031 | 157.883 | 155.764 |  | 1476.626 | 1572.962 |  | 7.093 | 7.1282 | 7.8484 | 7.6768 | 7.0198 | 6.8977 | 7 | 6.7688 | 57.4327 | 0.051689 |  | 62.069 | 100
19980519113000 | 1998-05-19 11:30 | 637.295 |  | 3.718 | 153.022 | 154.527 | 158.226 | 157.497 |  | 1476.542 | 1571.378 |  | 7.0876 | 7.1199 | 7.8445 | 7.679 | 7.0205 | 6.8772 | 6.9939 | 6.7537 | 57.3763 | 0.051639 |  | 62.069 | 100
19980519120000 | 1998-05-19 12:00 | 637.453 |  | 4.082 | 153.335 | 154.645 | 158.502 | 157.368 |  | 1482.959 | 1580.129 |  | 7.116 | 7.1252 | 7.8621 | 7.6775 | 7.032 | 6.8962 | 7.0093 | 6.7612 | 57.4795 | 0.051732 |  | 62.069 | 100
19980519123000 | 1998-05-19 12:30 | 636.509 |  | 3.842 | 153.659 | 154.944 | 158.973 | 157.667 |  | 1478.292 | 1575.129 |  | 7.0947 | 7.1426 | 7.8506 | 7.7065 | 7.0298 | 6.9016 | 7.0137 | 6.7695 | 57.509 | 0.051758 |  | 62.069 | 100
19980519130000 | 1998-05-19 13:00 | 635.434 |  | 4.94 | 154.056 | 157.146 | 159.331 | 159.127 |  | 1485.209 | 1583.879 |  | 7.1274 | 7.1526 | 7.9048 | 7.7302 | 7.0542 | 6.9146 | 7.0344 | 6.772 | 57.6902 | 0.051921 |  | 62.069 | 100
19980519133000 | 1998-05-19 13:30 | 635.906 |  | 4.331 | 154.925 | 156.337 | 160.186 | 157.822 |  | 1487.376 | 1585.879 |  | 7.1321 | 7.1519 | 7.885 | 7.7295 | 7.0603 | 6.9099 | 7.032 | 6.781 | 57.6817 | 0.051914 |  | 62.069 | 100
19980519140000 | 1998-05-19 14:00 | 635.329 |  | 19.12 | 155.407 | 157.157 | 160.708 | 160.128 |  | 1487.543 | 1582.879 |  | 7.1069 | 7.1609 | 7.8835 | 7.731 | 7.032 | 6.9192 | 7.0388 | 6.7825 | 57.6548 | 0.051889 |  | 62.069 | 100
19980519143000 | 1998-05-19 14:30 | 634.307 |  | 4.208 | 155.624 | 157.209 | 160.943 | 160.179 |  | 1486.126 | 1584.296 |  | 7.0854 | 7.1304 | 7.8315 | 7.7271 | 7.0244 | 6.8848 | 7.0144 | 6.7688 | 57.4668 | 0.05172 |  | 62.069 | 100
19980519150000 | 1998-05-19 15:00 | 635.959 |  | 4.942 | 156.114 | 157.833 | 161.463 | 160.556 |  | 1489.209 | 1586.462 |  | 7.0876 | 7.1572 | 7.8455 | 7.7407 | 7.0222 | 6.9116 | 7.0413 | 6.8 | 57.6061 | 0.051845 |  | 62.069 | 100
19980519153000 | 1998-05-19 15:30 | 636.902 |  | 4.331 | 156.452 | 158.576 | 161.872 | 161.299 |  | 1483.543 | 1581.962 |  | 7.0894 | 7.1443 | 7.8491 | 7.7173 | 7.0222 | 6.9023 | 7.0259 | 6.7666 | 57.5171 | 0.051765 |  | 62.069 | 100
19980519160000 | 1998-05-19 16:00 | 633.73 |  | 5.431 | 156.63 | 158.354 | 162.05 | 160.582 |  | 1488.209 | 1587.129 |  | 7.1016 | 7.1472 | 7.856 | 7.7156 | 7.0313 | 6.8977 | 7.0266 | 6.7773 | 57.5533 | 0.051798 |  | 62.069 | 100
19980519163000 | 1998-05-19 16:30 | 636.955 |  | 4.823 | 157.093 | 159.473 | 162.507 | 161.454 |  | 1488.126 | 1586.129 |  | 7.1008 | 7.1472 | 7.8455 | 7.7339 | 7.032 | 6.9077 | 7.0359 | 6.7742 | 57.5772 | 0.051819 |  | 62.069 | 100
19980519170000 | 1998-05-19 17:00 | 633.442 |  | 6.286 | 157.68 | 160.19 | 163.097 | 162.418 |  | 1497.21 | 1595.963 |  | 7.1113 | 7.1687 | 7.8682 | 7.7493 | 7.0388 | 6.9229 | 7.0535 | 6.7947 | 57.7074 | 0.051937 |  | 62.069 | 100
19980519173000 | 1998-05-19 17:30 | 631.895 |  | 21.806 | 158.228 | 159.628 | 163.664 | 161.361 |  | 1498.376 | 1597.629 |  | 7.1167 | 7.1479 | 7.8613 | 7.7263 | 7.0427 | 6.9092 | 7.0366 | 6.7749 | 57.6156 | 0.051854 |  | 62.069 | 100
19980519180000 | 1998-05-19 18:00 | 632.787 |  | 6.407 | 157.957 | 159.562 | 163.371 | 161.789 |  | 1490.959 | 1591.712 |  | 7.1167 | 7.1313 | 7.8789 | 7.6951 | 7.0374 | 6.907 | 7.042 | 6.759 | 57.5674 | 0.051811 |  | 62.069 | 100
19980519183000 | 1998-05-19 18:30 | 632.367 |  | 5.31 | 157.583 | 159.066 | 162.984 | 161.542 |  | 1493.96 | 1593.046 |  | 7.0962 | 7.1335 | 7.8469 | 7.7241 | 7.0298 | 6.9055 | 7.0413 | 6.7659 | 57.5432 | 0.051789 |  | 62.069 | 100
19980519190000 | 1998-05-19 19:00 | 637.322 |  | 7.139 | 157.048 | 157.633 | 162.365 | 159.613 |  | 1486.293 | 1581.545 |  | 7.0886 | 7.1313 | 7.8384 | 7.6807 | 7.0222 | 6.894 | 7.0276 | 6.7627 | 57.4455 | 0.051701 |  | 62.069 | 100
19980519193000 | 1998-05-19 19:30 | 581.511 |  | 4.335 | 155.113 | 152.239 | 160.442 | 153.971 |  | 1358.456 | 1444.042 |  | 6.6116 | 6.6223 | 7.2341 | 7.0632 | 6.5552 | 6.4346 | 6.5591 | 6.2927 | 53.3728 | 0.048036 |  | 62.069 | 100
19980519200000 | 1998-05-19 20:00 | 581.249 |  | 4.575 | 151.047 | 151.378 | 156.197 | 153.606 |  | 1359.122 | 1442.291 |  | 6.575 | 6.6255 | 7.1968 | 7.0657 | 6.5088 | 6.4399 | 6.5156 | 6.292 | 53.2193 | 0.047897 |  | 62.069 | 100
19980519203000 | 1998-05-19 20:30 | 525.859 |  | 1.756 | 150.693 | 151.079 | 155.801 | 153.554 |  | 1247.786 | 1329.871 |  | 6.0632 | 6.0693 | 6.5681 | 6.3936 | 6.0134 | 5.9541 | 6.0303 | 5.7886 | 48.8806 | 0.043993 |  | 62.069 | 100
19980519210000 | 1998-05-19 21:00 | 528.296 |  | 2.129 | 149.643 | 150.583 | 154.317 | 150.583 |  | 1251.619 | 1326.705 |  | 6.0669 | 6.1013 | 6.575 | 6.3904 | 6.0181 | 5.9761 | 6.05 | 5.7983 | 48.9761 | 0.044078 |  | 62.069 | 100
19980519213000 | 1998-05-19 21:30 | 532.936 |  | 1.637 | 150.028 | 150.439 | 152.474 | 150.192 |  | 1250.119 | 1326.205 |  | 6.0073 | 6.0371 | 6.5088 | 6.324 | 5.97 | 5.9351 | 6.0012 | 5.7588 | 48.5423 | 0.043688 |  | 62.069 | 100
19980519220000 | 1998-05-19 22:00 | 530.105 |  | 2.252 | 150.094 | 151.352 | 151.72 | 149.867 |  | 1254.453 | 1332.372 |  | 6.0195 | 6.0579 | 6.5078 | 6.3491 | 5.9731 | 5.9487 | 6.0173 | 5.7664 | 48.6398 | 0.043776 |  | 62.069 | 100
19980519223000 | 1998-05-19 22:30 | 532.805 |  | 2.005 | 150.611 | 150.362 | 151.69 | 148.629 |  | 1241.036 | 1317.038 |  | 6.0388 | 6.0737 | 6.5415 | 6.3889 | 5.99 | 5.9631 | 6.0388 | 5.78 | 48.8148 | 0.043933 |  | 62.069 | 100
19980519230000 | 1998-05-19 23:00 | 527.405 |  | 2.375 | 149.418 | 151.104 | 149.308 | 145.659 |  | 1213.118 | 1286.537 |  | 5.9419 | 5.9524 | 6.3936 | 6.2104 | 5.8884 | 5.8618 | 5.9211 | 5.677 | 47.8466 | 0.043062 |  | 62.069 | 100
19980519233000 | 1998-05-19 23:30 | 525.492 |  | 2.129 | 150.555 | 151.522 | 147.782 | 145.334 |  | 1220.535 | 1297.621 |  | 5.9778 | 6.0144 | 6.4453 | 6.3027 | 5.928 | 5.9121 | 5.9846 | 5.7458 | 48.3107 | 0.04348 |  | 62.069 | 100
19980520000000 | 1998-05-20 | 527.694 |  | 2.377 | 150.087 | 150.949 | 147.899 | 146.742 |  | 1201.201 | 1273.786 |  | 5.9121 | 5.9236 | 6.3767 | 6.1836 | 5.8647 | 5.8303 | 5.8984 | 5.6565 | 47.6459 | 0.042881 |  | 62.069 | 100
19980520003000 | 1998-05-20 00:30 | 426.664 |  | 0.531 | 150.071 | 149.738 | 148.164 | 146.52 |  | 1027.446 | 1083.698 |  | 5.0752 | 5.0386 | 5.2781 | 5.0867 | 5.0605 | 5.1079 | 5.1614 | 4.8425 | 40.6509 | 0.036586 |  | 62.069 | 100
19980520010000 | 1998-05-20 01:00 | 438.408 |  | 0.9 | 149.936 | 150.011 | 148.265 | 147.041 |  | 1056.864 | 1112.782 |  | 5.124 | 5.1011 | 5.3628 | 5.1599 | 5.0767 | 5.1499 | 5.2002 | 4.8989 | 41.0735 | 0.036966 |  | 62.069 | 100
19980520013000 | 1998-05-20 01:30 | 408.471 |  | 0.534 | 150.397 | 150.986 | 148.531 | 147.273 |  | 966.028 | 1016.196 |  | 4.6516 | 4.5967 | 4.7815 | 4.5242 | 4.5945 | 4.6516 | 4.7104 | 4.4128 | 36.9233 | 0.033231 |  | 62.069 | 100
19980520020000 | 1998-05-20 02:00 | 401.944 |  | 0.906 | 149.7 | 150.568 | 147.992 | 147.598 |  | 981.112 | 1029.613 |  | 4.7234 | 4.6631 | 4.8767 | 4.6021 | 4.7029 | 4.8081 | 4.853 | 4.5068 | 37.7361 | 0.033962 |  | 62.069 | 100
19980520023000 | 1998-05-20 02:30 | 348.598 |  | 0.286 | 150.04 | 150.605 | 148.246 | 147.635 |  | 845.191 | 871.358 |  | 1.6565 | 0.0078 | 5.2217 | 5.0049 | 4.9951 | 5.1262 | 5.1484 | 4.825 | 31.9856 | 0.028787 |  | 62.069 | 100
19980520030000 | 1998-05-20 03:00 | 336.775 |  | 0.656 | 148.721 | 149.327 | 147.085 | 146.109 |  | 846.191 | 872.108 |  | 0.0024 | 0.007 | 5.533 | 5.3108 | 5.2476 | 5.394 | 5.4253 | 5.0613 | 31.9814 | 0.028783 |  | 62.069 | 100
19980520033000 | 1998-05-20 03:30 | 334.494 |  | 0.167 | 149.957 | 151.436 | 147.914 | 147.723 |  | 851.024 | 863.108 |  | 0.0032 | 0.007 | 5.4124 | 5.2339 | 5.1721 | 5.3521 | 5.3804 | 4.9966 | 31.5577 | 0.028402 |  | 62.069 | 100
19980520040000 | 1998-05-20 04:00 | 338.269 |  | 1.399 | 150.486 | 150.978 | 148.901 | 147.512 |  | 844.691 | 856.941 |  | 0.004 | 0.007 | 5.4573 | 5.2246 | 5.207 | 5.3369 | 5.3604 | 4.9858 | 31.583 | 0.028425 |  | 62.069 | 100
19980520043000 | 1998-05-20 04:30 | 336.146 |  | 15.833 | 150.344 | 151.081 | 148.848 | 147.616 |  | 847.441 | 853.858 |  | 0.0032 | 0.0085 | 5.4773 | 5.2444 | 5.2231 | 5.3552 | 5.3772 | 5.0134 | 31.7023 | 0.028532 |  | 62.069 | 100
19980520050000 | 1998-05-20 05:00 | 341.074 |  | 0.658 | 149.966 | 149.869 | 148.274 | 145.166 |  | 821.107 | 832.274 |  | 0.0032 | 0.0078 | 5.4939 | 5.2559 | 5.2307 | 5.3398 | 5.3718 | 5.0002 | 31.7033 | 0.028533 |  | 62.069 | 100
19980520053000 | 1998-05-20 05:30 | 336.722 |  | 0.167 | 150.604 | 151.757 | 148.531 | 148.539 |  | 851.691 | 861.025 |  | 0.0032 | 0.0085 | 5.5671 | 5.3054 | 5.291 | 5.3872 | 5.4207 | 5.0325 | 32.0156 | 0.028814 |  | 62.069 | 100
19980520060000 | 1998-05-20 06:00 | 383.515 |  | 1.147 | 150.906 | 151.417 | 149.246 | 147.209 |  | 979.028 | 1022.529 |  | 0.0047 | 0.0085 | 6.6018 | 6.4492 | 6.0952 | 6.1868 | 6.2134 | 5.8655 | 37.4251 | 0.033683 |  | 62.069 | 100
19980520063000 | 1998-05-20 06:30 | 475.527 |  | 0.902 | 152.05 | 152.67 | 150.484 | 149.204 |  | 1157.45 | 1221.535 |  | 5.5872 | 5.4329 | 5.8403 | 5.6404 | 5.4436 | 5.459 | 5.5322 | 5.2476 | 44.1832 | 0.039765 |  | 62.069 | 100
19980520070000 | 1998-05-20 07:00 | 523.945 |  | 2.258 | 152.116 | 152.84 | 150.494 | 148.384 |  | 1274.953 | 1359.789 |  | 6.125 | 6.0188 | 6.5515 | 6.366 | 5.9717 | 5.9685 | 6.0273 | 5.7747 | 48.8035 | 0.043923 |  | 62.069 | 100
19980520073000 | 1998-05-20 07:30 | 535.401 |  | 1.766 | 151.177 | 148.492 | 149.462 | 144.284 |  | 1223.785 | 1299.121 |  | 6.0974 | 5.9731 | 6.4895 | 6.3186 | 5.9395 | 5.8992 | 5.9785 | 5.7136 | 48.4094 | 0.043568 |  | 62.069 | 100
19980520080000 | 1998-05-20 08:00 | 528.952 |  | 19.621 | 149.801 | 151.869 | 147.71 | 147.413 |  | 1228.369 | 1303.121 |  | 6.0701 | 5.9502 | 6.4338 | 6.2844 | 5.8975 | 5.8655 | 5.9426 | 5.7083 | 48.1524 | 0.043337 |  | 62.069 | 100
19980520083000 | 1998-05-20 08:30 | 531.442 |  | 1.273 | 150.877 | 150.79 | 149.235 | 146.582 |  | 1232.285 | 1306.871 |  | 6.0913 | 5.9998 | 6.4927 | 6.3333 | 5.928 | 5.8984 | 5.9724 | 5.7427 | 48.4586 | 0.043613 |  | 62.069 | 100
19980520090000 | 1998-05-20 09:00 | 530.734 |  | 1.518 | 150.405 | 150.661 | 148.97 | 146.948 |  | 1227.369 | 1301.454 |  | 6.0693 | 5.9822 | 6.437 | 6.311 | 5.906 | 5.8801 | 5.9402 | 5.7183 | 48.2441 | 0.04342 |  | 62.069 | 100
19980520093000 | 1998-05-20 09:30 | 528.952 |  | 1.149 | 150.537 | 151.326 | 148.893 | 147.613 |  | 1233.369 | 1308.038 |  | 6.3477 | 6.26 | 5.7534 | 5.594 | 6.1768 | 6.1204 | 6.186 | 5.9602 | 48.3985 | 0.043559 |  | 62.069 | 100
19980520100000 | 1998-05-20 10:00 | 537.445 |  | 1.395 | 150.656 | 151.274 | 148.904 | 147.809 |  | 1230.785 | 1305.454 |  | 6.2371 | 6.1365 | 6.8086 | 5.4421 | 6.0784 | 6.0037 | 6.0837 | 5.8503 | 48.6404 | 0.043776 |  | 62.069 | 100
19980520103000 | 1998-05-20 10:30 | 571.157 |  | 1.887 | 150.934 | 153.048 | 149.347 | 149.087 |  | 1313.788 | 1400.874 |  | 6.7285 | 6.623 | 7.3953 | 7.0955 | 6.5461 | 6.4529 | 6.5415 | 4.2717 | 51.6545 | 0.046489 |  | 62.069 | 100
19980520110000 | 1998-05-20 11:00 | 581.249 |  | 2.622 | 150.984 | 150.743 | 150.173 | 148.267 |  | 1329.621 | 1416.874 |  | 6.5149 | 6.4194 | 7.1418 | 6.8696 | 6.334 | 6.2708 | 6.3325 | 6.1487 | 52.0317 | 0.046829 |  | 62.069 | 100
19980520113000 | 1998-05-20 11:30 | 634.281 |  | 3.847 | 151.143 | 152.723 | 150.878 | 151.238 |  | 1445.542 | 1543.961 |  | 7.1069 | 7.0313 | 7.875 | 7.6448 | 6.9246 | 6.8252 | 6.9138 | 6.707 | 57.0286 | 0.051326 |  | 62.069 | 100
19980520120000 | 1998-05-20 12:00 | 637.322 |  | 3.725 | 151.483 | 152.568 | 153.893 | 154.548 |  | 1451.875 | 1548.128 |  | 7.1152 | 7.0266 | 7.8728 | 7.6394 | 6.9199 | 6.8154 | 6.9031 | 6.7131 | 57.0055 | 0.051305 |  | 62.069 | 100
19980520123000 | 1998-05-20 12:30 | 634.884 |  | 2.618 | 151.856 | 154.888 | 156.4 | 157.116 |  | 1479.376 | 1581.129 |  | 7.1038 | 7.0427 | 7.8577 | 7.6362 | 6.9177 | 6.8169 | 6.9009 | 6.697 | 56.9729 | 0.051276 |  | 62.069 | 100
19980520130000 | 1998-05-20 13:00 | 637.217 |  | 3.605 | 153.342 | 154.785 | 158.295 | 157.013 |  | 1491.043 | 1588.462 |  | 7.1602 | 7.0718 | 7.9446 | 7.689 | 6.9534 | 6.8489 | 6.9282 | 6.7383 | 57.3344 | 0.051601 |  | 62.069 | 100
19980520133000 | 1998-05-20 13:30 | 638.973 |  | 3.48 | 153.541 | 155.476 | 158.642 | 157.209 |  | 1481.459 | 1582.712 |  | 7.1396 | 7.0703 | 7.9331 | 7.6836 | 6.9512 | 6.8384 | 6.9246 | 6.739 | 57.2798 | 0.051552 |  | 62.069 | 100
19980520140000 | 1998-05-20 14:00 | 633.835 |  | 3.477 | 153.709 | 155.476 | 158.868 | 157.704 |  | 1492.793 | 1590.879 |  | 7.1436 | 7.0779 | 7.9446 | 7.6958 | 6.9504 | 6.8459 | 6.9307 | 6.7444 | 57.3333 | 0.0516 |  | 62.069 | 100
19980520143000 | 1998-05-20 14:30 | 637.872 |  | 5.193 | 154.203 | 152.794 | 159.303 | 156.259 |  | 1479.459 | 1574.545 |  | 7.1436 | 7.0779 | 7.9163 | 7.689 | 6.9543 | 6.8445 | 6.9207 | 6.7468 | 57.2931 | 0.051564 |  | 62.069 | 100
19980520150000 | 1998-05-20 15:00 | 634.097 |  | 4.825 | 152.538 | 154.903 | 157.738 | 156.389 |  | 1485.709 | 1581.962 |  | 7.1511 | 7.0725 | 7.9277 | 7.7073 | 6.9587 | 6.8489 | 6.9275 | 6.7429 | 57.3366 | 0.051603 |  | 62.069 | 100
19980520153000 | 1998-05-20 15:30 | 636.116 |  | 4.335 | 152.9 | 154.357 | 158.148 | 156.584 |  | 1477.459 | 1572.629 |  | 7.1357 | 7.0388 | 7.9087 | 7.647 | 6.9397 | 6.8025 | 6.884 | 6.7056 | 57.062 | 0.051356 |  | 62.069 | 100
19980520160000 | 1998-05-20 16:00 | 638.029 |  | 5.436 | 153.088 | 154.785 | 158.206 | 157.013 |  | 1477.042 | 1570.878 |  | 7.1382 | 7.0503 | 7.9094 | 7.6729 | 6.9458 | 6.8108 | 6.907 | 6.7139 | 57.1483 | 0.051433 |  | 62.069 | 100
19980520163000 | 1998-05-20 16:30 | 603.767 |  | 3.48 | 153.041 | 153.521 | 158.254 | 156.492 |  | 1356.622 | 1442.875 |  | 6.6589 | 6.5437 | 7.2922 | 6.9971 | 6.4385 | 6.3013 | 6.3789 | 6.2295 | 52.8401 | 0.047556 |  | 62.069 | 100
19980520170000 | 1998-05-20 17:00 | 578.025 |  | 3.849 | 150.467 | 150.133 | 155.885 | 152.361 |  | 1344.539 | 1424.458 |  | 6.5728 | 6.4834 | 7.2266 | 6.9214 | 6.4072 | 6.2859 | 6.3652 | 6.1753 | 52.4378 | 0.047194 |  | 62.069 | 100
19980520173000 | 1998-05-20 17:30 | 540.643 |  | 1.761 | 149.954 | 149.391 | 153.49 | 150.381 |  | 1267.453 | 1349.455 |  | 6.2615 | 6.147 | 6.8428 | 6.4966 | 6.1265 | 6.0205 | 6.0952 | 5.8923 | 49.8824 | 0.044894 |  | 62.069 | 100
19980520180000 | 1998-05-20 18:00 | 542.347 |  | 2.01 | 149.33 | 150.484 | 151.034 | 148.752 |  | 1251.786 | 1329.788 |  | 6.2385 | 6.1157 | 6.8069 | 6.4575 | 6.083 | 5.9846 | 6.0701 | 5.8472 | 49.6035 | 0.044643 |  | 62.069 | 100
19980520183000 | 1998-05-20 18:30 | 542.374 |  | 2.005 | 150.208 | 150.51 | 149.872 | 147.54 |  | 1243.369 | 1325.871 |  | 6.2341 | 6.1189 | 6.7856 | 6.4622 | 6.0715 | 6.0005 | 6.073 | 5.8511 | 49.5969 | 0.044637 |  | 62.069 | 100
19980520190000 | 1998-05-20 19:00 | 541.456 |  | 21.929 | 150.032 | 152.867 | 148.723 | 148.164 |  | 1267.37 | 1348.789 |  | 6.218 | 6.1135 | 6.781 | 6.4783 | 6.0669 | 5.9944 | 6.0745 | 5.8418 | 49.5684 | 0.044612 |  | 62.069 | 100
19980520193000 | 1998-05-20 19:30 | 541.98 |  | 2.254 | 151.4 | 150.964 | 150.056 | 148.984 |  | 1272.536 | 1354.456 |  | 6.2539 | 6.1272 | 6.8191 | 6.4766 | 6.0981 | 6.0151 | 6.092 | 5.8601 | 49.7421 | 0.044768 |  | 62.069 | 100
19980520200000 | 1998-05-20 20:00 | 505.647 |  | 1.638 | 150.03 | 149.387 | 150.188 | 146.664 |  | 1176.95 | 1244.952 |  | 5.7825 | 5.6221 | 6.2302 | 5.8296 | 5.6267 | 5.5642 | 5.6411 | 5.394 | 45.6904 | 0.041121 |  | 62.069 | 100
19980520203000 | 1998-05-20 20:30 | 502.58 |  | 1.269 | 149.768 | 151.64 | 148.418 | 145.947 |  | 1181.701 | 1252.369 |  | 5.7664 | 5.6152 | 6.2036 | 5.874 | 5.6167 | 5.5811 | 5.6526 | 5.3962 | 45.7058 | 0.041135 |  | 62.069 | 100
19980520210000 | 1998-05-20 21:00 | 502.449 |  | 1.52 | 150.819 | 150.898 | 148.519 | 146.69 |  | 1180.534 | 1252.119 |  | 5.7825 | 5.6221 | 6.2043 | 5.8625 | 5.6299 | 5.5811 | 5.6489 | 5.3979 | 45.7292 | 0.041156 |  | 62.069 | 100
19980520213000 | 1998-05-20 21:30 | 564.97 |  | 3.356 | 149.856 | 153.569 | 147.864 | 148.618 |  | 1291.62 | 1377.706 |  | 6.3638 | 6.2524 | 6.9709 | 6.636 | 6.1943 | 6.1233 | 6.2026 | 5.9685 | 50.7118 | 0.045641 |  | 62.069 | 100
19980520220000 | 1998-05-20 22:00 | 592.286 |  | 3.971 | 152.014 | 152.202 | 150.748 | 151.459 |  | 1356.789 | 1447.708 |  | 6.6506 | 6.5598 | 7.3213 | 7.0359 | 6.4736 | 6.4019 | 6.4683 | 6.2646 | 53.176 | 0.047858 |  | 62.069 | 100
19980520223000 | 1998-05-20 22:30 | 581.459 |  | 20.848 | 151.387 | 151.175 | 153.039 | 152.66 |  | 1315.454 | 1408.457 |  | 6.5376 | 6.4155 | 7.1809 | 6.8374 | 6.353 | 6.2424 | 6.3279 | 6.1311 | 52.0258 | 0.046823 |  | 62.069 | 100
19980520230000 | 1998-05-20 23:00 | 566.543 |  | 3.112 | 149.438 | 150.499 | 152.42 | 148.272 |  | 1299.204 | 1383.706 |  | 6.3325 | 6.2515 | 6.9482 | 6.646 | 6.1943 | 6.1172 | 6.1929 | 5.9951 | 50.6777 | 0.04561 |  | 62.069 | 100
19980520233000 | 1998-05-20 23:30 | 562.296 |  | 2.618 | 149.959 | 150.592 | 150.599 | 148.612 |  | 1289.704 | 1374.039 |  | 6.3843 | 6.2852 | 6.9802 | 6.6948 | 6.231 | 6.144 | 6.2202 | 6.0159 | 50.9556 | 0.04586 |  | 62.069 | 100
19980521000000 | 1998-05-21 | 562.27 |  | 2.867 | 150.758 | 153.108 | 150.382 | 150.88 |  | 1322.371 | 1409.04 |  | 6.3936 | 6.3003 | 7.0107 | 6.6902 | 6.2295 | 6.1592 | 6.2241 | 6.0205 | 51.0281 | 0.045925 |  | 62.069 | 100
19980521003000 | 1998-05-21 00:30 | 504.677 |  | 1.028 | 150.61 | 148.327 | 151.078 | 146.842 |  | 1182.951 | 1250.203 |  | 5.8052 | 5.6794 | 6.26 | 5.9304 | 5.6824 | 5.6177 | 5.6755 | 5.459 | 46.1096 | 0.041499 |  | 62.069 | 100
19980521010000 | 1998-05-21 01:00 | 459.851 |  | 1.145 | 148.887 | 148.678 | 148.081 | 144.966 |  | 1062.114 | 1118.032 |  | 5.3025 | 5.1094 | 5.5886 | 5.2217 | 5.1721 | 5.1323 | 5.1941 | 4.9309 | 41.6516 | 0.037486 |  | 62.069 | 100
19980521013000 | 1998-05-21 01:30 | 431.749 |  | 0.289 | 149.594 | 150.514 | 147.303 | 147.049 |  | 1032.78 | 1090.031 |  | 5.2322 | 5.0684 | 4.0994 | 5.1614 | 5.1133 | 5.1025 | 5.1667 | 4.8721 | 39.816 | 0.035834 |  | 62.069 | 100
19980521020000 | 1998-05-21 02:00 | 433.112 |  | 1.767 | 150.189 | 149.653 | 148.296 | 147.178 |  | 1015.446 | 1064.614 |  | 5.1187 | 4.9385 | 5.1111 | 4.9941 | 5.0012 | 5.0264 | 5.0728 | 4.77 | 40.0328 | 0.03603 |  | 62.069 | 100
19980521023000 | 1998-05-21 02:30 | 432.011 |  | 0.66 | 149.209 | 149.602 | 147.589 | 146.384 |  | 1002.112 | 1050.697 |  | 5.0217 | 4.8379 | 5.1575 | 4.8882 | 4.8745 | 4.9377 | 4.9797 | 4.6882 | 39.3854 | 0.035447 |  | 62.069 | 100
19980521030000 | 1998-05-21 03:00 | 421.132 |  | 0.661 | 150.304 | 151.294 | 148.464 | 147.828 |  | 987.445 | 1031.113 |  | 4.969 | 4.7539 | 5.1011 | 4.7952 | 4.8218 | 4.886 | 4.9287 | 4.6074 | 38.8631 | 0.034977 |  | 62.069 | 100
19980521033000 | 1998-05-21 03:30 | 454.162 |  | 0.906 | 151.076 | 151.67 | 149.483 | 148.205 |  | 1061.781 | 1119.699 |  | 5.2925 | 5.1545 | 5.5176 | 5.2888 | 5.1675 | 5.1895 | 5.2498 | 4.9819 | 41.8421 | 0.037658 |  | 62.069 | 100
19980521040000 | 1998-05-21 04:00 | 456.076 |  | 1.153 | 151.534 | 151.304 | 149.826 | 147.592 |  | 1074.698 | 1133.032 |  | 5.2896 | 5.1262 | 5.5208 | 5.2429 | 5.1567 | 5.1772 | 5.2361 | 4.9568 | 41.7063 | 0.037536 |  | 62.069 | 100
19980521043000 | 1998-05-21 04:30 | 448.867 |  | 0.537 | 150.591 | 150.041 | 148.901 | 146.328 |  | 1076.698 | 1132.366 |  | 5.3284 | 5.1843 | 5.5581 | 5.3186 | 5.2026 | 5.2231 | 5.282 | 4.9934 | 42.0905 | 0.037881 |  | 62.069 | 100
19980521050000 | 1998-05-21 05:00 | 421.945 |  | 0.785 | 150.065 | 151.083 | 148.174 | 147.122 |  | 1006.779 | 1057.03 |  | 4.989 | 4.8096 | 5.1033 | 4.8447 | 4.8584 | 4.895 | 4.9575 | 4.6616 | 39.1191 | 0.035207 |  | 62.069 | 100
19980521053000 | 1998-05-21 05:30 | 414.317 |  | 0.293 | 150.081 | 149.35 | 148.164 | 146.132 |  | 1007.029 | 1051.697 |  | 4.9141 | 4.7134 | 5.0232 | 4.7158 | 4.77 | 4.8257 | 4.8684 | 4.5632 | 38.3938 | 0.034554 |  | 62.069 | 100
19980521060000 | 1998-05-21 06:00 | 417.856 |  | 0.784 | 149.26 | 149.18 | 147.593 | 145.22 |  | 966.361 | 1010.279 |  | 4.8623 | 4.657 | 4.9453 | 4.6523 | 4.7302 | 4.7905 | 4.8379 | 4.5129 | 37.9884 | 0.03419 |  | 62.069 | 100
19980521063000 | 1998-05-21 06:30 | 414.081 |  | 0.542 | 149.555 | 150.717 | 147.593 | 147.252 |  | 963.944 | 1005.029 |  | 4.8538 | 4.6594 | 4.9539 | 4.6899 | 4.7234 | 4.7952 | 4.8354 | 4.519 | 38.03 | 0.034227 |  | 62.069 | 100
19980521070000 | 1998-05-21 07:00 | 419.088 |  | 0.906 | 150.649 | 150.547 | 148.843 | 147.824 |  | 970.278 | 1014.696 |  | 4.8569 | 4.6487 | 4.9614 | 4.6548 | 4.7195 | 4.7822 | 4.834 | 4.5051 | 37.9626 | 0.034166 |  | 62.069 | 100
19980521073000 | 1998-05-21 07:30 | 413.163 |  | 0.206 | 150.692 | 150.573 | 148.985 | 146.86 |  | 965.194 | 1008.362 |  | 4.9104 | 4.7021 | 5.0095 | 4.7349 | 4.7798 | 4.8271 | 4.8782 | 4.5601 | 38.4021 | 0.034562 |  | 62.069 | 100
19980521080000 | 1998-05-21 08:00 | 415.863 |  | 1.03 | 150.205 | 150.872 | 148.428 | 147.159 |  | 966.861 | 1008.946 |  | 4.9104 | 4.6555 | 4.9973 | 4.6594 | 4.7769 | 4.7852 | 4.8486 | 4.5227 | 38.156 | 0.03434 |  | 62.069 | 100
19980521083000 | 1998-05-21 08:30 | 470.232 |  | 0.54 | 151.021 | 153.373 | 149.176 | 150.403 |  | 1101.865 | 1164.283 |  | 5.5039 | 5.3474 | 5.7778 | 5.5251 | 5.3521 | 5.3589 | 5.4199 | 5.1384 | 43.4235 | 0.039081 |  | 62.069 | 100
19980521090000 | 1998-05-21 09:00 | 470.651 |  | 1.032 | 151.672 | 150.521 | 150.067 | 147.303 |  | 1093.448 | 1155.95 |  | 5.4475 | 5.2957 | 5.7205 | 5.4353 | 5.2949 | 5.281 | 5.3452 | 5.0867 | 42.9068 | 0.038616 |  | 62.069 | 100
19980521093000 | 1998-05-21 09:30 | 512.699 |  | 0.573 | 150.72 | 151.434 | 148.997 | 147.968 |  | 1215.202 | 1298.204 |  | 6.0388 | 5.9412 | 6.4744 | 6.283 | 5.8884 | 5.8877 | 5.9509 | 5.6924 | 48.1568 | 0.043341 |  | 62.069 | 100
19980521100000 | 1998-05-21 10:00 | 568.037 |  | 3.237 | 151.879 | 152.79 | 150.121 | 148.829 |  | 1364.039 | 1459.625 |  | 6.585 | 6.5042 | 7.1221 | 6.9993 | 6.395 | 6.3857 | 6.4485 | 6.2158 | 52.6556 | 0.04739 |  | 62.069 | 100
19980521103000 | 1998-05-21 10:30 | 578.68 |  | 1.888 | 152.149 | 150.824 | 151.874 | 151.567 |  | 1337.872 | 1426.458 |  | 6.5498 | 6.4468 | 7.1052 | 6.894 | 6.3699 | 6.2905 | 6.3652 | 6.1477 | 52.1691 | 0.046952 |  | 62.069 | 100
19980521110000 | 1998-05-21 11:00 | 583.032 |  | 2.75 | 150.542 | 150.422 | 152.744 | 150.917 |  | 1339.955 | 1426.124 |  | 6.5239 | 6.4316 | 7.0764 | 6.8757 | 6.3569 | 6.2813 | 6.3523 | 6.1365 | 52.0346 | 0.046831 |  | 62.069 | 100
19980521113000 | 1998-05-21 11:30 | 578.418 |  | 2.256 | 150.428 | 150.839 | 153.004 | 151.087 |  | 1336.205 | 1426.958 |  | 6.5186 | 6.4546 | 7.0571 | 6.894 | 6.3523 | 6.3013 | 6.3623 | 6.1555 | 52.0957 | 0.046886 |  | 62.069 | 100
19980521120000 | 1998-05-21 12:00 | 578.471 |  | 2.747 | 150.628 | 150.463 | 153.095 | 151.7 |  | 1335.955 | 1419.874 |  | 6.5156 | 6.4255 | 7.0564 | 6.8628 | 6.3455 | 6.2737 | 6.3362 | 6.1189 | 51.9346 | 0.046741 |  | 62.069 | 100
19980521123000 | 1998-05-21 12:30 | 580.148 |  | 2.254 | 150.465 | 150.385 | 152.907 | 151.128 |  | 1339.372 | 1426.708 |  | 6.5498 | 6.4346 | 7.1106 | 6.875 | 6.3706 | 6.2776 | 6.3469 | 6.1401 | 52.1052 | 0.046895 |  | 62.069 | 100
19980521130000 | 1998-05-21 13:00 | 581.013 |  | 20.236 | 150.077 | 151.076 | 152.429 | 151.324 |  | 1344.122 | 1428.874 |  | 6.5354 | 6.4216 | 7.0764 | 6.8604 | 6.3638 | 6.2607 | 6.324 | 6.1218 | 51.9641 | 0.046768 |  | 62.069 | 100
19980521133000 | 1998-05-21 13:30 | 578.392 |  | 2.501 | 150.594 | 151.128 | 152.499 | 150.385 |  | 1338.372 | 1425.874 |  | 6.5437 | 6.4338 | 7.0862 | 6.8894 | 6.3735 | 6.2783 | 6.3362 | 6.1318 | 52.0729 | 0.046866 |  | 62.069 | 100
19980521140000 | 1998-05-21 14:00 | 578.654 |  | 2.625 | 150.748 | 151.401 | 152.397 | 151.401 |  | 1339.622 | 1424.791 |  | 6.5461 | 6.4277 | 7.071 | 6.8474 | 6.3767 | 6.2722 | 6.3401 | 6.1311 | 52.0123 | 0.046811 |  | 62.069 | 100
19980521143000 | 1998-05-21 14:30 | 581.931 |  | 2.621 | 150.509 | 151.05 | 152.643 | 152.04 |  | 1347.122 | 1431.791 |  | 6.5254 | 6.4126 | 7.0466 | 6.8452 | 6.3638 | 6.26 | 6.3301 | 6.1211 | 51.9048 | 0.046714 |  | 62.069 | 100
19980521150000 | 1998-05-21 15:00 | 575.299 |  | 3.114 | 150.497 | 150.674 | 152.994 | 151.416 |  | 1339.872 | 1426.708 |  | 6.5088 | 6.4133 | 7.0427 | 6.865 | 6.3638 | 6.2729 | 6.3333 | 6.1279 | 51.9277 | 0.046735 |  | 62.069 | 100
19980521153000 | 1998-05-21 15:30 | 578.471 |  | 2.377 | 150.832 | 150.034 | 153.313 | 152.262 |  | 1342.705 | 1429.874 |  | 6.5461 | 6.4438 | 7.0649 | 6.8894 | 6.3782 | 6.2959 | 6.3569 | 6.1433 | 52.1185 | 0.046907 |  | 62.069 | 100
19980521160000 | 1998-05-21 16:00 | 577.894 |  | 3.116 | 150.034 | 150.504 | 153.225 | 150.999 |  | 1331.872 | 1417.541 |  | 6.5469 | 6.446 | 7.0916 | 6.875 | 6.3911 | 6.2959 | 6.363 | 6.1509 | 52.1604 | 0.046944 |  | 62.069 | 100
19980521163000 | 1998-05-21 16:30 | 573.778 |  | 2.504 | 150.336 | 153.149 | 152.799 | 152.654 |  | 1358.956 | 1446.542 |  | 6.5354 | 6.4302 | 7.0793 | 6.875 | 6.3867 | 6.283 | 6.353 | 6.1455 | 52.0881 | 0.046879 |  | 62.069 | 100
19980521170000 | 1998-05-21 17:00 | 573.752 |  | 2.993 | 151.179 | 151.143 | 154.457 | 152.876 |  | 1346.455 | 1431.708 |  | 6.5491 | 6.4438 | 7.0938 | 6.8909 | 6.3943 | 6.2935 | 6.3674 | 6.1577 | 52.1905 | 0.046971 |  | 62.069 | 100
19980521173000 | 1998-05-21 17:30 | 576.19 |  | 2.254 | 150.551 | 150.895 | 154.496 | 152.876 |  | 1350.289 | 1440.458 |  | 6.5537 | 6.4478 | 7.0747 | 6.897 | 6.3918 | 6.2905 | 6.366 | 6.1555 | 52.177 | 0.046959 |  | 62.069 | 100
19980521180000 | 1998-05-21 18:00 | 613.939 |  | 4.099 | 151.018 | 154.402 | 154.856 | 156.629 |  | 1459.709 | 1557.628 |  | 7.0222 | 6.926 | 7.637 | 7.5386 | 6.8506 | 6.7383 | 6.8291 | 6.6003 | 56.1421 | 0.050528 |  | 62.069 | 100
19980521183000 | 1998-05-21 18:30 | 624.529 |  | 3.606 | 153.325 | 154.35 | 157.82 | 156.825 |  | 1462.875 | 1561.545 |  | 7.0442 | 6.9412 | 7.6516 | 7.5256 | 6.8665 | 6.7415 | 6.8237 | 6.623 | 56.2173 | 0.050596 |  | 62.069 | 100
19980521190000 | 1998-05-21 19:00 | 590.005 |  | 4.22 | 151.643 | 149.167 | 156.504 | 151.147 |  | 1367.373 | 1450.542 |  | 6.6848 | 6.5881 | 7.2319 | 7.1106 | 6.5271 | 6.4148 | 6.4895 | 6.2913 | 53.3381 | 0.048004 |  | 62.069 | 100
19980521193000 | 1998-05-21 19:30 | 558.128 |  | 3.237 | 149.252 | 148.594 | 152.492 | 146.614 |  | 1287.87 | 1368.039 |  | 6.3501 | 6.25 | 6.842 | 6.6345 | 6.2065 | 6.1021 | 6.1807 | 5.9724 | 50.5383 | 0.045484 |  | 62.069 | 100
19980521200000 | 1998-05-21 20:00 | 557.421 |  | 3.113 | 149.728 | 151.72 | 149.608 | 147.512 |  | 1287.87 | 1367.539 |  | 6.343 | 6.2219 | 6.8008 | 6.5803 | 6.1836 | 6.0999 | 6.1721 | 5.9524 | 50.354 | 0.045319 |  | 62.069 | 100
19980521203000 | 1998-05-21 20:30 | 560.933 |  | 2.747 | 150.859 | 150.925 | 149.47 | 147.955 |  | 1284.203 | 1368.206 |  | 6.3508 | 6.231 | 6.8467 | 6.5994 | 6.1951 | 6.0989 | 6.1692 | 5.9448 | 50.4359 | 0.045392 |  | 62.069 | 100
19980521210000 | 1998-05-21 21:00 | 557.578 |  | 3.235 | 150.444 | 150.678 | 149.772 | 147.955 |  | 1284.703 | 1366.873 |  | 6.321 | 6.2166 | 6.7917 | 6.5789 | 6.1677 | 6.083 | 6.1577 | 5.9297 | 50.2463 | 0.045222 |  | 62.069 | 100
19980521213000 | 1998-05-21 21:30 | 558.417 |  | 2.621 | 150.463 | 151.838 | 149.869 | 148.62 |  | 1284.037 | 1367.539 |  | 6.3423 | 6.2241 | 6.8284 | 6.6047 | 6.1814 | 6.1104 | 6.1692 | 5.9495 | 50.41 | 0.045369 |  | 62.069 | 100
19980521220000 | 1998-05-21 22:00 | 557.735 |  | 3.606 | 150.756 | 151.369 | 150.092 | 148.893 |  | 1285.537 | 1368.206 |  | 6.3477 | 6.2263 | 6.833 | 6.6147 | 6.1882 | 6.1021 | 6.1721 | 5.9473 | 50.4314 | 0.045388 |  | 62.069 | 100
19980521223000 | 1998-05-21 22:30 | 607.595 |  | 4.341 | 151.256 | 152.906 | 151.002 | 154.143 |  | 1398.207 | 1494.71 |  | 6.8489 | 6.7458 | 7.4348 | 7.2891 | 6.6765 | 6.5667 | 6.6475 | 6.4285 | 54.6378 | 0.049174 |  | 62.069 | 100
19980521230000 | 1998-05-21 23:00 | 609.141 |  | 4.708 | 151.631 | 152.255 | 154.516 | 153.741 |  | 1397.54 | 1485.376 |  | 6.8604 | 6.7734 | 7.4434 | 7.3318 | 6.6858 | 6.5972 | 6.6697 | 6.4575 | 54.8192 | 0.049337 |  | 62.069 | 100
19980521233000 | 1998-05-21 23:30 | 506.696 |  | 1.398 | 150.241 | 147.748 | 154.038 | 147.253 |  | 1162.033 | 1228.452 |  | 5.8296 | 5.6665 | 6.1692 | 5.8823 | 5.6702 | 5.5825 | 5.6543 | 5.4238 | 45.8784 | 0.041291 |  | 62.069 | 100
19980522000000 | 1998-05-22 | 504.861 |  | 1.274 | 148.811 | 151.513 | 149.234 | 146.315 |  | 1166.867 | 1234.785 |  | 5.7563 | 5.6321 | 6.0913 | 5.8472 | 5.6306 | 5.6062 | 5.6626 | 5.4048 | 45.6311 | 0.041068 |  | 62.069 | 100
19980522003000 | 1998-05-22 00:30 | 465.356 |  | 0.785 | 150.565 | 149.388 | 147.857 | 145.428 |  | 1065.947 | 1119.615 |  | 5.3804 | 5.1948 | 5.5894 | 5.3176 | 5.2522 | 5.2346 | 5.3003 | 4.9995 | 42.2688 | 0.038042 |  | 62.069 | 100
19980522010000 | 1998-05-22 01:00 | 461.45 |  | 1.398 | 149.484 | 150.689 | 147.336 | 146.481 |  | 1072.031 | 1126.616 |  | 5.3535 | 5.1675 | 5.5886 | 5.2551 | 5.2231 | 5.2354 | 5.2788 | 4.979 | 42.081 | 0.037873 |  | 62.069 | 100
19980522013000 | 1998-05-22 01:30 | 409.493 |  | 0.09 | 150.07 | 149.528 | 148.129 | 146.311 |  | 947.611 | 988.362 |  | 4.7944 | 4.5891 | 4.8669 | 3.1442 | 4.676 | 4.7661 | 4.8013 | 4.4763 | 36.1143 | 0.032503 |  | 62.069 | 100
19980522020000 | 1998-05-22 02:00 | 406.112 |  | 15.961 | 148.911 | 150.008 | 147.448 | 147.038 |  | 942.027 | 980.862 |  | 5.2163 | 5.0415 | 5.417 | 1.0423 | 5.0835 | 5.0552 | 5.1667 | 4.7905 | 36.813 | 0.033132 |  | 62.069 | 100
19980522023000 | 1998-05-22 02:30 | 347.444 |  | 0.172 | 149.534 | 148.091 | 147.625 | 144.378 |  | 825.857 | 843.358 |  | 2.1073 | 4.7639 | 5.0537 | 0.995 | 4.8257 | 4.8577 | 4.95 | 4.5449 | 32.0982 | 0.028888 |  | 62.069 | 100
19980522030000 | 1998-05-22 03:00 | 342.044 |  | 0.539 | 149.21 | 150.969 | 147.133 | 147.008 |  | 819.607 | 825.44 |  | 2.0723 | 4.6516 | 4.928 | 0.9637 | 4.7395 | 4.7356 | 4.8569 | 4.429 | 31.3766 | 0.028239 |  | 62.069 | 100
19980522033000 | 1998-05-22 03:30 | 344.036 |  | 0.297 | 150.391 | 150.34 | 148.172 | 147.37 |  | 820.357 | 823.357 |  | 0.004 | 5.0149 | 5.3765 | 1.037 | 5.0728 | 5.0591 | 5.1589 | 4.7661 | 31.4893 | 0.02834 |  | 62.069 | 100
19980522040000 | 1998-05-22 04:00 | 337.797 |  | 0.663 | 150.474 | 152.501 | 148.747 | 149.778 |  | 847.191 | 859.441 |  | 0.0032 | 5.0544 | 5.4368 | 1.0507 | 5.1248 | 5.1284 | 5.2278 | 4.8257 | 31.8518 | 0.028667 |  | 62.069 | 100
19980522043000 | 1998-05-22 04:30 | 334.337 |  | 0.173 | 151.181 | 150.532 | 149.567 | 147.314 |  | 841.441 | 849.858 |  | 0.0024 | 5.0789 | 5.4673 | 1.0621 | 5.1453 | 5.1567 | 5.2583 | 4.8433 | 32.0143 | 0.028813 |  | 62.069 | 100
19980522050000 | 1998-05-22 05:00 | 340.602 |  | 1.031 | 150.08 | 150.738 | 148.261 | 147.026 |  | 835.524 | 845.858 |  | 0.0024 | 5.0483 | 5.3696 | 1.0484 | 5.0728 | 5.0989 | 5.1948 | 4.7988 | 31.634 | 0.028471 |  | 62.069 | 100
19980522053000 | 1998-05-22 05:30 | 340.471 |  | 0.17 | 150.458 | 151.141 | 148.475 | 148.171 |  | 847.941 | 859.191 |  | 0.0047 | 5.0728 | 5.4116 | 1.0477 | 5.0911 | 5.1101 | 5.2078 | 4.825 | 31.7708 | 0.028594 |  | 62.069 | 100
19980522060000 | 1998-05-22 06:00 | 341.048 |  | 2.381 | 150.628 | 149.264 | 148.744 | 146.789 |  | 822.94 | 834.691 |  | 0.0032 | 5.072 | 5.426 | 1.0522 | 5.1262 | 5.1133 | 5.2178 | 4.8264 | 31.8371 | 0.028653 |  | 62.069 | 100
19980522063000 | 1998-05-22 06:30 | 417.882 |  | 0.785 | 149.577 | 152.91 | 147.876 | 149.445 |  | 1016.279 | 1067.197 |  | 0.0032 | 6.4492 | 7.0176 | 1.3239 | 6.3645 | 6.3333 | 6.408 | 6.1135 | 40.0132 | 0.036012 |  | 62.069 | 100
19980522070000 | 1998-05-22 07:00 | 438.591 |  | 1.523 | 151.999 | 151.909 | 150.31 | 148.197 |  | 1044.03 | 1103.615 |  | 0.0032 | 5.8289 | 6.3135 | 6.0723 | 5.7922 | 5.793 | 5.8608 | 5.574 | 41.2379 | 0.037114 |  | 62.069 | 100
19980522073000 | 1998-05-22 07:30 | 570.921 |  | 4.341 | 152.234 | 155.297 | 150.639 | 152.079 |  | 1329.205 | 1417.624 |  | 6.5576 | 6.4834 | 7.0793 | 6.8679 | 6.3782 | 6.3538 | 6.4338 | 6.167 | 52.321 | 0.047089 |  | 62.069 | 100
19980522080000 | 1998-05-22 08:00 | 637.191 |  | 5.2 | 153.702 | 152.579 | 153.599 | 154.064 |  | 1475.792 | 1579.962 |  | 7.1741 | 7.0894 | 7.801 | 7.6042 | 6.9778 | 6.8984 | 6.9832 | 6.7415 | 57.2696 | 0.051543 |  | 62.069 | 100
19980522083000 | 1998-05-22 08:30 | 636.116 |  | 4.099 | 152.01 | 153.599 | 155.997 | 155.827 |  | 1481.626 | 1583.629 |  | 7.1274 | 7.0488 | 7.7568 | 7.5593 | 6.9268 | 6.8445 | 6.9307 | 6.7009 | 56.8952 | 0.051206 |  | 62.069 | 100
19980522090000 | 1998-05-22 09:00 | 635.723 |  | 4.952 | 152.85 | 154.903 | 158.012 | 156.636 |  | 1488.293 | 1591.379 |  | 7.1914 | 7.1174 | 7.8071 | 7.6309 | 6.9849 | 6.9045 | 6.9924 | 6.7581 | 57.3867 | 0.051648 |  | 62.069 | 100
19980522093000 | 1998-05-22 09:30 | 636.64 |  | 4.341 | 153.132 | 153.603 | 158.566 | 155.583 |  | 1482.459 | 1579.462 |  | 7.2014 | 7.1289 | 7.8438 | 7.6409 | 6.9971 | 6.907 | 6.9924 | 6.7695 | 57.481 | 0.051733 |  | 62.069 | 100
19980522100000 | 1998-05-22 10:00 | 635.723 |  | 4.708 | 152.539 | 153.732 | 158.138 | 156.455 |  | 1471.209 | 1567.712 |  | 7.1748 | 7.0955 | 7.8064 | 7.6125 | 6.9656 | 6.8657 | 6.9526 | 6.7397 | 57.2128 | 0.051492 |  | 62.069 | 100
19980522103000 | 1998-05-22 10:30 | 633.18 |  | 4.461 | 152.807 | 154.124 | 158.247 | 155.857 |  | 1478.626 | 1575.212 |  | 7.1824 | 7.074 | 7.8096 | 7.5852 | 6.9741 | 6.8628 | 6.9519 | 6.73 | 57.17 | 0.051453 |  | 62.069 | 100
19980522110000 | 1998-05-22 11:00 | 632.446 |  | 4.83 | 152.648 | 153.551 | 158.069 | 156.274 |  | 1471.959 | 1569.128 |  | 7.1418 | 7.061 | 7.7554 | 7.5906 | 6.9565 | 6.8474 | 6.9412 | 6.7153 | 57.0092 | 0.051308 |  | 62.069 | 100
19980522113000 | 1998-05-22 11:30 | 629.51 |  | 4.587 | 152.461 | 153.474 | 157.748 | 156.444 |  | 1479.292 | 1573.379 |  | 7.1792 | 7.0908 | 7.8125 | 7.6294 | 6.9778 | 6.8589 | 6.9473 | 6.7468 | 57.2427 | 0.051518 |  | 62.069 | 100
19980522120000 | 1998-05-22 12:00 | 633.075 |  | 4.833 | 152.308 | 153.345 | 157.659 | 155.82 |  | 1472.876 | 1568.545 |  | 7.1709 | 7.0801 | 7.8018 | 7.5935 | 6.9702 | 6.8567 | 6.9482 | 6.7268 | 57.1482 | 0.051433 |  | 62.069 | 100
19980522123000 | 1998-05-22 12:30 | 578.549 |  | 3.482 | 150.875 | 149.137 | 156.158 | 150.869 |  | 1342.622 | 1424.958 |  | 6.6399 | 6.5149 | 7.168 | 6.874 | 6.4675 | 6.3318 | 6.3979 | 6.1982 | 52.5922 | 0.047333 |  | 62.069 | 100
19980522130000 | 1998-05-22 13:00 | 575.928 |  | 3.73 | 149.817 | 152.499 | 152.786 | 151.509 |  | 1354.789 | 1438.291 |  | 6.5239 | 6.4194 | 7.0291 | 6.7415 | 6.3752 | 6.2698 | 6.3301 | 6.1318 | 51.8208 | 0.046639 |  | 62.069 | 100
19980522133000 | 1998-05-22 13:30 | 549.582 |  | 2.379 | 150.988 | 148.915 | 153.295 | 150.4 |  | 1286.204 | 1368.206 |  | 6.2532 | 6.1379 | 6.6902 | 6.3821 | 6.1021 | 5.9998 | 6.0693 | 5.8601 | 49.4947 | 0.044545 |  | 62.069 | 100
19980522140000 | 1998-05-22 14:00 | 589.192 |  | 4.216 | 149.728 | 152.329 | 152.446 | 151.834 |  | 1393.457 | 1485.626 |  | 6.6848 | 6.595 | 7.2158 | 6.9993 | 6.5286 | 6.4492 | 6.511 | 6.2913 | 53.275 | 0.047948 |  | 62.069 | 100
19980522143000 | 1998-05-22 14:30 | 587.436 |  | 2.868 | 151.37 | 151.339 | 154.02 | 153.319 |  | 1383.206 | 1469.792 |  | 6.7207 | 6.5942 | 7.2441 | 6.9695 | 6.54 | 6.4277 | 6.5042 | 6.2729 | 53.2733 | 0.047946 |  | 62.069 | 100
19980522150000 | 1998-05-22 15:00 | 581.983 |  | 3.364 | 150.487 | 151.586 | 155.156 | 153.814 |  | 1381.54 | 1466.709 |  | 6.7041 | 6.572 | 7.2236 | 6.9612 | 6.5149 | 6.4094 | 6.488 | 6.2637 | 53.1369 | 0.047823 |  | 62.069 | 100
19980522153000 | 1998-05-22 15:30 | 592.181 |  | 3.728 | 149.965 | 150.818 | 154.228 | 150.57 |  | 1354.122 | 1443.458 |  | 6.6506 | 6.5286 | 7.187 | 6.8916 | 6.4729 | 6.366 | 6.4399 | 6.2227 | 52.7593 | 0.047483 |  | 62.069 | 100
19980522160000 | 1998-05-22 16:00 | 553.751 |  | 1.321 | 149.969 | 150.193 | 152.27 | 150.193 |  | 1216.952 | 1295.287 |  | 6.1326 | 6.0044 | 6.5742 | 6.2195 | 5.9829 | 5.8586 | 5.9434 | 5.7373 | 48.4529 | 0.043608 |  | 62.069 | 100
19980522163000 | 1998-05-22 16:30 | 550.054 |  | 17.062 | 149.312 | 150.637 | 149.935 | 146.182 |  | 1243.452 | 1320.788 |  | 6.1631 | 6.0317 | 6.6003 | 6.2698 | 6.0173 | 5.8967 | 5.9807 | 5.7549 | 48.7145 | 0.043843 |  | 62.069 | 100
19980522170000 | 1998-05-22 17:00 | 546.778 |  | 2.261 | 150.172 | 151.209 | 148.177 | 147.002 |  | 1233.952 | 1313.704 |  | 6.1426 | 5.9998 | 6.5688 | 6.2478 | 5.9846 | 5.9106 | 5.98 | 5.7449 | 48.5791 | 0.043721 |  | 62.069 | 100
19980522173000 | 1998-05-22 17:30 | 547.721 |  | 1.771 | 150.508 | 150.441 | 148.217 | 146.976 |  | 1230.202 | 1308.704 |  | 6.1372 | 5.9983 | 6.5552 | 6.2454 | 5.9778 | 5.887 | 5.9685 | 5.7297 | 48.4991 | 0.043649 |  | 62.069 | 100
19980522180000 | 1998-05-22 18:00 | 543.16 |  | 2.503 | 150.635 | 150.936 | 148.905 | 147.471 |  | 1239.952 | 1320.621 |  | 6.166 | 6.0349 | 6.5933 | 6.282 | 6.009 | 5.9473 | 6.012 | 5.7771 | 48.8216 | 0.043939 |  | 62.069 | 100
19980522183000 | 1998-05-22 18:30 | 545.493 |  | 1.891 | 150.833 | 151.679 | 149.105 | 145.986 |  | 1237.202 | 1316.204 |  | 6.1509 | 6.0295 | 6.572 | 6.2759 | 5.9998 | 5.9265 | 5.999 | 5.7625 | 48.7161 | 0.043844 |  | 62.069 | 100
19980522190000 | 1998-05-22 19:00 | 542.216 |  | 2.137 | 150.366 | 150.663 | 148.661 | 146.455 |  | 1236.869 | 1313.288 |  | 6.1555 | 6.012 | 6.5872 | 6.2524 | 6.0044 | 5.915 | 5.9814 | 5.7419 | 48.6498 | 0.043785 |  | 62.069 | 100
19980522193000 | 1998-05-22 19:30 | 545.205 |  | 2.013 | 150.292 | 150.441 | 148.384 | 146.481 |  | 1233.619 | 1312.788 |  | 6.1455 | 6.0166 | 6.575 | 6.2607 | 5.9868 | 5.9204 | 5.9915 | 5.751 | 48.6475 | 0.043783 |  | 62.069 | 100
19980522200000 | 1998-05-22 20:00 | 541.482 |  | 2.261 | 150.442 | 151.302 | 148.658 | 147.589 |  | 1240.036 | 1321.205 |  | 6.1799 | 6.0432 | 6.6299 | 6.3049 | 6.0249 | 5.957 | 6.0288 | 5.7815 | 48.9501 | 0.044055 |  | 62.069 | 100
19980522203000 | 1998-05-22 20:30 | 500.483 |  | 1.278 | 150.841 | 148.605 | 149.193 | 145.635 |  | 1146.866 | 1215.285 |  | 5.7617 | 5.5933 | 6.0859 | 5.7251 | 5.6077 | 5.5535 | 5.6199 | 5.3643 | 45.3114 | 0.04078 |  | 62.069 | 100
19980522210000 | 1998-05-22 21:00 | 497.94 |  | 1.521 | 149.377 | 150.219 | 147.468 | 146.754 |  | 1135.366 | 1206.701 |  | 5.7244 | 5.575 | 6.0571 | 5.7068 | 5.6008 | 5.5535 | 5.6199 | 5.3459 | 45.1834 | 0.040665 |  | 62.069 | 100
19980522213000 | 1998-05-22 21:30 | 503.498 |  | 1.154 | 150.293 | 150.962 | 148.383 | 147.744 |  | 1138.783 | 1204.785 |  | 5.7275 | 5.5933 | 6.0425 | 5.7197 | 5.5962 | 5.5496 | 5.6228 | 5.3513 | 45.2029 | 0.040683 |  | 62.069 | 100
19980522220000 | 1998-05-22 22:00 | 504.284 |  | 1.768 | 150.632 | 150.689 | 148.898 | 146.728 |  | 1145.033 | 1212.618 |  | 5.7305 | 5.5779 | 6.0547 | 5.7175 | 5.5984 | 5.5459 | 5.6084 | 5.3459 | 45.1792 | 0.040661 |  | 62.069 | 100
19980522223000 | 1998-05-22 22:30 | 536.973 |  | 1.645 | 151.491 | 152.107 | 149.878 | 148.394 |  | 1220.952 | 1304.037 |  | 6.0876 | 5.9707 | 6.4912 | 6.1897 | 5.9419 | 5.8792 | 5.9495 | 5.6992 | 48.209 | 0.043388 |  | 62.069 | 100
19980522230000 | 1998-05-22 23:00 | 535.846 |  | 2.015 | 150.876 | 151.039 | 149.966 | 148.812 |  | 1223.035 | 1302.037 |  | 6.1104 | 6.0012 | 6.5315 | 6.2393 | 5.9778 | 5.9067 | 5.9792 | 5.7344 | 48.4805 | 0.043632 |  | 62.069 | 100
19980522233000 | 1998-05-22 23:30 | 536.606 |  | 1.521 | 150.397 | 151.209 | 149.927 | 147.992 |  | 1222.702 | 1302.954 |  | 6.1121 | 5.9875 | 6.5376 | 6.2148 | 5.9609 | 5.8877 | 5.9578 | 5.7183 | 48.3767 | 0.043539 |  | 62.069 | 100
19980523000000 | 1998-05-23 | 535.925 |  | 1.89 | 150.65 | 151.9 | 150.194 | 148.187 |  | 1229.202 | 1305.037 |  | 6.0928 | 5.9922 | 6.5002 | 6.2166 | 5.9556 | 5.8992 | 5.9639 | 5.7297 | 48.3502 | 0.043515 |  | 62.069 | 100
19980523003000 | 1998-05-23 00:30 | 467.479 |  | 0.907 | 150.094 | 147.342 | 149.54 | 144.867 |  | 1086.948 | 1149.116 |  | 5.407 | 5.2583 | 5.6604 | 5.3079 | 5.3125 | 5.3186 | 5.3445 | 5.063 | 42.6722 | 0.038405 |  | 62.069 | 100
19980523010000 | 1998-05-23 01:00 | 417.567 |  | 0.66 | 148.699 | 148.93 | 146.929 | 145.712 |  | 964.444 | 1012.612 |  | 4.9697 | 4.7493 | 5.104 | 3.9888 | 4.8623 | 4.9294 | 4.9438 | 4.6128 | 38.1601 | 0.034344 |  | 62.069 | 100
19980523013000 | 1998-05-23 01:30 | 416.886 |  | 0.417 | 149.238 | 150.426 | 147.378 | 146.466 |  | 971.945 | 1015.029 |  | 5.0476 | 4.844 | 5.1995 | 4.01 | 4.9219 | 4.9302 | 4.9873 | 4.6584 | 38.5989 | 0.034739 |  | 62.069 | 100
19980523020000 | 1998-05-23 02:00 | 418.406 |  | 0.779 | 150.527 | 151.298 | 148.594 | 149.813 |  | 980.445 | 1031.446 |  | 5.384 | 5.2041 | 5.5994 | 4.3931 | 5.2261 | 5.2375 | 1.9388 | 4.9844 | 37.9674 | 0.034171 |  | 62.069 | 100
19980523023000 | 1998-05-23 02:30 | 384.275 |  | 0.538 | 150.968 | 149.277 | 149.439 | 146.802 |  | 893.026 | 934.944 |  | 4.918 | 1.8411 | 5.0264 | 3.9216 | 4.811 | 4.821 | 4.9531 | 4.5632 | 34.8554 | 0.03137 |  | 62.069 | 100
19980523030000 | 1998-05-23 03:00 | 394.394 |  | 0.661 | 148.969 | 150.499 | 147.453 | 146.787 |  | 910.693 | 951.111 |  | 5.0056 | 1.8182 | 5.124 | 3.9667 | 4.8745 | 4.886 | 5.0103 | 4.6541 | 35.3394 | 0.031805 |  | 62.069 | 100
19980523033000 | 1998-05-23 03:30 | 396.91 |  | 0.418 | 150.135 | 151.253 | 148.333 | 147.787 |  | 925.277 | 965.028 |  | 5.1392 | 1.8556 | 5.3125 | 4.145 | 4.9995 | 5.0225 | 5.1528 | 4.7815 | 36.4086 | 0.032768 |  | 62.069 | 100
19980523040000 | 1998-05-23 04:00 | 396.308 |  | 1.644 | 150.862 | 150.299 | 149.174 | 147.577 |  | 933.11 | 981.695 |  | 5.1912 | 1.8655 | 5.3657 | 4.1985 | 5.0562 | 5.0544 | 5.1941 | 4.8271 | 36.7527 | 0.033077 |  | 62.069 | 100
19980523043000 | 1998-05-23 04:30 | 354.207 |  | 0.082 | 150.093 | 151.171 | 148.494 | 147.211 |  | 847.108 | 890.859 |  | 4.6982 | 1.7411 | 4.76 | 3.6515 | 4.5945 | 4.6235 | 4.7668 | 4.3586 | 33.1942 | 0.029875 |  | 62.069 | 100
19980523050000 | 1998-05-23 05:00 | 356.278 |  | 0.662 | 149.74 | 150.558 | 147.848 | 146.845 |  | 837.191 | 875.525 |  | 4.5923 | 1.7167 | 4.6167 | 3.5669 | 4.4563 | 4.5349 | 4.6584 | 4.2671 | 32.4093 | 0.029168 |  | 62.069 | 100
19980523053000 | 1998-05-23 05:30 | 362.57 |  | 0.29 | 150.05 | 149.671 | 148.097 | 146.206 |  | 842.941 | 878.275 |  | 4.7012 | 1.7335 | 4.7485 | 3.6622 | 4.5632 | 4.606 | 4.7188 | 4.345 | 33.0784 | 0.029771 |  | 62.069 | 100
19980523060000 | 1998-05-23 06:00 | 356.855 |  | 2.258 | 150.044 | 152.25 | 148.381 | 149.774 |  | 879.859 | 920.36 |  | 4.7532 | 1.7557 | 4.8333 | 3.7362 | 4.6304 | 4.6655 | 4.7883 | 4.4031 | 33.5657 | 0.030209 |  | 62.069 | 100
19980523063000 | 1998-05-23 06:30 | 390.016 |  | 0.212 | 151.5 | 150.502 | 149.803 | 147.532 |  | 965.611 | 1020.779 |  | 5.2393 | 1.9014 | 5.4504 | 4.355 | 5.1392 | 5.1956 | 5.3093 | 4.9424 | 37.5326 | 0.033779 |  | 62.069 | 100
19980523070000 | 1998-05-23 07:00 | 407.92 |  | 15.719 | 151.126 | 151.518 | 149.268 | 148.052 |  | 964.611 | 1019.446 |  | 4.8157 | 3.251 | 4.8997 | 4.5884 | 4.6838 | 4.7119 | 4.7937 | 4.4563 | 36.2005 | 0.03258 |  | 62.069 | 100
19980523073000 | 1998-05-23 07:30 | 388.234 |  | 0.418 | 150.76 | 150.177 | 148.987 | 146.712 |  | 949.027 | 1000.112 |  | 4.6792 | 4.49 | 4.7546 | 4.3755 | 4.5701 | 4.6189 | 4.7295 | 4.3533 | 36.5711 | 0.032914 |  | 62.069 | 100
19980523080000 | 1998-05-23 08:00 | 487.009 |  | 2.258 | 150.526 | 153.694 | 148.673 | 149.733 |  | 1179.951 | 1250.203 |  | 5.854 | 5.7405 | 6.2227 | 5.9167 | 5.7046 | 5.7075 | 5.8374 | 5.4795 | 46.4629 | 0.041817 |  | 62.069 | 100
19980523083000 | 1998-05-23 08:30 | 523.84 |  | 1.767 | 152.105 | 150.857 | 150.377 | 147.639 |  | 1211.118 | 1287.87 |  | 6.012 | 5.9021 | 6.4065 | 6.1243 | 5.8472 | 5.8145 | 5.9609 | 5.6497 | 47.7172 | 0.042945 |  | 62.069 | 100
19980523090000 | 1998-05-23 09:00 | 569.61 |  | 4.587 | 150.856 | 151.042 | 149.069 | 147.824 |  | 1355.372 | 1451.208 |  | 6.6101 | 6.54 | 7.1357 | 6.9282 | 6.4407 | 6.4065 | 6.5376 | 6.2393 | 52.8381 | 0.047554 |  | 62.069 | 100
19980523093000 | 1998-05-23 09:30 | 587.986 |  | 3.237 | 151.855 | 151.474 | 150.556 | 148.999 |  | 1391.29 | 1487.459 |  | 6.7666 | 6.6841 | 7.3152 | 7.1213 | 6.5994 | 6.5393 | 6.6804 | 6.3774 | 54.0837 | 0.048675 |  | 62.069 | 100
19980523100000 | 1998-05-23 10:00 | 626.469 |  | 5.568 | 151.594 | 151.634 | 152.362 | 153.366 |  | 1460.459 | 1566.378 |  | 7.0747 | 6.9688 | 7.6729 | 7.4517 | 6.8801 | 6.7856 | 6.9321 | 6.6392 | 56.4051 | 0.050765 |  | 62.069 | 100
19980523103000 | 1998-05-23 10:30 | 628.723 |  | 3.974 | 151.54 | 152.51 | 155.295 | 154.985 |  | 1458.958 | 1558.878 |  | 7.0779 | 6.9727 | 7.6875 | 7.4585 | 6.8818 | 6.7581 | 6.9229 | 6.627 | 56.3864 | 0.050748 |  | 62.069 | 100
19980523110000 | 1998-05-23 11:00 | 631.292 |  | 4.708 | 151.93 | 153.02 | 156.705 | 155 |  | 1456.708 | 1553.295 |  | 7.0725 | 6.9839 | 7.6768 | 7.4585 | 6.8811 | 6.7781 | 6.9282 | 6.6475 | 56.4266 | 0.050784 |  | 62.069 | 100
19980523113000 | 1998-05-23 11:30 | 628.697 |  | 3.724 | 151.893 | 153.334 | 156.929 | 155.809 |  | 1463.792 | 1560.295 |  | 7.0725 | 6.9839 | 7.6851 | 7.4646 | 6.8811 | 6.7764 | 6.9329 | 6.6475 | 56.444 | 0.0508 |  | 62.069 | 100
19980523120000 | 1998-05-23 12:00 | 578.707 |  | 3.85 | 152.25 | 151.25 | 157.372 | 153.973 |  | 1312.204 | 1391.29 |  | 6.4851 | 6.3638 | 6.9702 | 6.6597 | 6.3149 | 6.176 | 6.3354 | 6.0737 | 51.3788 | 0.046241 |  | 62.069 | 100
19980523123000 | 1998-05-23 12:30 | 574.591 |  | 2.008 | 150.154 | 152.488 | 155.4 | 153.478 |  | 1353.706 | 1440.875 |  | 6.5667 | 6.4607 | 7.0815 | 6.7971 | 6.4019 | 6.2844 | 6.4338 | 6.1548 | 52.1809 | 0.046963 |  | 62.069 | 100
19980523130000 | 1998-05-23 13:00 | 574.722 |  | 3.113 | 150.817 | 151.42 | 155.231 | 153.401 |  | 1354.872 | 1439.625 |  | 6.5728 | 6.4668 | 7.0854 | 6.7993 | 6.405 | 6.3035 | 6.4485 | 6.1624 | 52.2437 | 0.047019 |  | 62.069 | 100
19980523133000 | 1998-05-23 13:30 | 576.426 |  | 3.111 | 150.237 | 150.208 | 155.232 | 153.179 |  | 1356.206 | 1440.791 |  | 6.5796 | 6.4705 | 7.0977 | 6.8154 | 6.4172 | 6.3142 | 6.4622 | 6.1699 | 52.3267 | 0.047094 |  | 62.069 | 100
19980523140000 | 1998-05-23 14:00 | 575.771 |  | 2.991 | 150.231 | 151.472 | 155.422 | 154.442 |  | 1364.873 | 1451.208 |  | 6.5964 | 6.4766 | 7.1335 | 6.8542 | 6.4263 | 6.3279 | 6.4797 | 6.1753 | 52.4699 | 0.047223 |  | 62.069 | 100
19980523143000 | 1998-05-23 14:30 | 547.145 |  | 2.988 | 150.416 | 148.93 | 155.532 | 151.158 |  | 1220.868 | 1300.204 |  | 6.1372 | 5.9929 | 6.5232 | 6.186 | 5.9556 | 5.8289 | 5.98 | 5.7222 | 48.326 | 0.043493 |  | 62.069 | 100
19980523150000 | 1998-05-23 15:00 | 544.077 |  | 2.498 | 148.939 | 150.714 | 151.867 | 147.497 |  | 1243.286 | 1318.371 |  | 6.1538 | 6.0349 | 6.5728 | 6.2568 | 6.0105 | 5.9395 | 6.0693 | 5.7717 | 48.8093 | 0.043928 |  | 62.069 | 100
19980523153000 | 1998-05-23 15:30 | 547.459 |  | 1.762 | 150.224 | 151.364 | 149.962 | 148.147 |  | 1244.702 | 1322.955 |  | 6.2004 | 6.064 | 6.6392 | 6.2996 | 6.0334 | 5.9639 | 6.1013 | 5.7961 | 49.0979 | 0.044188 |  | 62.069 | 100
19980523160000 | 1998-05-23 16:00 | 548.298 |  | 2.621 | 150.814 | 150.4 | 149.867 | 148.172 |  | 1243.119 | 1321.955 |  | 6.144 | 6.0188 | 6.5515 | 6.2371 | 5.9829 | 5.9272 | 6.0518 | 5.7458 | 48.6591 | 0.043793 |  | 62.069 | 100
19980523163000 | 1998-05-23 16:30 | 545.729 |  | 2.009 | 150.439 | 150.529 | 150.236 | 149.292 |  | 1248.786 | 1329.121 |  | 6.1731 | 6.0295 | 6.6116 | 6.2676 | 6.0144 | 5.9541 | 6.0845 | 5.7625 | 48.8973 | 0.044008 |  | 62.069 | 100
19980523170000 | 1998-05-23 17:00 | 544.209 |  | 3.114 | 150.554 | 151.05 | 150.754 | 149.318 |  | 1243.619 | 1324.705 |  | 6.147 | 6.0098 | 6.5774 | 6.2515 | 5.9861 | 5.9236 | 6.0601 | 5.752 | 48.7075 | 0.043837 |  | 62.069 | 100
19980523173000 | 1998-05-23 17:30 | 583.242 |  | 3.971 | 150.995 | 153.16 | 151.131 | 151.674 |  | 1354.289 | 1449.875 |  | 6.604 | 6.4956 | 7.1152 | 6.8237 | 6.4294 | 6.3667 | 6.4888 | 6.1868 | 52.5102 | 0.047259 |  | 62.069 | 100
19980523180000 | 1998-05-23 18:00 | 631.738 |  | 5.193 | 152.25 | 154.815 | 154.525 | 156.795 |  | 1457.542 | 1556.128 |  | 7.1152 | 6.981 | 7.7234 | 7.4585 | 6.9063 | 6.7964 | 6.9534 | 6.6475 | 56.5817 | 0.050924 |  | 62.069 | 100
19980523183000 | 1998-05-23 18:30 | 629.379 |  | 4.582 | 153.905 | 155.923 | 158.545 | 158.646 |  | 1466.959 | 1567.795 |  | 7.0977 | 6.9961 | 7.7034 | 7.4783 | 6.8962 | 6.8025 | 6.9526 | 6.6528 | 56.5796 | 0.050922 |  | 62.069 | 100
19980523190000 | 1998-05-23 19:00 | 587.41 |  | 3.85 | 154.54 | 154.283 | 159.625 | 156.511 |  | 1345.455 | 1426.541 |  | 6.6377 | 6.4851 | 7.1548 | 6.8306 | 6.4607 | 6.3318 | 6.4668 | 6.199 | 52.5665 | 0.04731 |  | 62.069 | 100
19980523193000 | 1998-05-23 19:30 | 558.784 |  | 2.864 | 151.904 | 149.58 | 157.288 | 152.798 |  | 1294.37 | 1377.623 |  | 6.3569 | 6.2126 | 6.8481 | 6.4995 | 6.2195 | 6.083 | 6.2166 | 5.929 | 50.3652 | 0.045329 |  | 62.069 | 100
19980523200000 | 1998-05-23 20:00 | 555.35 |  | 3.481 | 150.007 | 151.065 | 154.925 | 152.798 |  | 1297.121 | 1381.623 |  | 6.343 | 6.1868 | 6.8269 | 6.4553 | 6.1904 | 6.051 | 6.1897 | 5.9021 | 50.1452 | 0.045131 |  | 62.069 | 100
19980523203000 | 1998-05-23 20:30 | 533.801 |  | 2.373 | 150.527 | 149.606 | 154.514 | 152.081 |  | 1201.618 | 1279.62 |  | 5.9875 | 5.8022 | 6.3591 | 5.9692 | 5.8198 | 5.6787 | 5.8159 | 5.5337 | 46.9661 | 0.042269 |  | 62.069 | 100
19980523210000 | 1998-05-23 21:00 | 527.903 |  | 21.692 | 149.519 | 150.803 | 152.933 | 150.308 |  | 1221.618 | 1297.037 |  | 6.0281 | 5.8411 | 6.4255 | 6.0083 | 5.887 | 5.7793 | 5.915 | 5.5771 | 47.4614 | 0.042715 |  | 62.069 | 100
19980523213000 | 1998-05-23 21:30 | 522.451 |  | 21.938 | 150.068 | 150.829 | 151.487 | 149.343 |  | 1221.868 | 1299.121 |  | 6.0303 | 5.8235 | 6.4216 | 6.012 | 5.8884 | 5.7832 | 5.9114 | 5.5732 | 47.4436 | 0.042699 |  | 62.069 | 100
19980523220000 | 1998-05-23 22:00 | 572.205 |  | 3.728 | 150.719 | 154.124 | 151.503 | 152.391 |  | 1333.122 | 1423.958 |  | 6.5178 | 6.4172 | 7.0129 | 6.7429 | 6.3577 | 6.2776 | 6.4133 | 6.1196 | 51.859 | 0.046673 |  | 62.069 | 100
19980523223000 | 1998-05-23 22:30 | 574.04 |  | 3.115 | 151.453 | 150.932 | 154.092 | 153.655 |  | 1351.539 | 1437.875 |  | 6.5613 | 6.4529 | 7.0747 | 6.8306 | 6.3928 | 6.3271 | 6.459 | 6.1653 | 52.2637 | 0.047037 |  | 62.069 | 100
19980523230000 | 1998-05-23 23:00 | 576.793 |  | 3.849 | 150.461 | 151.102 | 154.427 | 151.845 |  | 1349.955 | 1440.208 |  | 6.5652 | 6.4683 | 7.0703 | 6.8276 | 6.3943 | 6.3301 | 6.4683 | 6.1707 | 52.2948 | 0.047065 |  | 62.069 | 100
19980523233000 | 1998-05-23 23:30 | 504.73 |  | 1.644 | 149.612 | 147.585 | 153.201 | 146.842 |  | 1183.451 | 1258.62 |  | 5.8618 | 5.7244 | 6.1975 | 5.9021 | 5.7275 | 5.6558 | 5.7961 | 5.491 | 46.3562 | 0.041721 |  | 62.069 | 100
19980524000000 | 1998-05-24 | 505.857 |  | 2.018 | 149.03 | 150.88 | 148.858 | 145.435 |  | 1168.534 | 1239.119 |  | 5.7732 | 5.6411 | 6.1042 | 5.7893 | 5.6282 | 5.6091 | 5.7327 | 5.4124 | 45.6902 | 0.041121 |  | 62.069 | 100
19980524003000 | 1998-05-24 00:30 | 504.861 |  | 1.401 | 150.306 | 151.179 | 147.342 | 145.982 |  | 1163.367 | 1234.035 |  | 5.7922 | 5.6458 | 6.1523 | 5.7754 | 5.6665 | 5.6145 | 5.7502 | 5.4077 | 45.8046 | 0.041224 |  | 62.069 | 100
19980524010000 | 1998-05-24 01:00 | 504.625 |  | 1.646 | 150.968 | 151.179 | 148.91 | 147.962 |  | 1184.034 | 1258.119 |  | 5.7947 | 5.6519 | 6.1257 | 5.7954 | 5.6558 | 5.6184 | 5.7502 | 5.4231 | 45.8152 | 0.041234 |  | 62.069 | 100
19980524013000 | 1998-05-24 01:30 | 502.764 |  | 1.032 | 150.78 | 151.205 | 149.233 | 146.997 |  | 1182.534 | 1255.369 |  | 5.813 | 5.6885 | 6.1584 | 5.8442 | 5.6748 | 5.6526 | 5.7961 | 5.4519 | 46.0795 | 0.041472 |  | 62.069 | 100
19980524020000 | 1998-05-24 02:00 | 504.337 |  | 2.142 | 150.374 | 150.189 | 148.872 | 146.724 |  | 1186.701 | 1259.703 |  | 5.8022 | 5.6482 | 6.1462 | 5.7832 | 5.668 | 5.6299 | 5.7625 | 5.4224 | 45.8626 | 0.041276 |  | 62.069 | 100
19980524023000 | 1998-05-24 02:30 | 464.098 |  | 0.906 | 150.103 | 149.643 | 148.64 | 146.672 |  | 1076.531 | 1138.199 |  | 5.259 | 5.0264 | 5.436 | 5.0142 | 5.1155 | 5.0774 | 5.2163 | 4.8562 | 41.001 | 0.036901 |  | 62.069 | 100
19980524030000 | 1998-05-24 03:00 | 427.398 |  | 1.157 | 148.925 | 148.287 | 147.019 | 143.337 |  | 987.278 | 1035.696 |  | 4.9553 | 4.7646 | 5.0789 | 4.6943 | 4.8447 | 4.9097 | 5.0125 | 4.6189 | 38.8789 | 0.034991 |  | 62.069 | 100
19980524033000 | 1998-05-24 03:30 | 427.188 |  | 0.786 | 148.812 | 150.499 | 146.538 | 147.529 |  | 987.695 | 1037.363 |  | 4.9758 | 4.7822 | 5.0874 | 4.7378 | 4.8386 | 4.8982 | 5.0171 | 4.6304 | 38.9675 | 0.035071 |  | 62.069 | 100
19980524040000 | 1998-05-24 04:00 | 427.188 |  | 1.035 | 150.421 | 150.979 | 148.494 | 148.009 |  | 1013.279 | 1067.697 |  | 5.114 | 4.9463 | 5.2673 | 4.9065 | 4.9697 | 5.0117 | 5.1477 | 4.7363 | 40.0995 | 0.03609 |  | 62.069 | 100
19980524043000 | 1998-05-24 04:30 | 479.014 |  | 1.278 | 151.59 | 151.903 | 149.974 | 147.942 |  | 1106.948 | 1169.95 |  | 5.491 | 5.3352 | 5.7686 | 5.4084 | 5.343 | 5.333 | 5.4673 | 5.127 | 43.2735 | 0.038946 |  | 62.069 | 100
19980524050000 | 1998-05-24 05:00 | 475.475 |  | 1.646 | 151.047 | 151.733 | 149.362 | 147.772 |  | 1090.781 | 1157.617 |  | 5.4763 | 5.3108 | 5.7373 | 5.3596 | 5.3262 | 5.291 | 5.4382 | 5.0979 | 43.0373 | 0.038734 |  | 62.069 | 100
19980524053000 | 1998-05-24 05:30 | 465.041 |  | 1.031 | 150.719 | 150.743 | 148.665 | 146.535 |  | 1040.447 | 1103.365 |  | 5.2009 | 4.9758 | 5.3574 | 4.9431 | 5.0461 | 4.9805 | 5.1111 | 4.8135 | 40.4284 | 0.036386 |  | 62.069 | 100
19980524060000 | 1998-05-24 06:00 | 440.007 |  | 0.908 | 149.744 | 149.856 | 147.945 | 145.896 |  | 1008.779 | 1061.28 |  | 5.1079 | 4.9097 | 5.2505 | 4.873 | 4.9622 | 4.9592 | 5.0806 | 4.7349 | 39.878 | 0.03589 |  | 62.069 | 100
19980524063000 | 1998-05-24 06:30 | 492.33 |  | 0.785 | 150.491 | 153.125 | 148.689 | 150.155 |  | 1124.116 | 1188.367 |  | 5.6809 | 5.5481 | 5.9983 | 5.7083 | 5.5283 | 5.4902 | 5.6328 | 5.3269 | 44.9138 | 0.040422 |  | 62.069 | 100
19980524070000 | 1998-05-24 07:00 | 495.922 |  | 1.767 | 151.623 | 150.65 | 149.858 | 146.937 |  | 1140.116 | 1206.451 |  | 5.6313 | 5.4719 | 5.9448 | 5.5757 | 5.478 | 5.4346 | 5.5671 | 5.2627 | 44.3661 | 0.039929 |  | 62.069 | 100
19980524073000 | 1998-05-24 07:30 | 587.698 |  | 3.365 | 151.682 | 154.43 | 150.191 | 151.954 |  | 1344.622 | 1437.875 |  | 6.6116 | 6.4797 | 7.1243 | 6.8596 | 6.4302 | 6.3293 | 6.4751 | 6.1882 | 52.498 | 0.047248 |  | 62.069 | 100
19980524080000 | 1998-05-24 08:00 | 576.426 |  | 3.849 | 151.821 | 150.629 | 153.027 | 151.371 |  | 1337.955 | 1425.124 |  | 6.498 | 6.3843 | 7.01 | 6.7153 | 6.3369 | 6.241 | 6.3843 | 6.1082 | 51.678 | 0.04651 |  | 62.069 | 100
19980524083000 | 1998-05-24 08:30 | 570.266 |  | 2.378 | 150.312 | 152.598 | 153.315 | 153.341 |  | 1347.789 | 1434.791 |  | 6.4934 | 6.4011 | 6.9871 | 6.7153 | 6.334 | 6.2561 | 6.3904 | 6.1135 | 51.6909 | 0.046522 |  | 62.069 | 100
19980524090000 | 1998-05-24 09:00 | 573.385 |  | 2.745 | 150.989 | 151.024 | 155.021 | 153.5 |  | 1349.539 | 1439.291 |  | 6.4819 | 6.3721 | 6.981 | 6.7048 | 6.3179 | 6.2302 | 6.376 | 6.092 | 51.5559 | 0.0464 |  | 62.069 | 100
19980524093000 | 1998-05-24 09:30 | 608.669 |  | 3.728 | 151.285 | 154.608 | 155.781 | 156.341 |  | 1475.626 | 1577.379 |  | 6.929 | 6.7957 | 7.499 | 7.2725 | 6.7314 | 6.6323 | 6.7688 | 6.479 | 55.1077 | 0.049597 |  | 62.069 | 100
19980524100000 | 1998-05-24 10:00 | 608.669 |  | 4.093 | 154.187 | 156.238 | 159.178 | 158.713 |  | 1445.292 | 1539.044 |  | 6.8901 | 6.7383 | 7.447 | 7.1702 | 6.6956 | 6.54 | 6.698 | 6.4187 | 54.5979 | 0.049138 |  | 62.069 | 100
19980524103000 | 1998-05-24 10:30 | 617.74 |  | 4.95 | 155.47 | 154.845 | 160.604 | 157.32 |  | 1445.042 | 1542.128 |  | 6.9146 | 6.7781 | 7.4897 | 7.2258 | 6.7346 | 6.5864 | 6.7354 | 6.4553 | 54.9199 | 0.049428 |  | 62.069 | 100
19980524110000 | 1998-05-24 11:00 | 621.96 |  | 5.199 | 153.309 | 153.633 | 158.551 | 155.613 |  | 1446.292 | 1541.044 |  | 6.9465 | 6.813 | 7.5393 | 7.261 | 6.7642 | 6.6223 | 6.7681 | 6.4941 | 55.2085 | 0.049688 |  | 62.069 | 100
19980524113000 | 1998-05-24 11:30 | 624.398 |  | 20.597 | 152.764 | 153.855 | 158.044 | 156.578 |  | 1453.458 | 1551.378 |  | 6.9727 | 6.833 | 7.554 | 7.29 | 6.7803 | 6.6345 | 6.7842 | 6.5078 | 55.3565 | 0.049821 |  | 62.069 | 100
19980524120000 | 1998-05-24 12:00 | 624.031 |  | 3.142 | 153.094 | 154.077 | 158.33 | 156.799 |  | 1451.708 | 1547.044 |  | 6.9771 | 6.8352 | 7.554 | 7.2632 | 6.7825 | 6.6255 | 6.7903 | 6.5125 | 55.3403 | 0.049806 |  | 62.069 | 100
19980524123000 | 1998-05-24 12:30 | 625.473 |  | 4.216 | 153.09 | 153.855 | 158.316 | 156.825 |  | 1453.292 | 1547.378 |  | 6.9871 | 6.8452 | 7.5798 | 7.2891 | 6.7993 | 6.6431 | 6.7947 | 6.5149 | 55.4532 | 0.049908 |  | 62.069 | 100
19980524130000 | 1998-05-24 13:00 | 624.11 |  | 4.83 | 152.695 | 153.086 | 158.02 | 155.809 |  | 1458.708 | 1553.795 |  | 6.958 | 6.8528 | 7.5554 | 7.3196 | 6.7825 | 6.646 | 6.8025 | 6.5125 | 55.4293 | 0.049886 |  | 62.069 | 100
19980524133000 | 1998-05-24 13:30 | 627.046 |  | 4.83 | 152.107 | 152.695 | 157.306 | 155.17 |  | 1452.958 | 1549.378 |  | 6.9587 | 6.8323 | 7.5479 | 7.2969 | 6.7651 | 6.627 | 6.7795 | 6.5042 | 55.3116 | 0.04978 |  | 62.069 | 100
19980524140000 | 1998-05-24 14:00 | 577.055 |  | 2.871 | 151.5 | 149.92 | 156.786 | 152.643 |  | 1343.539 | 1426.791 |  | 6.5994 | 6.4895 | 7.1243 | 6.813 | 6.4468 | 6.3186 | 6.4521 | 6.1897 | 52.4334 | 0.04719 |  | 62.069 | 100
19980524143000 | 1998-05-24 14:30 | 576.74 |  | 3.114 | 149.658 | 150.714 | 154.042 | 150.962 |  | 1318.038 | 1404.54 |  | 6.4644 | 6.3562 | 6.9504 | 6.6482 | 6.2959 | 6.1807 | 6.324 | 6.0571 | 51.2769 | 0.046149 |  | 62.069 | 100
19980524150000 | 1998-05-24 15:00 | 574.748 |  | 3.855 | 150.761 | 152.38 | 153.136 | 152.876 |  | 1344.955 | 1433.708 |  | 6.5095 | 6.395 | 7.0093 | 6.717 | 6.3462 | 6.2417 | 6.3904 | 6.0981 | 51.7072 | 0.046536 |  | 62.069 | 100
19980524153000 | 1998-05-24 15:30 | 577.501 |  | 2.866 | 150.752 | 152.499 | 154.655 | 154.232 |  | 1385.29 | 1474.209 |  | 6.6018 | 6.4675 | 7.1191 | 6.7964 | 6.4202 | 6.3064 | 6.4561 | 6.1653 | 52.3328 | 0.0471 |  | 62.069 | 100
19980524160000 | 1998-05-24 16:00 | 577.317 |  | 3.728 | 150.87 | 149.931 | 155.594 | 152.406 |  | 1351.622 | 1437.541 |  | 6.511 | 6.3882 | 7.0083 | 6.7407 | 6.3462 | 6.2471 | 6.3867 | 6.0974 | 51.7256 | 0.046553 |  | 62.069 | 100
19980524163000 | 1998-05-24 16:30 | 602.614 |  | 3.85 | 150.332 | 154.113 | 154.463 | 155.846 |  | 1432.708 | 1529.627 |  | 6.7856 | 6.6895 | 7.3296 | 7.0642 | 6.6047 | 6.5056 | 6.6499 | 6.3523 | 53.9814 | 0.048583 |  | 62.069 | 100
19980524170000 | 1998-05-24 17:00 | 622.432 |  | 5.935 | 152.623 | 153.762 | 157.025 | 156.733 |  | 1459.459 | 1556.711 |  | 7 | 6.8833 | 7.6064 | 7.3425 | 6.8093 | 6.6934 | 6.8374 | 6.5476 | 55.7199 | 0.050148 |  | 62.069 | 100
19980524173000 | 1998-05-24 17:30 | 634.989 |  | 5.322 | 152.005 | 152.942 | 156.999 | 155.17 |  | 1484.793 | 1584.046 |  | 7.1313 | 7.0198 | 7.7668 | 7.5281 | 6.9443 | 6.8201 | 6.9778 | 6.6758 | 56.864 | 0.051178 |  | 62.069 | 100
19980524180000 | 1998-05-24 18:00 | 635.723 |  | 6.303 | 151.71 | 152.957 | 156.887 | 155.433 |  | 1480.959 | 1582.045 |  | 7.1138 | 6.9971 | 7.7234 | 7.4722 | 6.9116 | 6.7896 | 6.9451 | 6.6528 | 56.6056 | 0.050945 |  | 62.069 | 100
19980524183000 | 1998-05-24 18:30 | 633.337 |  | 4.704 | 152.045 | 153.674 | 157.269 | 156.149 |  | 1477.626 | 1577.879 |  | 7.1106 | 7 | 7.7241 | 7.4807 | 6.9055 | 6.7842 | 6.9397 | 6.6536 | 56.5984 | 0.050939 |  | 62.069 | 100
19980524190000 | 1998-05-24 19:00 | 637.007 |  | 6.424 | 152.447 | 153.818 | 157.748 | 156.541 |  | 1485.626 | 1585.046 |  | 7.1106 | 6.991 | 7.7339 | 7.4836 | 6.9084 | 6.7856 | 6.936 | 6.646 | 56.5951 | 0.050936 |  | 62.069 | 100
19980524193000 | 1998-05-24 19:30 | 637.374 |  | 5.809 | 152.986 | 154.483 | 158.211 | 156.464 |  | 1483.793 | 1584.379 |  | 7.1152 | 7.0093 | 7.7454 | 7.5081 | 6.9031 | 6.7932 | 6.949 | 6.6575 | 56.6808 | 0.051013 |  | 62.069 | 100
19980524200000 | 1998-05-24 20:00 | 635.277 |  | 6.051 | 153.275 | 154.483 | 158.536 | 157.454 |  | 1483.959 | 1584.629 |  | 7.1267 | 7.0176 | 7.7478 | 7.5059 | 6.9253 | 6.804 | 6.9512 | 6.665 | 56.7435 | 0.051069 |  | 62.069 | 100
19980524203000 | 1998-05-24 20:30 | 634.176 |  | 5.318 | 153.661 | 154.679 | 158.801 | 158.145 |  | 1480.376 | 1577.629 |  | 7.0977 | 6.99 | 7.7234 | 7.4822 | 6.8862 | 6.7795 | 6.9275 | 6.6453 | 56.5318 | 0.050879 |  | 62.069 | 100
19980524210000 | 1998-05-24 21:00 | 637.898 |  | 6.788 | 153.8 | 154.849 | 158.938 | 158.067 |  | 1483.876 | 1584.629 |  | 7.1091 | 7.0129 | 7.7529 | 7.5088 | 6.9077 | 6.7856 | 6.9404 | 6.6597 | 56.6771 | 0.051009 |  | 62.069 | 100
19980524213000 | 1998-05-24 21:30 | 635.146 |  | 5.442 | 154.328 | 155.932 | 159.449 | 157.912 |  | 1486.709 | 1587.879 |  | 7.1221 | 7.0374 | 7.7744 | 7.5547 | 6.9314 | 6.814 | 6.9673 | 6.6833 | 56.8846 | 0.051196 |  | 62.069 | 100
19980524220000 | 1998-05-24 22:00 | 633.258 |  | 7.399 | 154.722 | 156.179 | 159.872 | 158.407 |  | 1485.793 | 1585.296 |  | 7.0886 | 7.0007 | 7.7285 | 7.4875 | 6.9045 | 6.7795 | 6.9275 | 6.6543 | 56.5711 | 0.050914 |  | 62.069 | 100
19980524223000 | 1998-05-24 22:30 | 634.831 |  | 5.807 | 155.082 | 156.298 | 160.157 | 158.278 |  | 1481.459 | 1580.712 |  | 7.1138 | 7.0161 | 7.7529 | 7.5105 | 6.9167 | 6.7986 | 6.9604 | 6.6719 | 56.7409 | 0.051067 |  | 62.069 | 100
19980524230000 | 1998-05-24 23:00 | 637.217 |  | 6.912 | 155.195 | 155.999 | 160.291 | 158.226 |  | 1485.126 | 1587.379 |  | 7.1479 | 7.0298 | 7.7896 | 7.5127 | 6.9397 | 6.8184 | 6.9778 | 6.6858 | 56.9017 | 0.051212 |  | 62.069 | 100
19980524233000 | 1998-05-24 23:30 | 631.056 |  | 5.074 | 155.02 | 156.324 | 160.119 | 158.056 |  | 1478.959 | 1578.712 |  | 7.1321 | 7.019 | 7.7576 | 7.521 | 6.9343 | 6.8069 | 6.9543 | 6.6711 | 56.7963 | 0.051117 |  | 62.069 | 100
19980525000000 | 1998-05-25 | 605.157 |  | 6.053 | 155.151 | 155.725 | 160.173 | 157.458 |  | 1366.873 | 1453.375 |  | 6.6772 | 6.5271 | 7.2053 | 6.8757 | 6.45 | 6.3088 | 6.4568 | 6.2148 | 52.7157 | 0.047444 |  | 62.069 | 100
19980525003000 | 1998-05-25 00:30 | 577.081 |  | 3.967 | 152.779 | 153.08 | 157.745 | 154.813 |  | 1330.121 | 1417.541 |  | 6.4209 | 6.2935 | 6.907 | 6.5598 | 6.2249 | 6.0867 | 6.231 | 5.9807 | 50.7045 | 0.045634 |  | 62.069 | 100
19980525010000 | 1998-05-25 01:00 | 529.555 |  | 3.605 | 150.1 | 149.991 | 154.922 | 149.743 |  | 1241.286 | 1313.204 |  | 6.0623 | 5.9243 | 6.488 | 6.1226 | 5.9121 | 5.8044 | 5.9395 | 5.6511 | 47.9043 | 0.043114 |  | 62.069 | 100
19980525013000 | 1998-05-25 01:30 | 485.122 |  | 1.154 | 149.939 | 148.934 | 151.837 | 147.944 |  | 1086.115 | 1145.783 |  | 5.877 | 5.7244 | 6.2295 | 5.8511 | 1.9929 | 5.6504 | 5.7839 | 5.481 | 42.5902 | 0.038331 |  | 62.069 | 100
19980525020000 | 1998-05-25 02:00 | 412.429 |  | 21.821 | 148.453 | 148.801 | 148.081 | 141.871 |  | 993.362 | 1038.363 |  | 4.9172 | 4.7561 | 5.0469 | 4.6533 | 4.7722 | 4.9141 | 5.0178 | 4.6013 | 38.6789 | 0.034811 |  | 62.069 | 100
19980525023000 | 1998-05-25 02:30 | 412.927 |  | 0.295 | 149.049 | 150.818 | 145.848 | 147.352 |  | 985.278 | 1029.446 |  | 4.9553 | 4.751 | 5.0759 | 4.6829 | 4.8242 | 4.8853 | 4.9934 | 4.5938 | 38.7618 | 0.034886 |  | 62.069 | 100
19980525030000 | 1998-05-25 03:00 | 419.009 |  | 1.399 | 150.263 | 150.984 | 148.43 | 148.756 |  | 993.612 | 1033.446 |  | 4.9072 | 4.7356 | 5.0256 | 4.644 | 4.77 | 4.8088 | 4.9233 | 4.5442 | 38.3587 | 0.034523 |  | 62.069 | 100
19980525033000 | 1998-05-25 03:30 | 369.962 |  | 0.54 | 150.745 | 149.86 | 149.19 | 146.642 |  | 862.358 | 892.109 |  | 3.2266 | 2.9779 | 4.6318 | 4.2581 | 4.4998 | 4.573 | 4.6951 | 4.2756 | 33.1379 | 0.029824 |  | 62.069 | 100
19980525040000 | 1998-05-25 04:00 | 373.501 |  | 3.118 | 149.242 | 148.855 | 147.267 | 145.637 |  | 885.859 | 914.61 |  | 3.177 | 3.0313 | 4.908 | 4.5281 | 4.6792 | 4.6968 | 4.8142 | 4.4365 | 34.2711 | 0.030844 |  | 62.069 | 100
19980525043000 | 1998-05-25 04:30 | 367.629 |  | 15.839 | 149.606 | 151.068 | 147.615 | 147.602 |  | 879.025 | 912.526 |  | 3.174 | 3.0564 | 4.8997 | 4.5356 | 4.6807 | 4.7363 | 4.8599 | 4.4563 | 34.3989 | 0.030959 |  | 62.069 | 100
19980525050000 | 1998-05-25 05:00 | 365.086 |  | 0.66 | 150.608 | 152.564 | 148.793 | 149.841 |  | 896.859 | 940.86 |  | 3.1923 | 3.0488 | 4.9043 | 4.5364 | 4.696 | 4.7151 | 4.8364 | 4.4548 | 34.3841 | 0.030946 |  | 62.069 | 100
19980525053000 | 1998-05-25 05:30 | 429.914 |  | 0.787 | 151.775 | 152.42 | 150.391 | 148.707 |  | 1016.613 | 1064.364 |  | 4.886 | 4.7266 | 5.1453 | 4.7998 | 4.8782 | 4.9004 | 5.0247 | 4.6921 | 39.0531 | 0.035148 |  | 62.069 | 100
19980525060000 | 1998-05-25 06:00 | 421.237 |  | 1.03 | 151.294 | 150.099 | 149.523 | 147.624 |  | 1017.029 | 1063.781 |  | 5.0073 | 4.8455 | 5.1819 | 4.834 | 4.8928 | 4.9072 | 5.0286 | 4.6707 | 39.368 | 0.035431 |  | 62.069 | 100
19980525063000 | 1998-05-25 06:30 | 519.148 |  | 2.133 | 150.911 | 155.05 | 149.169 | 151.337 |  | 1242.702 | 1323.121 |  | 6.0134 | 5.906 | 6.4187 | 6.1477 | 5.8845 | 5.803 | 5.9602 | 5.645 | 47.7785 | 0.043001 |  | 62.069 | 100
19980525070000 | 1998-05-25 07:00 | 521.428 |  | 2.137 | 152.108 | 150.506 | 150.656 | 147.041 |  | 1270.37 | 1357.456 |  | 6.1165 | 6.0066 | 6.5735 | 6.283 | 6.0334 | 5.9639 | 6.1028 | 5.7764 | 48.8561 | 0.04397 |  | 62.069 | 100
19980525073000 | 1998-05-25 07:30 | 628.487 |  | 5.442 | 151.129 | 154.899 | 150.394 | 153.909 |  | 1487.793 | 1600.129 |  | 7.1877 | 7.0869 | 7.8613 | 7.6042 | 7.0405 | 6.9023 | 7.0671 | 6.759 | 57.509 | 0.051758 |  | 62.069 | 100
19980525080000 | 1998-05-25 08:00 | 625.263 |  | 5.443 | 152.467 | 152.65 | 155.299 | 154.382 |  | 1466.542 | 1567.295 |  | 7.0664 | 6.9871 | 7.7263 | 7.4685 | 6.9275 | 6.7886 | 6.936 | 6.637 | 56.5374 | 0.050884 |  | 62.069 | 100
19980525083000 | 1998-05-25 08:30 | 631.135 |  | 4.707 | 151.943 | 153.876 | 156.36 | 155.362 |  | 1479.959 | 1579.545 |  | 7.1541 | 7.0076 | 7.821 | 7.4915 | 7.0122 | 6.8086 | 7.0259 | 6.6658 | 56.9867 | 0.051288 |  | 62.069 | 100
19980525090000 | 1998-05-25 09:00 | 630.06 |  | 5.565 | 152.515 | 154.83 | 157.248 | 156.068 |  | 1481.209 | 1584.629 |  | 7.1777 | 7.0327 | 7.856 | 7.5264 | 7.0405 | 6.8406 | 7.0366 | 6.6995 | 57.21 | 0.051489 |  | 62.069 | 100
19980525093000 | 1998-05-25 09:30 | 630.847 |  | 5.075 | 153.35 | 155.17 | 158.049 | 157.15 |  | 1487.459 | 1591.962 |  | 7.1709 | 7.0427 | 7.8491 | 7.5508 | 7.0298 | 6.8284 | 7.0259 | 6.6995 | 57.1971 | 0.051477 |  | 62.069 | 100
19980525100000 | 1998-05-25 10:00 | 631.083 |  | 5.81 | 153.992 | 156.005 | 158.701 | 157.49 |  | 1482.876 | 1585.379 |  | 7.1709 | 7.0466 | 7.853 | 7.5532 | 7.0413 | 6.8215 | 7.0313 | 6.7056 | 57.2234 | 0.051501 |  | 62.069 | 100
19980525103000 | 1998-05-25 10:30 | 634.307 |  | 5.198 | 154.464 | 155.876 | 159.192 | 157.609 |  | 1481.459 | 1585.129 |  | 7.1602 | 7.0459 | 7.8376 | 7.531 | 7.0298 | 6.8245 | 7.0291 | 6.6858 | 57.1439 | 0.05143 |  | 62.069 | 100
19980525110000 | 1998-05-25 11:00 | 635.277 |  | 7.155 | 154.751 | 156.371 | 159.526 | 159.342 |  | 1483.626 | 1586.296 |  | 7.1626 | 7.0474 | 7.8455 | 7.5532 | 7.0298 | 6.8252 | 7.0259 | 6.6941 | 57.1837 | 0.051465 |  | 62.069 | 100
19980525113000 | 1998-05-25 11:30 | 632.131 |  | 5.563 | 155.268 | 157.14 | 159.898 | 159.367 |  | 1478.459 | 1581.462 |  | 7.145 | 7.0229 | 7.8193 | 7.55 | 7.0039 | 6.8147 | 7.0154 | 6.6826 | 57.0538 | 0.051348 |  | 62.069 | 100
19980525120000 | 1998-05-25 12:00 | 634.491 |  | 7.639 | 155.585 | 157.361 | 160.22 | 158.599 |  | 1481.626 | 1582.379 |  | 7.1487 | 6.9939 | 7.8157 | 7.5044 | 7.0061 | 6.7886 | 6.9885 | 6.6665 | 56.9124 | 0.051221 |  | 62.069 | 100
19980525123000 | 1998-05-25 12:30 | 630.716 |  | 6.052 | 155.971 | 157.816 | 160.776 | 159.796 |  | 1486.459 | 1587.296 |  | 7.158 | 7.0222 | 7.8301 | 7.5149 | 7.0276 | 6.8079 | 7.0137 | 6.6833 | 57.0577 | 0.051352 |  | 62.069 | 100
19980525130000 | 1998-05-25 13:00 | 628.199 |  | 8.131 | 156.297 | 158.233 | 161.165 | 159.718 |  | 1466.042 | 1567.212 |  | 7.1091 | 6.9688 | 7.7783 | 7.4609 | 6.9771 | 6.7703 | 6.9709 | 6.6316 | 56.667 | 0.051 |  | 62.069 | 100
19980525133000 | 1998-05-25 13:30 | 625.447 |  | 6.176 | 156.256 | 157.986 | 161.069 | 159.223 |  | 1478.042 | 1579.962 |  | 7.1267 | 6.9885 | 7.8018 | 7.4661 | 6.9856 | 6.7764 | 6.981 | 6.6353 | 56.7614 | 0.051085 |  | 62.069 | 100
19980525140000 | 1998-05-25 14:00 | 624.424 |  | 7.762 | 156.039 | 157.047 | 160.929 | 158.532 |  | 1468.125 | 1572.045 |  | 7.1069 | 6.9595 | 7.7629 | 7.4409 | 6.9702 | 6.7529 | 6.9497 | 6.623 | 56.566 | 0.050909 |  | 62.069 | 100
19980525143000 | 1998-05-25 14:30 | 616.665 |  | 6.546 | 155.84 | 157.919 | 160.702 | 159.652 |  | 1475.959 | 1579.545 |  | 7.0603 | 6.9382 | 7.708 | 7.4243 | 6.9246 | 6.7354 | 6.9329 | 6.6003 | 56.324 | 0.050692 |  | 62.069 | 100
19980525150000 | 1998-05-25 15:00 | 615.066 |  | 6.787 | 156.738 | 158.61 | 161.581 | 160.343 |  | 1471.876 | 1573.795 |  | 7.0718 | 6.9497 | 7.7332 | 7.4395 | 6.9336 | 6.7397 | 6.9382 | 6.6047 | 56.4104 | 0.050769 |  | 62.069 | 100
19980525153000 | 1998-05-25 15:30 | 618.788 |  | 7.155 | 156.759 | 158.048 | 161.757 | 160.028 |  | 1468.709 | 1569.295 |  | 7.0542 | 6.9146 | 7.7095 | 7.3982 | 6.9063 | 6.7085 | 6.9045 | 6.5728 | 56.1686 | 0.050552 |  | 62.069 | 100
19980525160000 | 1998-05-25 16:00 | 614.935 |  | 9.115 | 156.315 | 158.151 | 161.34 | 159.884 |  | 1469.375 | 1567.712 |  | 7.0405 | 6.894 | 7.7034 | 7.3701 | 6.9031 | 6.688 | 6.8916 | 6.5627 | 56.0534 | 0.050448 |  | 62.069 | 100
19980525163000 | 1998-05-25 16:30 | 615.04 |  | 21.814 | 155.943 | 157.342 | 160.931 | 159.322 |  | 1459.709 | 1555.878 |  | 6.9778 | 6.8467 | 7.6248 | 7.3281 | 6.8521 | 6.6521 | 6.8467 | 6.5149 | 55.6432 | 0.050079 |  | 62.069 | 100
19980525170000 | 1998-05-25 17:00 | 615.459 |  | 9.966 | 155.664 | 157.445 | 160.526 | 159.426 |  | 1458.125 | 1555.795 |  | 6.9939 | 6.8306 | 7.634 | 7.2944 | 6.8467 | 6.6384 | 6.8367 | 6.5027 | 55.5774 | 0.05002 |  | 62.069 | 100
19980525173000 | 1998-05-25 17:30 | 613.231 |  | 6.79 | 155.363 | 156.559 | 160.158 | 157.796 |  | 1456.792 | 1552.961 |  | 7.0244 | 6.8726 | 7.6606 | 7.3572 | 6.8909 | 6.6858 | 6.8887 | 6.5315 | 55.9117 | 0.050321 |  | 62.069 | 100
19980525180000 | 1998-05-25 18:00 | 617.137 |  | 8.984 | 154.657 | 156.363 | 159.492 | 157.353 |  | 1461.709 | 1559.128 |  | 7.0129 | 6.8818 | 7.6492 | 7.3511 | 6.8696 | 6.6887 | 6.8506 | 6.5476 | 55.8515 | 0.050266 |  | 62.069 | 100
19980525183000 | 1998-05-25 18:30 | 619.077 |  | 7.521 | 153.784 | 155.125 | 158.679 | 156.115 |  | 1450.458 | 1546.794 |  | 7.0007 | 6.875 | 7.6355 | 7.3669 | 6.8574 | 6.6873 | 6.8323 | 6.54 | 55.7951 | 0.050216 |  | 62.069 | 100
19980525190000 | 1998-05-25 19:00 | 619.155 |  | 20.244 | 153.219 | 154.656 | 158.153 | 156.884 |  | 1448.625 | 1542.544 |  | 6.9802 | 6.8567 | 7.6042 | 7.3235 | 6.8391 | 6.6765 | 6.8337 | 6.5261 | 55.64 | 0.050076 |  | 62.069 | 100
19980525193000 | 1998-05-25 19:30 | 621.541 |  | 6.913 | 153.316 | 154.527 | 158.241 | 156.754 |  | 1448.542 | 1541.544 |  | 6.9666 | 6.8679 | 7.5881 | 7.3486 | 6.8306 | 6.6804 | 6.8398 | 6.5347 | 55.6567 | 0.050091 |  | 62.069 | 100
19980525200000 | 1998-05-25 20:00 | 620.492 |  | 9.113 | 153.508 | 154.748 | 158.392 | 156.729 |  | 1443.458 | 1539.794 |  | 6.9612 | 6.8467 | 7.5891 | 7.3083 | 6.8191 | 6.6621 | 6.8162 | 6.511 | 55.5137 | 0.049962 |  | 62.069 | 100
19980525203000 | 1998-05-25 20:30 | 618.605 |  | 7.4 | 153.527 | 155.218 | 158.392 | 156.95 |  | 1450.375 | 1542.378 |  | 6.9795 | 6.8582 | 7.6135 | 7.3318 | 6.8467 | 6.6765 | 6.8337 | 6.5232 | 55.6631 | 0.050097 |  | 62.069 | 100
19980525210000 | 1998-05-25 21:00 | 614.358 |  | 8.618 | 154.361 | 156.249 | 159.261 | 157.734 |  | 1468.542 | 1562.878 |  | 7.0115 | 6.8894 | 7.644 | 7.3616 | 6.8765 | 6.7085 | 6.8628 | 6.5476 | 55.9019 | 0.050312 |  | 62.069 | 100
19980525213000 | 1998-05-25 21:30 | 614.751 |  | 5.809 | 155.316 | 156.053 | 160.088 | 158.528 |  | 1467.292 | 1566.795 |  | 7.0076 | 6.874 | 7.6362 | 7.3623 | 6.8604 | 6.6909 | 6.8481 | 6.5393 | 55.8188 | 0.050237 |  | 62.069 | 100
19980525220000 | 1998-05-25 22:00 | 613.807 |  | 8.985 | 155.22 | 155.181 | 160.025 | 157.904 |  | 1467.792 | 1561.712 |  | 6.9771 | 6.8779 | 7.6028 | 7.3303 | 6.842 | 6.6865 | 6.8445 | 6.5339 | 55.695 | 0.050126 |  | 62.069 | 100
19980525223000 | 1998-05-25 22:30 | 613.362 |  | 6.422 | 154.708 | 155.794 | 159.602 | 158.27 |  | 1469.875 | 1567.628 |  | 6.9666 | 6.8711 | 7.5942 | 7.3296 | 6.8337 | 6.6658 | 6.8291 | 6.5178 | 55.6079 | 0.050047 |  | 62.069 | 100
19980525230000 | 1998-05-25 23:00 | 618.578 |  | 8.74 | 154.299 | 153.293 | 159.261 | 155.521 |  | 1437.708 | 1531.877 |  | 6.9351 | 6.8359 | 7.5593 | 7.2632 | 6.8 | 6.6255 | 6.7749 | 6.479 | 55.2729 | 0.049746 |  | 62.069 | 100
19980525233000 | 1998-05-25 23:30 | 552.44 |  | 6.179 | 150.457 | 149.606 | 155.182 | 148.616 |  | 1282.62 | 1363.789 |  | 6.2356 | 6.1128 | 6.6926 | 6.3684 | 6.1111 | 5.9692 | 6.1233 | 5.8303 | 49.4433 | 0.044499 |  | 62.069 | 100
19980526000000 | 1998-05-26 | 459.196 |  | 3.118 | 149.44 | 148.575 | 150.728 | 145.605 |  | 1049.78 | 1116.949 |  | 5.1865 | 4.9653 | 5.3689 | 4.9194 | 5.0339 | 4.9836 | 5.114 | 4.7859 | 40.3575 | 0.036322 |  | 62.069 | 100
19980526003000 | 1998-05-26 00:30 | 425.484 |  | 1.272 | 148.524 | 150.045 | 146.68 | 145.095 |  | 983.195 | 1044.697 |  | 4.8828 | 4.6746 | 5.0256 | 4.6218 | 4.7959 | 4.8569 | 4.9431 | 4.4983 | 38.299 | 0.034469 |  | 62.069 | 100
19980526010000 | 1998-05-26 01:00 | 423.334 |  | 2.012 | 149.657 | 150.536 | 147.279 | 147.318 |  | 994.195 | 1059.03 |  | 4.9514 | 4.7676 | 5.0928 | 4.6914 | 4.8354 | 4.9065 | 5.0149 | 4.6089 | 38.8689 | 0.034982 |  | 62.069 | 100
19980526013000 | 1998-05-26 01:30 | 418.59 |  | 1.153 | 150.308 | 150.753 | 148.513 | 148.526 |  | 985.362 | 1049.53 |  | 5.0735 | 4.9309 | 5.2529 | 4.876 | 4.9697 | 3.4775 | 5.1567 | 4.7378 | 38.475 | 0.034628 |  | 62.069 | 100
19980526020000 | 1998-05-26 02:00 | 416.571 |  | 0.905 | 150.525 | 151.234 | 149.042 | 147.521 |  | 977.945 | 1040.697 |  | 5.1133 | 4.988 | 5.3284 | 5.0063 | 5.0012 | 3.5386 | 5.2017 | 4.8264 | 39.0039 | 0.035104 |  | 62.069 | 100
19980526023000 | 1998-05-26 02:30 | 419.009 |  | 1.031 | 150.724 | 151.544 | 148.52 | 147.336 |  | 992.279 | 1057.114 |  | 4.937 | 4.7578 | 5.0667 | 4.7378 | 4.8181 | 4.8569 | 4.979 | 4.5999 | 38.7532 | 0.034878 |  | 62.069 | 100
19980526030000 | 1998-05-26 03:00 | 417.934 |  | 1.275 | 150.7 | 150.513 | 148.694 | 147.79 |  | 987.195 | 1049.53 |  | 4.9546 | 4.7761 | 5.0889 | 4.7517 | 4.8311 | 4.8652 | 5.0063 | 4.6089 | 38.8828 | 0.034995 |  | 62.069 | 100
19980526033000 | 1998-05-26 03:30 | 423.334 |  | 0.908 | 150.106 | 150.394 | 148.738 | 147.177 |  | 970.445 | 1032.613 |  | 4.9355 | 4.731 | 5.0767 | 4.696 | 4.8257 | 4.8623 | 4.979 | 4.5923 | 38.6985 | 0.034829 |  | 62.069 | 100
19980526040000 | 1998-05-26 04:00 | 425.012 |  | 1.4 | 150.156 | 152.23 | 148.351 | 149.012 |  | 990.445 | 1051.447 |  | 4.9392 | 4.7378 | 5.0706 | 4.6846 | 4.825 | 4.8538 | 4.9805 | 4.5784 | 38.6699 | 0.034803 |  | 62.069 | 100
19980526043000 | 1998-05-26 04:30 | 426.218 |  | 0.784 | 151.3 | 151.473 | 149.59 | 148.007 |  | 993.862 | 1054.864 |  | 4.9209 | 4.7356 | 5.0569 | 4.7051 | 4.8225 | 4.8577 | 4.9758 | 4.5906 | 38.6651 | 0.034799 |  | 62.069 | 100
19980526050000 | 1998-05-26 05:00 | 423.964 |  | 0.908 | 150.387 | 150.013 | 148.633 | 146.548 |  | 993.529 | 1057.53 |  | 4.95 | 4.7388 | 5.105 | 4.6921 | 4.8347 | 4.8569 | 4.9797 | 4.5891 | 38.7463 | 0.034872 |  | 62.069 | 100
19980526053000 | 1998-05-26 05:30 | 421.735 |  | 0.537 | 150.08 | 151.081 | 148.262 | 148.111 |  | 1000.945 | 1066.614 |  | 4.9036 | 4.7463 | 5.0361 | 4.709 | 4.7959 | 4.8386 | 4.9661 | 4.5845 | 38.5801 | 0.034722 |  | 62.069 | 100
19980526060000 | 1998-05-26 06:00 | 421.001 |  | 0.904 | 150.648 | 151.225 | 149.121 | 147.512 |  | 1005.612 | 1070.031 |  | 4.9209 | 4.7571 | 5.0522 | 4.718 | 4.8171 | 4.8623 | 4.9744 | 4.6052 | 38.7072 | 0.034836 |  | 62.069 | 100
19980526063000 | 1998-05-26 06:30 | 489.316 |  | 1.52 | 149.856 | 151.184 | 147.89 | 146.729 |  | 1160.95 | 1240.202 |  | 5.7595 | 5.6519 | 6.0952 | 5.8381 | 5.6443 | 5.6587 | 5.7778 | 5.4299 | 45.8554 | 0.04127 |  | 62.069 | 100
19980526070000 | 1998-05-26 07:00 | 597.004 |  | 22.428 | 152.742 | 154.562 | 151.055 | 151.839 |  | 1397.707 | 1498.46 |  | 6.7964 | 6.7163 | 7.4104 | 7.1792 | 6.6726 | 6.6079 | 6.7383 | 6.4094 | 54.5305 | 0.049077 |  | 62.069 | 100
19980526073000 | 1998-05-26 07:30 | 624.791 |  | 5.684 | 152.8 | 152.936 | 154.184 | 154.174 |  | 1456.458 | 1555.795 |  | 7.0291 | 6.9314 | 7.6821 | 7.4524 | 6.8933 | 6.781 | 6.9106 | 6.604 | 56.2839 | 0.050656 |  | 62.069 | 100
19980526080000 | 1998-05-26 08:00 | 624.424 |  | 6.66 | 152.13 | 153.343 | 156.383 | 154.828 |  | 1459.375 | 1559.378 |  | 7.0496 | 6.9709 | 7.6768 | 7.447 | 6.9038 | 6.7964 | 6.9268 | 6.6194 | 56.3907 | 0.050752 |  | 62.069 | 100
19980526083000 | 1998-05-26 08:30 | 626.469 |  | 5.927 | 152.48 | 153.502 | 157.108 | 155.235 |  | 1456.875 | 1553.461 |  | 7.0154 | 6.9253 | 7.6606 | 7.4136 | 6.8726 | 6.7703 | 6.8872 | 6.6072 | 56.1522 | 0.050537 |  | 62.069 | 100
19980526090000 | 1998-05-26 09:00 | 618.631 |  | 8.38 | 152.573 | 153.595 | 157.454 | 156.07 |  | 1431.541 | 1524.71 |  | 7.0938 | 7.0115 | 7.7439 | 7.499 | 6.9429 | 6.8496 | 6.9673 | 4.5708 | 54.6788 | 0.049211 |  | 62.069 | 100
19980526093000 | 1998-05-26 09:30 | 616.376 |  | 24.149 | 152.578 | 153.558 | 157.854 | 156.281 |  | 1451.375 | 1547.544 |  | 7.2556 | 7.158 | 7.9324 | 7.689 | 7.1052 | 6.9832 | 7.1008 | 4.5754 | 55.7996 | 0.05022 |  | 62.069 | 100
19980526100000 | 1998-05-26 10:00 | 618.893 |  | 5.929 | 152.972 | 154.615 | 158.261 | 156.1 |  | 1443.791 | 1540.044 |  | 7.084 | 6.9863 | 7.7202 | 7.4685 | 6.9443 | 6.8208 | 6.9282 | 5.6543 | 55.6066 | 0.050046 |  | 62.069 | 100
19980526103000 | 1998-05-26 10:30 | 618.002 |  | 6.05 | 152.94 | 153.599 | 158.378 | 156.322 |  | 1435.375 | 1529.794 |  | 7.209 | 7.1121 | 7.876 | 7.5967 | 7.0588 | 6.9299 | 7.0588 | 4.5273 | 55.3686 | 0.049832 |  | 62.069 | 100
19980526110000 | 1998-05-26 11:00 | 622.301 |  | 7.51 | 152.409 | 153.104 | 157.92 | 155.332 |  | 1461.625 | 1557.795 |  | 7.0046 | 6.9092 | 7.6272 | 7.3745 | 6.8557 | 6.7314 | 6.8582 | 6.6162 | 55.977 | 0.050379 |  | 62.069 | 100
19980526113000 | 1998-05-26 11:30 | 621.541 |  | 5.563 | 152.652 | 155.084 | 157.736 | 157.312 |  | 1452.625 | 1546.461 |  | 6.9917 | 6.8955 | 7.624 | 7.3533 | 6.8428 | 6.7207 | 6.842 | 6.6155 | 55.8855 | 0.050297 |  | 62.069 | 100
19980526120000 | 1998-05-26 12:00 | 612.942 |  | 7.146 | 153.155 | 154.537 | 158.107 | 156.023 |  | 1450.042 | 1549.628 |  | 7.2266 | 7.1267 | 7.8674 | 7.6606 | 7.0671 | 6.958 | 4.9058 | 6.8506 | 55.6628 | 0.050097 |  | 62.069 | 100
19980526123000 | 1998-05-26 12:30 | 629.693 |  | 6.662 | 152.629 | 154.589 | 157.65 | 156.322 |  | 1486.959 | 1564.962 |  | 7.0718 | 6.9709 | 7.7285 | 7.4661 | 6.9421 | 6.804 | 6.9443 | 6.7056 | 56.6333 | 0.05097 |  | 62.069 | 100
19980526130000 | 1998-05-26 13:00 | 633.783 |  | 8.375 | 153.039 | 154.682 | 156.918 | 153.939 |  | 1487.459 | 1566.962 |  | 7.1335 | 7.0413 | 7.782 | 7.5554 | 6.9788 | 6.865 | 6.9932 | 6.7598 | 57.109 | 0.051398 |  | 62.069 | 100
19980526133000 | 1998-05-26 13:30 | 636.693 |  | 6.662 | 153.237 | 155.032 | 155.519 | 154.29 |  | 1490.376 | 1569.045 |  | 7.1335 | 7.032 | 7.7896 | 7.5281 | 6.9856 | 6.8557 | 7.0015 | 6.7415 | 57.0675 | 0.051361 |  | 62.069 | 100
19980526140000 | 1998-05-26 14:00 | 637.191 |  | 8.249 | 153.777 | 155.893 | 155.896 | 154.656 |  | 1488.209 | 1567.795 |  | 7.1335 | 7.0381 | 7.7905 | 7.5371 | 6.9771 | 6.8628 | 6.9993 | 6.7581 | 57.0965 | 0.051387 |  | 62.069 | 100
19980526143000 | 1998-05-26 14:30 | 634.779 |  | 6.907 | 154.321 | 156.492 | 156.34 | 155.502 |  | 1489.459 | 1570.962 |  | 7.1487 | 7.061 | 7.814 | 7.5601 | 6.9893 | 6.8726 | 7.0122 | 6.7749 | 57.2328 | 0.05151 |  | 62.069 | 100
19980526150000 | 1998-05-26 15:00 | 638.554 |  | 9.348 | 154.833 | 156.714 | 156.873 | 155.723 |  | 1496.46 | 1579.879 |  | 7.1777 | 7.0779 | 7.8384 | 7.5996 | 7.0313 | 6.8962 | 7.0344 | 6.791 | 57.4465 | 0.051702 |  | 62.069 | 100
19980526153000 | 1998-05-26 15:30 | 636.876 |  | 7.637 | 155.242 | 156.023 | 157.2 | 156.518 |  | 1490.209 | 1571.878 |  | 7.1091 | 7.0251 | 7.7622 | 7.5303 | 6.9504 | 6.8391 | 6.9741 | 6.7322 | 56.9225 | 0.05123 |  | 62.069 | 100
19980526160000 | 1998-05-26 16:00 | 625.971 |  | 9.474 | 155.101 | 155.775 | 157.167 | 154.785 |  | 1463.042 | 1538.794 |  | 7.0068 | 6.9092 | 7.6423 | 7.3806 | 6.855 | 6.7231 | 6.8635 | 6.627 | 56.0075 | 0.050407 |  | 62.069 | 100
19980526163000 | 1998-05-26 16:30 | 620.649 |  | 7.639 | 154.538 | 156.1 | 156.676 | 155.358 |  | 1464.042 | 1542.878 |  | 6.9978 | 6.9063 | 7.6423 | 7.4158 | 6.8704 | 6.7605 | 6.8916 | 6.6421 | 56.1268 | 0.050514 |  | 62.069 | 100
19980526170000 | 1998-05-26 17:00 | 622.301 |  | 8.745 | 154.862 | 156.621 | 156.923 | 156.126 |  | 1465.959 | 1538.711 |  | 7.0137 | 6.9192 | 7.6509 | 7.4287 | 6.8779 | 6.7383 | 6.8872 | 6.6377 | 56.1536 | 0.050538 |  | 62.069 | 100
19980526173000 | 1998-05-26 17:30 | 621.436 |  | 6.423 | 155.207 | 156.776 | 157.252 | 155.786 |  | 1465.625 | 1542.461 |  | 7.019 | 6.9116 | 7.6492 | 7.3982 | 6.8704 | 6.7581 | 6.8916 | 6.6431 | 56.1412 | 0.050527 |  | 62.069 | 100
19980526180000 | 1998-05-26 18:00 | 621.069 |  | 8.619 | 155.22 | 156.204 | 157.313 | 156.204 |  | 1464.125 | 1541.544 |  | 7.0237 | 6.9106 | 7.6667 | 7.373 | 6.8711 | 6.7451 | 6.884 | 6.6277 | 56.1019 | 0.050492 |  | 62.069 | 100
19980526183000 | 1998-05-26 18:30 | 621.619 |  | 6.541 | 155.229 | 157.22 | 157.339 | 156.477 |  | 1464.959 | 1541.044 |  | 7.0007 | 6.8916 | 7.6462 | 7.3745 | 6.8657 | 6.7422 | 6.8848 | 6.6223 | 56.028 | 0.050425 |  | 62.069 | 100
19980526190000 | 1998-05-26 19:00 | 622.537 |  | 9.474 | 155.526 | 157.245 | 157.65 | 156.503 |  | 1464.709 | 1540.378 |  | 6.9924 | 6.8879 | 7.6309 | 7.3738 | 6.8574 | 6.7361 | 6.8733 | 6.6162 | 55.968 | 0.050371 |  | 62.069 | 100
19980526193000 | 1998-05-26 19:30 | 620.099 |  | 7.154 | 155.551 | 157.271 | 157.652 | 156.776 |  | 1466.292 | 1539.044 |  | 7.0039 | 6.8833 | 7.634 | 7.3708 | 6.8521 | 6.7285 | 6.8628 | 6.6064 | 55.9418 | 0.050348 |  | 62.069 | 100
19980526200000 | 1998-05-26 20:00 | 622.904 |  | 10.089 | 155.541 | 157.519 | 157.689 | 156.776 |  | 1458.542 | 1534.044 |  | 6.9849 | 6.8794 | 7.6035 | 7.3511 | 6.8345 | 6.7231 | 6.8574 | 6.6018 | 55.8357 | 0.050252 |  | 62.069 | 100
19980526203000 | 1998-05-26 20:30 | 622.851 |  | 6.908 | 155.73 | 157.271 | 157.905 | 157.271 |  | 1462.542 | 1537.877 |  | 7.0076 | 6.8811 | 7.6362 | 7.3745 | 6.8521 | 6.739 | 6.8711 | 6.6201 | 55.9817 | 0.050384 |  | 62.069 | 100
19980526210000 | 1998-05-26 21:00 | 621.514 |  | 10.211 | 156.122 | 158.38 | 158.196 | 157.39 |  | 1462.459 | 1541.461 |  | 7.0154 | 6.8901 | 7.6362 | 7.3723 | 6.8582 | 6.7361 | 6.8657 | 6.6155 | 55.9895 | 0.050391 |  | 62.069 | 100
19980526213000 | 1998-05-26 21:30 | 620.78 |  | 23.027 | 156.178 | 158.003 | 158.395 | 157.755 |  | 1465.625 | 1544.044 |  | 7.0222 | 6.9077 | 7.6631 | 7.3799 | 6.8811 | 6.762 | 6.8887 | 6.6384 | 56.1431 | 0.050529 |  | 62.069 | 100
19980526220000 | 1998-05-26 22:00 | 621.226 |  | 10.82 | 156.177 | 157.833 | 158.395 | 156.843 |  | 1464.042 | 1538.794 |  | 6.9893 | 6.9009 | 7.6218 | 7.3877 | 6.8467 | 6.7483 | 6.8801 | 6.623 | 55.9978 | 0.050398 |  | 62.069 | 100
19980526223000 | 1998-05-26 22:30 | 621.121 |  | 7.645 | 156.177 | 157.951 | 158.36 | 156.466 |  | 1466.375 | 1543.211 |  | 6.9863 | 6.8994 | 7.6172 | 7.3975 | 6.8506 | 6.7397 | 6.8726 | 6.6223 | 55.9856 | 0.050387 |  | 62.069 | 100
19980526230000 | 1998-05-26 23:00 | 610.137 |  | 10.58 | 156.174 | 156.78 | 158.32 | 156.285 |  | 1447.292 | 1518.794 |  | 6.9246 | 6.8245 | 7.5515 | 7.2671 | 6.781 | 6.6797 | 6.8054 | 6.5576 | 55.3914 | 0.049852 |  | 62.069 | 100
19980526233000 | 1998-05-26 23:30 | 558.364 |  | 5.563 | 155.657 | 154.774 | 157.654 | 154.279 |  | 1309.871 | 1359.706 |  | 6.4216 | 6.2751 | 6.9185 | 6.5789 | 6.283 | 6.1401 | 6.2759 | 6.0417 | 50.9348 | 0.045841 |  | 62.069 | 100
19980527000000 | 1998-05-27 | 575.246 |  | 24.758 | 152.944 | 154.124 | 155.025 | 152.391 |  | 1373.289 | 1432.791 |  | 6.5835 | 6.4438 | 7.1113 | 6.8101 | 6.4453 | 6.3232 | 6.4453 | 6.1904 | 52.3529 | 0.047118 |  | 62.069 | 100
19980527003000 | 1998-05-27 00:30 | 519.384 |  | 4.214 | 152.915 | 153.954 | 155.12 | 156.924 |  | 1242.619 | 1284.62 |  | 6.0906 | 5.9304 | 6.4744 | 6.1196 | 5.9517 | 5.8403 | 5.9739 | 5.7014 | 48.0823 | 0.043274 |  | 62.069 | 100
19980527010000 | 1998-05-27 01:00 | 523.211 |  | 6.784 | 150.642 | 151.179 | 154.557 | 150.189 |  | 1262.453 | 1304.204 |  | 6.0593 | 5.9053 | 6.4553 | 6.0884 | 5.9395 | 5.8618 | 5.9785 | 5.6802 | 47.9683 | 0.043171 |  | 62.069 | 100
19980527013000 | 1998-05-27 01:30 | 444.253 |  | 2.505 | 149.602 | 147.193 | 151.435 | 145.213 |  | 1084.781 | 1078.864 |  | 5.2078 | 5.0317 | 5.3872 | 5.0271 | 5.1094 | 5.1492 | 5.2429 | 4.8828 | 41.0381 | 0.036934 |  | 62.069 | 100
19980527020000 | 1998-05-27 02:00 | 441.449 |  | 3.847 | 148.733 | 150.463 | 147.335 | 145.265 |  | 1078.781 | 1071.864 |  | 5.2117 | 5.0081 | 5.4131 | 5.0264 | 5.1033 | 5.1255 | 5.2239 | 4.8508 | 40.9628 | 0.036867 |  | 62.069 | 100
19980527023000 | 1998-05-27 02:30 | 438.853 |  | 1.765 | 150.515 | 151.556 | 148.004 | 147.348 |  | 1088.115 | 1083.698 |  | 5.2644 | 5.0735 | 5.468 | 5.114 | 5.1667 | 5.2041 | 5.2932 | 4.9119 | 41.4958 | 0.037346 |  | 62.069 | 100
19980527030000 | 1998-05-27 03:00 | 443.886 |  | 3.238 | 150.488 | 150.68 | 149.032 | 147.215 |  | 1080.364 | 1074.948 |  | 5.2454 | 5.0759 | 5.459 | 5.0979 | 5.1277 | 5.1689 | 5.2781 | 4.8989 | 41.3518 | 0.037217 |  | 62.069 | 100
19980527033000 | 1998-05-27 03:30 | 447.95 |  | 1.763 | 150.194 | 150.588 | 148.642 | 146.875 |  | 1089.115 | 1084.698 |  | 5.2537 | 5.0454 | 5.4429 | 5.0835 | 5.1208 | 5.1345 | 5.2505 | 4.8835 | 41.2148 | 0.037093 |  | 62.069 | 100
19980527040000 | 1998-05-27 04:00 | 444.62 |  | 2.501 | 150.012 | 151.171 | 148.13 | 146.221 |  | 1081.948 | 1073.614 |  | 5.2627 | 5.0857 | 5.4834 | 5.1064 | 5.1384 | 5.1628 | 5.2788 | 4.9004 | 41.4186 | 0.037277 |  | 62.069 | 100
19980527043000 | 1998-05-27 04:30 | 442.523 |  | 1.517 | 150.437 | 151.496 | 148.469 | 148.031 |  | 1076.364 | 1069.614 |  | 5.2666 | 5.114 | 5.4688 | 5.1599 | 5.1338 | 5.1965 | 5.3101 | 4.9438 | 41.5935 | 0.037434 |  | 62.069 | 100
19980527050000 | 1998-05-27 05:00 | 446.56 |  | 2.38 | 151.371 | 151.064 | 149.718 | 147.846 |  | 1106.448 | 1106.198 |  | 5.2795 | 5.1201 | 5.4834 | 5.1553 | 5.156 | 5.1782 | 5.2993 | 4.9377 | 41.6095 | 0.037449 |  | 62.069 | 100
19980527053000 | 1998-05-27 05:30 | 520.222 |  | 3.602 | 151.18 | 154.111 | 149.741 | 150.398 |  | 1262.036 | 1302.537 |  | 6.105 | 5.9707 | 6.5354 | 6.2317 | 5.9646 | 5.9128 | 6.054 | 5.7412 | 48.5154 | 0.043664 |  | 62.069 | 100
19980527060000 | 1998-05-27 06:00 | 583.556 |  | 8.131 | 152.178 | 153.018 | 153.021 | 155.246 |  | 1427.708 | 1494.293 |  | 6.752 | 6.6582 | 7.2944 | 7.0876 | 6.6003 | 6.5559 | 6.6797 | 6.3882 | 54.0163 | 0.048615 |  | 62.069 | 100
19980527063000 | 1998-05-27 06:30 | 612.654 |  | 6.05 | 153.518 | 156.277 | 157.839 | 158.257 |  | 1478.626 | 1555.128 |  | 6.9871 | 6.8567 | 7.6143 | 7.3501 | 6.8337 | 6.7214 | 6.855 | 6.5842 | 55.8025 | 0.050222 |  | 62.069 | 100
19980527070000 | 1998-05-27 07:00 | 622.275 |  | 9.23 | 154.108 | 152.826 | 159.107 | 155.549 |  | 1454.458 | 1520.71 |  | 6.9795 | 6.8977 | 7.6096 | 7.3975 | 6.833 | 6.7451 | 6.8855 | 6.6216 | 55.9695 | 0.050373 |  | 62.069 | 100
19980527073000 | 1998-05-27 07:30 | 626.731 |  | 7.396 | 152.126 | 152.62 | 157.402 | 155.59 |  | 1466.959 | 1537.794 |  | 7.0298 | 6.9382 | 7.6553 | 7.428 | 6.8733 | 6.7764 | 6.9192 | 6.6553 | 56.2755 | 0.050648 |  | 62.069 | 100
19980527080000 | 1998-05-27 08:00 | 625.289 |  | 8.741 | 151.92 | 153.728 | 157.315 | 155.461 |  | 1474.376 | 1548.211 |  | 7.0725 | 6.9778 | 7.718 | 7.4814 | 6.9092 | 6.8025 | 6.9519 | 6.6833 | 56.5966 | 0.050937 |  | 62.069 | 100
19980527083000 | 1998-05-27 08:30 | 630.113 |  | 7.882 | 152.455 | 155.28 | 157.916 | 157.26 |  | 1488.793 | 1563.712 |  | 7.074 | 6.99 | 7.7119 | 7.5112 | 6.9307 | 6.8284 | 6.9626 | 6.7056 | 56.7144 | 0.051043 |  | 62.069 | 100
19980527090000 | 1998-05-27 09:00 | 628.854 |  | 9.843 | 153.597 | 155.45 | 159.056 | 158.173 |  | 1486.293 | 1563.378 |  | 7.0991 | 7.0251 | 7.7539 | 7.5532 | 6.9421 | 6.855 | 6.9839 | 6.7336 | 56.9459 | 0.051251 |  | 62.069 | 100
19980527093000 | 1998-05-27 09:30 | 633.547 |  | 7.642 | 154.266 | 155.893 | 159.716 | 158.369 |  | 1485.876 | 1560.045 |  | 7.0938 | 7 | 7.7461 | 7.5264 | 6.9404 | 6.8391 | 6.9878 | 6.7214 | 56.855 | 0.051169 |  | 62.069 | 100
19980527100000 | 1998-05-27 10:00 | 628.645 |  | 10.577 | 154.083 | 155.048 | 159.698 | 158.018 |  | 1487.459 | 1563.795 |  | 7.1008 | 7.0093 | 7.7454 | 7.4915 | 6.9351 | 6.8323 | 6.968 | 6.7139 | 56.7963 | 0.051117 |  | 62.069 | 100
19980527103000 | 1998-05-27 10:30 | 631.03 |  | 8.373 | 153.964 | 155.125 | 159.604 | 158.096 |  | 1486.959 | 1563.378 |  | 7.0962 | 6.9961 | 7.7407 | 7.4937 | 6.9275 | 6.8123 | 6.9526 | 6.7024 | 56.7215 | 0.051049 |  | 62.069 | 100
19980527110000 | 1998-05-27 11:00 | 634.15 |  | 10.822 | 154.177 | 156.012 | 159.871 | 158.982 |  | 1492.293 | 1566.962 |  | 7.1213 | 7.0107 | 7.7852 | 7.5088 | 6.9482 | 6.8245 | 6.9634 | 6.7139 | 56.876 | 0.051188 |  | 62.069 | 100
19980527113000 | 1998-05-27 11:30 | 639.602 |  | 8.495 | 154.562 | 156.115 | 160.368 | 159.828 |  | 1490.959 | 1566.628 |  | 7.1191 | 7.0229 | 7.7905 | 7.5127 | 6.9587 | 6.8284 | 6.9741 | 6.7185 | 56.9249 | 0.051232 |  | 62.069 | 100
19980527120000 | 1998-05-27 12:00 | 642.224 |  | 26.573 | 154.995 | 157.131 | 160.81 | 159.359 |  | 1502.293 | 1579.629 |  | 7.1267 | 7.0313 | 7.7834 | 7.4958 | 6.9648 | 6.8284 | 6.968 | 6.7102 | 56.9086 | 0.051218 |  | 62.069 | 100
19980527123000 | 1998-05-27 12:30 | 637.794 |  | 8.49 | 155.436 | 156.714 | 161.281 | 159.189 |  | 1494.876 | 1573.212 |  | 7.1548 | 7.0596 | 7.8279 | 7.5723 | 7.0039 | 6.8618 | 7.0122 | 6.7512 | 57.2437 | 0.051519 |  | 62.069 | 100
19980527130000 | 1998-05-27 13:00 | 639.891 |  | 13.275 | 155.322 | 157.379 | 161.29 | 159.854 |  | 1494.376 | 1571.545 |  | 7.1533 | 7.0283 | 7.8125 | 7.5325 | 6.9727 | 6.8459 | 6.9839 | 6.7307 | 57.0598 | 0.051354 |  | 62.069 | 100
19980527133000 | 1998-05-27 13:30 | 640.782 |  | 8.615 | 155.695 | 157.028 | 161.508 | 160.493 |  | 1496.626 | 1574.212 |  | 7.1335 | 7.0251 | 7.7813 | 7.5403 | 6.9641 | 6.8467 | 6.9878 | 6.7307 | 57.0095 | 0.051309 |  | 62.069 | 100
19980527140000 | 1998-05-27 14:00 | 637.61 |  | 11.555 | 155.926 | 157.962 | 161.863 | 160.685 |  | 1492.543 | 1574.295 |  | 7.1396 | 7.0427 | 7.8018 | 7.5493 | 6.9788 | 6.8474 | 6.9932 | 6.739 | 57.0918 | 0.051383 |  | 62.069 | 100
19980527143000 | 1998-05-27 14:30 | 641.254 |  | 5.341 | 156.264 | 157.092 | 162.204 | 159.815 |  | 1493.626 | 1571.045 |  | 7.1267 | 7.0352 | 7.792 | 7.5371 | 6.9656 | 6.8428 | 6.9878 | 6.7253 | 57.0125 | 0.051311 |  | 62.069 | 100
19980527150000 | 1998-05-27 15:00 | 631.24 |  | 11.796 | 156.412 | 156.235 | 162.392 | 159.206 |  | 1479.626 | 1559.211 |  | 7.1038 | 7.0068 | 7.7668 | 7.4998 | 6.9404 | 6.8201 | 6.9656 | 6.7092 | 56.8125 | 0.051131 |  | 62.069 | 100
19980527153000 | 1998-05-27 15:30 | 626.6 |  | 9.345 | 156.321 | 157.576 | 162.372 | 160.299 |  | 1476.709 | 1549.878 |  | 7.0251 | 6.9314 | 7.6775 | 7.3989 | 6.8635 | 6.7544 | 6.894 | 6.6345 | 56.1793 | 0.050561 |  | 62.069 | 100
19980527160000 | 1998-05-27 16:00 | 628.75 |  | 11.432 | 156.411 | 157.148 | 162.291 | 159.871 |  | 1473.542 | 1546.461 |  | 7.0007 | 6.9131 | 7.6318 | 7.3938 | 6.8413 | 6.7314 | 6.8726 | 6.6094 | 55.9941 | 0.050395 |  | 62.069 | 100
19980527163000 | 1998-05-27 16:30 | 626.312 |  | 9.842 | 156.788 | 158.607 | 162.658 | 161.083 |  | 1467.292 | 1538.961 |  | 7.0039 | 6.9077 | 7.644 | 7.3701 | 6.8428 | 6.7429 | 6.874 | 6.6072 | 55.9926 | 0.050393 |  | 62.069 | 100
19980527170000 | 1998-05-27 17:00 | 628.147 |  | 12.166 | 157.431 | 159.505 | 163.207 | 162.475 |  | 1465.375 | 1534.877 |  | 6.9856 | 6.8933 | 7.6143 | 7.3701 | 6.8269 | 6.7275 | 6.8704 | 6.604 | 55.8921 | 0.050303 |  | 62.069 | 100
19980527173000 | 1998-05-27 17:30 | 629.012 |  | 9.471 | 157.889 | 159.453 | 163.568 | 162.424 |  | 1468.042 | 1539.878 |  | 6.9595 | 6.8657 | 7.6042 | 7.3188 | 6.8208 | 6.7139 | 6.8428 | 6.5759 | 55.7016 | 0.050131 |  | 62.069 | 100
19980527180000 | 1998-05-27 18:00 | 623.192 |  | 13.521 | 158.183 | 159.598 | 163.955 | 162.568 |  | 1467.292 | 1540.711 |  | 6.9727 | 6.8711 | 7.6064 | 7.3464 | 6.8237 | 6.7192 | 6.8582 | 6.5911 | 55.7888 | 0.05021 |  | 62.069 | 100
19980527183000 | 1998-05-27 18:30 | 612.444 |  | 10.449 | 157.993 | 158.582 | 163.738 | 161.057 |  | 1441.625 | 1511.21 |  | 6.8413 | 6.7712 | 7.4502 | 7.2068 | 6.6987 | 6.623 | 6.7529 | 6.4858 | 54.8299 | 0.049347 |  | 62.069 | 100
19980527190000 | 1998-05-27 19:00 | 607.726 |  | 14.15 | 157.09 | 158.437 | 162.766 | 160.418 |  | 1444.042 | 1509.46 |  | 6.8618 | 6.7727 | 7.4707 | 7.2312 | 6.7078 | 6.6201 | 6.7605 | 6.4844 | 54.9092 | 0.049418 |  | 62.069 | 100
19980527193000 | 1998-05-27 19:30 | 602.981 |  | 9.843 | 157.449 | 161.149 | 163.134 | 164.12 |  | 1467.625 | 1541.544 |  | 6.8467 | 6.7886 | 7.457 | 7.2305 | 6.6934 | 6.6201 | 6.7581 | 6.4934 | 54.8878 | 0.049399 |  | 62.069 | 100
19980527200000 | 1998-05-27 20:00 | 603.505 |  | 12.42 | 159.765 | 161.707 | 165.449 | 163.687 |  | 1467.625 | 1537.461 |  | 6.8506 | 6.7642 | 7.4524 | 7.2305 | 6.6948 | 6.6194 | 6.7581 | 6.4844 | 54.8544 | 0.049369 |  | 62.069 | 100
19980527203000 | 1998-05-27 20:30 | 604.292 |  | 9.35 | 159.392 | 159.886 | 164.985 | 162.114 |  | 1467.792 | 1536.627 |  | 6.8489 | 6.7458 | 7.457 | 7.187 | 6.7009 | 6.6079 | 6.7368 | 6.4722 | 54.7565 | 0.049281 |  | 62.069 | 100
19980527210000 | 1998-05-27 21:00 | 600.517 |  | 12.41 | 158.384 | 159.701 | 163.946 | 161.681 |  | 1467.542 | 1536.211 |  | 6.8665 | 6.7673 | 7.4714 | 7.2319 | 6.7285 | 6.6277 | 6.7659 | 6.4819 | 54.9411 | 0.049447 |  | 62.069 | 100
19980527213000 | 1998-05-27 21:30 | 603.977 |  | 7.88 | 157.37 | 158.138 | 163.144 | 160.366 |  | 1465.375 | 1532.627 |  | 6.8733 | 6.7651 | 7.4976 | 7.2434 | 6.73 | 6.6323 | 6.7581 | 6.4934 | 54.9932 | 0.049494 |  | 62.069 | 100
19980527220000 | 1998-05-27 22:00 | 622.537 |  | 13.894 | 155.265 | 154.322 | 161.135 | 157.045 |  | 1458.542 | 1522.71 |  | 6.9702 | 6.8506 | 7.6064 | 7.3228 | 6.8208 | 6.7024 | 6.8323 | 6.5681 | 55.6736 | 0.050106 |  | 62.069 | 100
19980527223000 | 1998-05-27 22:30 | 621.567 |  | 10.209 | 153.63 | 155.142 | 159.552 | 158.607 |  | 1453.208 | 1518.96 |  | 6.9839 | 6.8406 | 7.6157 | 7.312 | 6.8208 | 6.6841 | 6.8154 | 6.5627 | 55.6352 | 0.050072 |  | 62.069 | 100
19980527230000 | 1998-05-27 23:00 | 627.124 |  | 12.785 | 154.42 | 156.679 | 160.067 | 159.402 |  | 1467.292 | 1539.044 |  | 7.0344 | 6.9275 | 7.6531 | 7.425 | 6.8833 | 6.7681 | 6.9023 | 6.6421 | 56.2358 | 0.050612 |  | 62.069 | 100
19980527233000 | 1998-05-27 23:30 | 623.559 |  | 9.963 | 155.331 | 156.679 | 160.89 | 159.402 |  | 1451.042 | 1528.127 |  | 6.9199 | 6.8169 | 7.5454 | 7.3022 | 6.7681 | 6.6384 | 6.7849 | 6.5278 | 55.3036 | 0.049773 |  | 62.069 | 100
19980528000000 | 1998-05-28 | 526.042 |  | 9.107 | 154.099 | 150.83 | 159.871 | 153.801 |  | 1278.62 | 1314.704 |  | 6.0303 | 5.8801 | 6.4529 | 6.0938 | 5.928 | 5.835 | 5.948 | 5.6716 | 47.8397 | 0.043056 |  | 62.069 | 100
19980528003000 | 1998-05-28 00:30 | 521.533 |  | 3.032 | 149.934 | 152.393 | 155.948 | 152.641 |  | 1247.953 | 1282.453 |  | 5.9724 | 5.835 | 6.3599 | 6.0273 | 5.8647 | 5.8076 | 5.9333 | 5.6228 | 47.423 | 0.042681 |  | 62.069 | 100
19980528010000 | 1998-05-28 01:00 | 495.686 |  | 6.779 | 150.594 | 149.526 | 154.702 | 151.754 |  | 1166.783 | 1186.201 |  | 5.6238 | 5.4163 | 5.9189 | 5.5269 | 5.5032 | 5.4192 | 5.5291 | 5.2361 | 44.1735 | 0.039756 |  | 62.069 | 100
19980528013000 | 1998-05-28 01:30 | 421.395 |  | 1.759 | 148.933 | 147.886 | 152.681 | 146.896 |  | 1045.03 | 1025.779 |  | 5.0659 | 4.8792 | 5.2314 | 4.821 | 4.9783 | 5.0422 | 5.1362 | 3.2533 | 38.4075 | 0.034567 |  | 62.069 | 100
19980528020000 | 1998-05-28 02:00 | 342.306 |  | 1.762 | 148.429 | 146.22 | 148.678 | 140.775 |  | 882.192 | 781.772 |  | 4.741 | 0.0063 | 4.8066 | 4.9714 | 4.6609 | 4.8096 | 4.8936 | 2.9573 | 31.8467 | 0.028662 |  | 62.069 | 100
19980528023000 | 1998-05-28 02:30 | 350.826 |  | 1.516 | 147.73 | 149.933 | 144.867 | 145.972 |  | 887.442 | 796.106 |  | 4.6716 | 0.0078 | 4.7273 | 4.8867 | 4.5808 | 4.7205 | 4.8103 | 2.8986 | 31.3036 | 0.028173 |  | 62.069 | 100
19980528030000 | 1998-05-28 03:00 | 341.598 |  | 1.145 | 150.238 | 150.634 | 148.097 | 148.407 |  | 874.692 | 776.272 |  | 4.7195 | 0.007 | 4.8181 | 4.9661 | 4.634 | 4.7791 | 4.8669 | 2.9352 | 31.7259 | 0.028553 |  | 62.069 | 100
19980528033000 | 1998-05-28 03:30 | 349.384 |  | 1.028 | 150.252 | 150.062 | 148.908 | 145.607 |  | 895.942 | 810.19 |  | 4.7683 | 0.0078 | 4.8555 | 5.0117 | 4.6685 | 4.7668 | 4.8813 | 2.9535 | 31.9134 | 0.028722 |  | 62.069 | 100
19980528040000 | 1998-05-28 04:00 | 341.231 |  | 1.519 | 150.583 | 150.815 | 148.607 | 148.34 |  | 898.526 | 807.607 |  | 4.8042 | 0.0078 | 4.8943 | 5.0896 | 4.7173 | 4.8271 | 4.9363 | 2.9932 | 32.2698 | 0.029043 |  | 62.069 | 100
19980528043000 | 1998-05-28 04:30 | 339.711 |  | 0.41 | 150.341 | 150.346 | 148.733 | 145.891 |  | 880.359 | 780.522 |  | 4.7349 | 0.007 | 4.8408 | 5.0623 | 4.6577 | 4.76 | 4.895 | 2.9749 | 31.9326 | 0.028739 |  | 62.069 | 100
19980528050000 | 1998-05-28 05:00 | 347.47 |  | 0.535 | 150.061 | 150.305 | 148.034 | 148.078 |  | 874.692 | 772.356 |  | 4.7378 | 0.007 | 4.8096 | 4.9683 | 4.6265 | 4.6516 | 4.8164 | 2.9207 | 31.5379 | 0.028384 |  | 62.069 | 100
19980528053000 | 1998-05-28 05:30 | 473.954 |  | 2.007 | 150.864 | 154.436 | 149.382 | 151.713 |  | 1160.033 | 1183.451 |  | 6.6033 | 0.0101 | 7.1892 | 6.9666 | 6.5063 | 6.498 | 6.6201 | 4.2434 | 44.637 | 0.040173 |  | 62.069 | 100
19980528060000 | 1998-05-28 06:00 | 541.64 |  | 10.33 | 153.355 | 153.708 | 151.501 | 149.253 |  | 1311.704 | 1368.789 |  | 6.4712 | 6.479 | 6.9619 | 6.7131 | 6.3301 | 6.2981 | 6.4294 | 4.1123 | 49.7951 | 0.044816 |  | 62.069 | 100
19980528063000 | 1998-05-28 06:30 | 616.691 |  | 7.634 | 153.499 | 153.919 | 153.142 | 156.642 |  | 1462.375 | 1540.211 |  | 7.2937 | 7.3145 | 7.9858 | 7.7507 | 7.1267 | 7.0366 | 7.1824 | 4.6265 | 56.3169 | 0.050685 |  | 62.069 | 100
19980528070000 | 1998-05-28 07:00 | 627.911 |  | 20.117 | 153.415 | 155.493 | 157.889 | 158.216 |  | 1468.292 | 1541.794 |  | 7.3411 | 7.3501 | 8.0503 | 7.7759 | 7.1985 | 7.0581 | 7.2144 | 4.6418 | 56.6302 | 0.050967 |  | 62.069 | 100
19980528073000 | 1998-05-28 07:30 | 633.18 |  | 8 | 153.589 | 155.962 | 159.241 | 159.18 |  | 1472.709 | 1543.544 |  | 7.3174 | 7.3608 | 8.0137 | 7.7813 | 7.1587 | 7.0649 | 7.1985 | 4.6516 | 56.5469 | 0.050892 |  | 62.069 | 100
19980528080000 | 1998-05-28 08:00 | 630.113 |  | 10.332 | 154.055 | 155.622 | 159.84 | 158.097 |  | 1470.209 | 1543.544 |  | 7.1084 | 7.0671 | 7.7676 | 7.4822 | 6.9634 | 6.7842 | 6.9863 | 6.6169 | 56.7761 | 0.051098 |  | 62.069 | 100
19980528083000 | 1998-05-28 08:30 | 632.498 |  | 8.979 | 153.691 | 154.75 | 159.576 | 158.216 |  | 1496.96 | 1571.962 |  | 7.3572 | 7.3501 | 8.0557 | 7.8088 | 7.1938 | 7.0535 | 7.2144 | 4.7051 | 56.7386 | 0.051065 |  | 62.069 | 100
19980528090000 | 1998-05-28 09:00 | 639.34 |  | 10.573 | 153.961 | 155.766 | 159.985 | 159.232 |  | 1491.459 | 1564.212 |  | 7.4243 | 7.4211 | 8.123 | 7.8584 | 7.2563 | 7.0916 | 7.2656 | 4.6943 | 57.1346 | 0.051421 |  | 62.069 | 100
19980528093000 | 1998-05-28 09:30 | 637.636 |  | 8.122 | 154.367 | 156.313 | 160.532 | 159.531 |  | 1489.293 | 1564.628 |  | 7.4043 | 7.4143 | 8.126 | 7.8333 | 7.2625 | 7.0801 | 7.2542 | 4.6882 | 57.0629 | 0.051357 |  | 62.069 | 100
19980528100000 | 1998-05-28 10:00 | 635.959 |  | 12.296 | 154.836 | 157.159 | 160.969 | 160.624 |  | 1485.209 | 1558.961 |  | 7.3867 | 7.3975 | 8.1128 | 7.8333 | 7.2351 | 7.0657 | 7.2412 | 4.6829 | 56.9552 | 0.05126 |  | 62.069 | 100
19980528103000 | 1998-05-28 10:30 | 639.13 |  | 8.245 | 155.421 | 157.081 | 161.365 | 160.052 |  | 1487.293 | 1565.795 |  | 7.1313 | 7.1113 | 7.7751 | 7.4905 | 6.9778 | 6.791 | 6.9626 | 6.6682 | 56.9078 | 0.051217 |  | 62.069 | 100
19980528110000 | 1998-05-28 11:00 | 633.258 |  | 12.415 | 155.709 | 157.576 | 161.503 | 160.299 |  | 1483.876 | 1557.461 |  | 7.145 | 7.1252 | 7.8027 | 7.5112 | 6.9932 | 6.8062 | 6.9788 | 6.6941 | 57.0564 | 0.051351 |  | 62.069 | 100
19980528113000 | 1998-05-28 11:30 | 631.24 |  | 9.101 | 156.14 | 158.592 | 161.983 | 161.315 |  | 1486.459 | 1563.628 |  | 7.1504 | 7.1121 | 7.7881 | 7.5027 | 6.9795 | 6.8 | 6.9756 | 6.6812 | 56.9896 | 0.051291 |  | 62.069 | 100
19980528120000 | 1998-05-28 12:00 | 633.18 |  | 12.908 | 156.51 | 158.164 | 162.393 | 161.134 |  | 1488.126 | 1560.045 |  | 7.1228 | 7.103 | 7.76 | 7.4897 | 6.9771 | 6.7925 | 6.968 | 6.6704 | 56.8835 | 0.051195 |  | 62.069 | 100
19980528123000 | 1998-05-28 12:30 | 632.21 |  | 8.612 | 156.609 | 158.241 | 162.53 | 161.212 |  | 1485.376 | 1557.461 |  | 7.126 | 7.0815 | 7.7554 | 7.4792 | 6.9595 | 6.7742 | 6.9473 | 6.6536 | 56.7767 | 0.051099 |  | 62.069 | 100
19980528130000 | 1998-05-28 13:00 | 618.264 |  | 12.169 | 157.254 | 160.769 | 163.172 | 163.986 |  | 1477.209 | 1555.461 |  | 7.0571 | 7.0298 | 7.6929 | 7.4082 | 6.9092 | 6.7192 | 6.9009 | 6.604 | 56.3213 | 0.050689 |  | 62.069 | 100
19980528133000 | 1998-05-28 13:30 | 621.803 |  | 7.64 | 158.375 | 159.897 | 164.169 | 162.125 |  | 1484.376 | 1560.378 |  | 7.0603 | 7.0291 | 7.6882 | 7.3953 | 6.894 | 6.72 | 6.897 | 6.6094 | 56.2933 | 0.050664 |  | 62.069 | 100
19980528140000 | 1998-05-28 14:00 | 626.443 |  | 11.061 | 157.996 | 158.881 | 163.76 | 161.851 |  | 1487.293 | 1561.378 |  | 7.0442 | 7.019 | 7.6875 | 7.3982 | 6.8955 | 6.7292 | 6.897 | 6.614 | 56.2846 | 0.050656 |  | 62.069 | 100
19980528143000 | 1998-05-28 14:30 | 624.424 |  | 8.485 | 157.435 | 159.025 | 163.371 | 161.748 |  | 1492.126 | 1567.462 |  | 7.0313 | 7.0955 | 7.6614 | 7.3623 | 6.8689 | 6.6941 | 6.8679 | 6.5903 | 56.1717 | 0.050555 |  | 62.069 | 100
19980528150000 | 1998-05-28 15:00 | 623.402 |  | 6.701 | 157.429 | 157.447 | 163.38 | 159.923 |  | 1458.875 | 1527.877 |  | 6.9961 | 7.0564 | 7.6272 | 7.3174 | 6.8513 | 6.6758 | 6.8428 | 6.5515 | 55.9185 | 0.050327 |  | 62.069 | 100
19980528153000 | 1998-05-28 15:30 | 630.27 |  | 8.734 | 155.798 | 156.653 | 161.766 | 159.871 |  | 1479.292 | 1555.795 |  | 7.0703 | 7.126 | 7.699 | 7.3899 | 6.9177 | 6.7397 | 6.9238 | 6.6133 | 56.4797 | 0.050832 |  | 62.069 | 100
19980528160000 | 1998-05-28 16:00 | 632.603 |  | 12.036 | 155.889 | 157.122 | 161.804 | 159.845 |  | 1485.543 | 1562.128 |  | 7.1077 | 7.1748 | 7.7515 | 7.4355 | 6.9558 | 6.7842 | 6.9512 | 6.6438 | 56.8045 | 0.051124 |  | 62.069 | 100
19980528163000 | 1998-05-28 16:30 | 632.577 |  | 9.588 | 156.482 | 158.231 | 162.433 | 160.954 |  | 1489.293 | 1564.212 |  | 7.1274 | 7.1687 | 7.7783 | 7.4609 | 6.9771 | 6.7871 | 6.9849 | 6.6604 | 56.9448 | 0.05125 |  | 62.069 | 100
19980528170000 | 1998-05-28 17:00 | 632.184 |  | 12.653 | 156.847 | 158.633 | 162.822 | 161.109 |  | 1490.293 | 1566.045 |  | 7.0991 | 7.1426 | 7.7317 | 7.4304 | 6.9314 | 6.7659 | 6.9421 | 6.6338 | 56.677 | 0.051009 |  | 62.069 | 100
19980528173000 | 1998-05-28 17:30 | 634.779 |  | 9.593 | 156.866 | 158.035 | 162.884 | 161.005 |  | 1488.209 | 1563.628 |  | 7.0764 | 7.1199 | 7.698 | 7.3906 | 6.9153 | 6.7375 | 6.9207 | 6.6011 | 56.4595 | 0.050814 |  | 62.069 | 100
19980528180000 | 1998-05-28 18:00 | 632.053 |  | 14.149 | 156.819 | 158.426 | 162.784 | 161.397 |  | 1477.209 | 1552.211 |  | 7.0808 | 7.1069 | 7.7112 | 7.4136 | 6.9138 | 6.7354 | 6.9106 | 6.5986 | 56.4709 | 0.050824 |  | 62.069 | 100
19980528183000 | 1998-05-28 18:30 | 632.21 |  | 9.345 | 157.068 | 158.881 | 162.972 | 162.099 |  | 1480.126 | 1556.045 |  | 7.0962 | 7.1343 | 7.7461 | 7.4456 | 6.9368 | 6.7605 | 6.9321 | 6.6323 | 56.6839 | 0.051016 |  | 62.069 | 100
19980528190000 | 1998-05-28 19:00 | 632.446 |  | 14.646 | 157.238 | 158.726 | 163.288 | 162.686 |  | 1481.209 | 1557.795 |  | 7.0276 | 7.1343 | 7.657 | 7.4219 | 6.875 | 6.7476 | 6.8733 | 6.6162 | 56.3529 | 0.050718 |  | 62.069 | 100
19980528193000 | 1998-05-28 19:30 | 617.897 |  | 9.592 | 157.413 | 159.077 | 163.493 | 162.047 |  | 1453.792 | 1522.627 |  | 6.9436 | 7.0413 | 7.5547 | 7.2908 | 6.8 | 6.6719 | 6.8062 | 6.5308 | 55.6393 | 0.050075 |  | 62.069 | 100
19980528200000 | 1998-05-28 20:00 | 626.443 |  | 14.394 | 157.563 | 159.948 | 163.597 | 162.424 |  | 1475.292 | 1551.545 |  | 6.981 | 7.0657 | 7.5981 | 7.3083 | 6.8276 | 6.697 | 6.8398 | 6.5605 | 55.878 | 0.05029 |  | 62.069 | 100
19980528203000 | 1998-05-28 20:30 | 628.12 |  | 10.454 | 158.206 | 159.453 | 164.18 | 162.671 |  | 1482.709 | 1555.295 |  | 7 | 7.0938 | 7.6064 | 7.3806 | 6.8391 | 6.7207 | 6.8557 | 6.5789 | 56.0752 | 0.050468 |  | 62.069 | 100
19980528210000 | 1998-05-28 21:00 | 623.926 |  | 15.138 | 157.732 | 159.272 | 163.762 | 162.738 |  | 1486.876 | 1562.545 |  | 7.0366 | 7.1182 | 7.6624 | 7.3938 | 6.8711 | 6.7422 | 6.8833 | 6.6025 | 56.3101 | 0.050679 |  | 62.069 | 100
19980528213000 | 1998-05-28 21:30 | 622.563 |  | 21.464 | 157.278 | 158.36 | 163.331 | 163.311 |  | 1481.292 | 1553.961 |  | 7.0076 | 7.1091 | 7.6257 | 7.3938 | 6.8513 | 6.7314 | 6.8711 | 6.5957 | 56.1857 | 0.050567 |  | 62.069 | 100
19980528220000 | 1998-05-28 22:00 | 620.125 |  | 15.012 | 156.694 | 157.643 | 162.709 | 160.366 |  | 1483.126 | 1557.628 |  | 7.0283 | 7.1199 | 7.6455 | 7.4021 | 6.8726 | 6.7512 | 6.8862 | 6.6033 | 56.3091 | 0.050678 |  | 62.069 | 100
19980528223000 | 1998-05-28 22:30 | 614.096 |  | 10.208 | 156.251 | 157.421 | 162.108 | 159.897 |  | 1475.709 | 1551.878 |  | 7.0305 | 7.126 | 7.6523 | 7.415 | 6.8711 | 6.7573 | 6.8962 | 6.6208 | 56.3692 | 0.050732 |  | 62.069 | 100
19980528230000 | 1998-05-28 23:00 | 619.444 |  | 12.042 | 155.649 | 156.276 | 161.39 | 158.999 |  | 1487.459 | 1560.628 |  | 7.0244 | 7.1243 | 7.6523 | 7.4233 | 6.8618 | 6.7529 | 6.8818 | 6.6162 | 56.337 | 0.050703 |  | 62.069 | 100
19980528233000 | 1998-05-28 23:30 | 618.867 |  | 9.596 | 155.17 | 155.988 | 160.755 | 158.463 |  | 1481.709 | 1554.878 |  | 7.0588 | 7.1519 | 7.6814 | 7.4502 | 6.8977 | 6.7703 | 6.9153 | 6.6492 | 56.5748 | 0.050917 |  | 62.069 | 100
19980529000000 | 1998-05-29 | 605.366 |  | 12.412 | 154.548 | 155.884 | 160.106 | 158.112 |  | 1421.208 | 1489.793 |  | 6.8008 | 6.8618 | 7.3784 | 7.1045 | 6.6208 | 6.4805 | 6.6187 | 6.3911 | 54.2566 | 0.048831 |  | 62.069 | 100
19980529003000 | 1998-05-29 00:30 | 532.936 |  | 5.313 | 152.424 | 147.716 | 158.029 | 151.676 |  | 1272.786 | 1312.454 |  | 6.1462 | 6.2363 | 6.5469 | 6.2607 | 6.0205 | 5.928 | 6.0493 | 5.7747 | 48.9626 | 0.044066 |  | 62.069 | 100
19980529010000 | 1998-05-29 01:00 | 531.39 |  | 8.617 | 149.301 | 150.062 | 153.235 | 149.814 |  | 1264.036 | 1304.871 |  | 6.125 | 6.2141 | 6.5193 | 6.2256 | 6.0029 | 5.9395 | 6.0518 | 5.7556 | 48.8338 | 0.04395 |  | 62.069 | 100
19980529013000 | 1998-05-29 01:30 | 525.282 |  | 6.537 | 150.856 | 152.873 | 152.925 | 153.616 |  | 1313.121 | 1361.622 |  | 6.189 | 6.2913 | 6.6338 | 6.3508 | 6.054 | 5.99 | 6.1243 | 5.8242 | 49.4574 | 0.044512 |  | 62.069 | 100
19980529020000 | 1998-05-29 02:00 | 530.394 |  | 11.563 | 151.278 | 151.207 | 155.505 | 153.682 |  | 1238.452 | 1280.37 |  | 6.0647 | 6.092 | 6.4385 | 6.073 | 5.8967 | 5.8008 | 5.9373 | 5.6604 | 47.9634 | 0.043167 |  | 62.069 | 100
19980529023000 | 1998-05-29 02:30 | 478.961 |  | 2.866 | 149.473 | 149.696 | 153.996 | 150.686 |  | 1151.366 | 1173.867 |  | 5.5786 | 5.6375 | 5.835 | 5.5085 | 5.4414 | 5.4353 | 5.5505 | 5.2278 | 44.2146 | 0.039793 |  | 62.069 | 100
19980529030000 | 1998-05-29 03:00 | 472.591 |  | 5.798 | 149.495 | 150.505 | 151.292 | 148.03 |  | 1143.283 | 1154.616 |  | 5.5146 | 5.6299 | 5.7998 | 5.4856 | 5.3909 | 5.4177 | 5.5269 | 5.1926 | 43.958 | 0.039562 |  | 62.069 | 100
19980529033000 | 1998-05-29 03:30 | 476.681 |  | 2.5 | 149.749 | 147.468 | 149.2 | 142.271 |  | 1134.116 | 1136.283 |  | 5.5093 | 5.6077 | 5.7671 | 5.4536 | 5.3955 | 5.4199 | 5.5269 | 5.1675 | 43.8475 | 0.039463 |  | 62.069 | 100
19980529040000 | 1998-05-29 04:00 | 477.65 |  | 5.433 | 149.085 | 151.676 | 145.606 | 146.973 |  | 1116.949 | 1116.949 |  | 3.8278 | 5.7771 | 5.9883 | 5.6809 | 5.5771 | 5.5833 | 5.7053 | 5.342 | 43.4818 | 0.039134 |  | 62.069 | 100
19980529043000 | 1998-05-29 04:30 | 453.795 |  | 2.132 | 150.631 | 149.19 | 148.356 | 147.21 |  | 1051.03 | 1050.53 |  | 4.8433 | 5.2292 | 5.2986 | 4.9172 | 5.0034 | 5.0073 | 5.1301 | 4.7988 | 40.2279 | 0.036205 |  | 62.069 | 100
19980529050000 | 1998-05-29 05:00 | 420.425 |  | 2.621 | 149.492 | 151.769 | 148.167 | 147.561 |  | 1038.946 | 1017.613 |  | 4.8767 | 5.0522 | 5.0957 | 4.7654 | 4.8538 | 4.9514 | 5.0508 | 4.6448 | 39.2908 | 0.035362 |  | 62.069 | 100
19980529053000 | 1998-05-29 05:30 | 371.194 |  | 20.578 | 150.507 | 148.643 | 148.801 | 144.931 |  | 976.028 | 926.277 |  | 1.7358 | 3.5447 | 5.4795 | 5.1599 | 5.1858 | 5.2827 | 5.3604 | 4.9561 | 36.7049 | 0.033034 |  | 62.069 | 100
19980529060000 | 1998-05-29 06:00 | 385.848 |  | 2.131 | 149.532 | 150.819 | 147.53 | 147.107 |  | 971.695 | 919.86 |  | 1.6656 | 3.4143 | 5.2476 | 4.9058 | 4.9958 | 5.1072 | 5.198 | 4.7837 | 35.318 | 0.031786 |  | 62.069 | 100
19980529063000 | 1998-05-29 06:30 | 513.774 |  | 2.868 | 151.122 | 155.652 | 149.134 | 151.444 |  | 1283.62 | 1340.205 |  | 2.6078 | 6.6743 | 7.0754 | 6.8162 | 6.4224 | 6.4011 | 6.5347 | 6.1843 | 48.7162 | 0.043845 |  | 62.069 | 100
19980529070000 | 1998-05-29 07:00 | 604.239 |  | 11.186 | 154.014 | 152.341 | 153.371 | 153.579 |  | 1414.374 | 1480.792 |  | 6.7476 | 6.9734 | 7.4617 | 7.219 | 6.7146 | 6.6658 | 6.7947 | 6.4629 | 55.0397 | 0.049536 |  | 62.069 | 100
19980529073000 | 1998-05-29 07:30 | 625.84 |  | 8.247 | 150.874 | 153.213 | 154.596 | 153.708 |  | 1473.209 | 1549.294 |  | 6.9429 | 7.1511 | 7.6821 | 7.425 | 6.8779 | 6.7932 | 6.9368 | 6.6316 | 56.4406 | 0.050797 |  | 62.069 | 100
19980529080000 | 1998-05-29 08:00 | 630.27 |  | 10.329 | 150.912 | 152.053 | 155.63 | 154.776 |  | 1485.209 | 1561.545 |  | 7.0229 | 7.2205 | 7.7668 | 7.5281 | 6.9558 | 6.8582 | 6.9954 | 6.7002 | 57.0479 | 0.051343 |  | 62.069 | 100
19980529083000 | 1998-05-29 08:30 | 636.981 |  | 7.513 | 150.998 | 152.145 | 156.758 | 155.859 |  | 1490.293 | 1566.545 |  | 7.0237 | 7.229 | 7.7676 | 7.5378 | 6.9551 | 6.8528 | 6.9993 | 6.7092 | 57.0745 | 0.051367 |  | 62.069 | 100
19980529090000 | 1998-05-29 09:00 | 630.427 |  | 9.889 | 150.958 | 151.181 | 157.135 | 156.132 |  | 1487.126 | 1560.045 |  | 7.0076 | 7.229 | 7.7432 | 7.5173 | 6.9512 | 6.855 | 6.9939 | 6.7102 | 57.0074 | 0.051307 |  | 62.069 | 100
19980529093000 | 1998-05-29 09:30 | 630.925 |  | 7.023 | 150.83 | 152.899 | 157.168 | 156.364 |  | 1480.376 | 1553.211 |  | 6.99 | 7.1946 | 7.7339 | 7.5088 | 6.9282 | 6.8201 | 6.958 | 6.6787 | 56.8123 | 0.051131 |  | 62.069 | 100
19980529100000 | 1998-05-29 10:00 | 632.262 |  | 10.444 | 151.607 | 153.564 | 157.992 | 157.03 |  | 1481.126 | 1555.045 |  | 6.9961 | 7.2014 | 7.7454 | 7.5027 | 6.9329 | 6.8101 | 6.9473 | 6.6711 | 56.807 | 0.051126 |  | 62.069 | 100
19980529103000 | 1998-05-29 10:30 | 630.349 |  | 7.512 | 152.343 | 153.956 | 158.798 | 158.907 |  | 1487.876 | 1563.045 |  | 7.0496 | 7.2473 | 7.8071 | 7.5525 | 6.9885 | 6.8467 | 6.9893 | 6.7231 | 57.2041 | 0.051484 |  | 62.069 | 100
19980529110000 | 1998-05-29 11:00 | 627.753 |  | 9.588 | 152.848 | 154.255 | 159.385 | 158.463 |  | 1479.292 | 1553.295 |  | 6.9824 | 7.1992 | 7.74 | 7.4951 | 6.9314 | 6.8208 | 6.9551 | 6.6826 | 56.8066 | 0.051126 |  | 62.069 | 100
19980529113000 | 1998-05-29 11:30 | 636.063 |  | 7.507 | 153.352 | 154.724 | 159.877 | 158.437 |  | 1487.043 | 1560.961 |  | 7.0442 | 7.229 | 7.7974 | 7.5464 | 6.9795 | 6.8445 | 6.9849 | 6.7139 | 57.1398 | 0.051426 |  | 62.069 | 100
19980529120000 | 1998-05-29 12:00 | 636.509 |  | 11.055 | 153.807 | 155.91 | 160.327 | 158.633 |  | 1496.293 | 1573.962 |  | 7.0276 | 7.2244 | 7.7981 | 7.5234 | 6.9817 | 6.8474 | 6.9932 | 6.7031 | 57.0989 | 0.051389 |  | 62.069 | 100
19980529123000 | 1998-05-29 12:30 | 624.844 |  | 6.159 | 154.537 | 155.859 | 161.068 | 159.077 |  | 1483.709 | 1557.878 |  | 6.9749 | 7.167 | 7.698 | 7.46 | 6.9124 | 6.7896 | 6.9299 | 6.6514 | 56.5832 | 0.050925 |  | 62.069 | 100
19980529130000 | 1998-05-29 13:00 | 626.626 |  | 9.582 | 154.943 | 155.781 | 161.543 | 160.484 |  | 1489.543 | 1564.378 |  | 6.9871 | 7.1985 | 7.7485 | 7.4897 | 6.9351 | 6.8115 | 6.9512 | 6.6797 | 56.8013 | 0.051121 |  | 62.069 | 100
19980529133000 | 1998-05-29 13:30 | 626.469 |  | 6.28 | 155.309 | 157.019 | 161.982 | 160.237 |  | 1477.709 | 1550.461 |  | 6.9368 | 7.135 | 7.6775 | 7.4265 | 6.8801 | 6.7659 | 6.9077 | 6.6208 | 56.3503 | 0.050715 |  | 62.069 | 100
19980529140000 | 1998-05-29 14:00 | 628.225 |  | 26.674 | 155.434 | 157.23 | 162.165 | 160.695 |  | 1478.542 | 1549.461 |  | 6.9131 | 7.1174 | 7.6401 | 7.3867 | 6.8643 | 6.7451 | 6.8848 | 6.5994 | 56.1509 | 0.050536 |  | 62.069 | 100
19980529143000 | 1998-05-29 14:30 | 627.439 |  | 6.399 | 155.787 | 157.514 | 162.573 | 160.979 |  | 1485.459 | 1560.628 |  | 6.958 | 7.1411 | 7.6868 | 7.4463 | 6.9001 | 6.7749 | 6.9221 | 6.6353 | 56.4646 | 0.050818 |  | 62.069 | 100
19980529150000 | 1998-05-29 15:00 | 627.596 |  | 9.582 | 156.296 | 157.957 | 163.124 | 161.918 |  | 1485.543 | 1557.711 |  | 6.9458 | 7.1267 | 7.6775 | 7.4326 | 6.8916 | 6.7605 | 6.9001 | 6.6194 | 56.3542 | 0.050719 |  | 62.069 | 100
19980529153000 | 1998-05-29 15:30 | 626.259 |  | 7.384 | 156.614 | 158.256 | 163.399 | 161.722 |  | 1486.376 | 1560.545 |  | 6.9565 | 7.1375 | 7.7019 | 7.4272 | 6.8916 | 6.772 | 6.9199 | 6.6277 | 56.4343 | 0.050791 |  | 62.069 | 100
19980529160000 | 1998-05-29 16:00 | 627.439 |  | 9.708 | 156.965 | 158.153 | 163.765 | 162.114 |  | 1483.876 | 1560.795 |  | 6.9534 | 7.1389 | 7.6882 | 7.405 | 6.8894 | 6.7749 | 6.9214 | 6.6238 | 56.395 | 0.050755 |  | 62.069 | 100
19980529163000 | 1998-05-29 16:30 | 625.735 |  | 7.262 | 157.221 | 158.896 | 164.072 | 162.361 |  | 1486.793 | 1561.712 |  | 6.9612 | 7.1465 | 7.6919 | 7.4487 | 6.8984 | 6.7764 | 6.9084 | 6.6262 | 56.4577 | 0.050812 |  | 62.069 | 100
19980529170000 | 1998-05-29 17:00 | 626.731 |  | 9.83 | 157.413 | 158.818 | 164.237 | 162.036 |  | 1493.46 | 1565.128 |  | 6.9878 | 7.1663 | 7.7324 | 7.4539 | 6.9351 | 6.7971 | 6.9421 | 6.6543 | 56.669 | 0.051002 |  | 62.069 | 100
19980529173000 | 1998-05-29 17:30 | 624.844 |  | 7.383 | 157.793 | 159.287 | 164.644 | 162.505 |  | 1495.96 | 1568.962 |  | 6.991 | 7.1724 | 7.7302 | 7.46 | 6.9336 | 6.791 | 6.9482 | 6.6482 | 56.6746 | 0.051007 |  | 62.069 | 100
19980529180000 | 1998-05-29 18:00 | 628.225 |  | 10.438 | 158.136 | 160.03 | 165.077 | 163.496 |  | 1493.043 | 1567.462 |  | 6.9871 | 7.1641 | 7.7439 | 7.457 | 6.9238 | 6.7993 | 6.9451 | 6.6514 | 56.6717 | 0.051005 |  | 62.069 | 100
19980529183000 | 1998-05-29 18:30 | 620.859 |  | 22.058 | 158.516 | 160.211 | 165.427 | 164.172 |  | 1496.876 | 1568.378 |  | 6.9299 | 7.1313 | 7.6699 | 7.415 | 6.8733 | 6.7529 | 6.9038 | 6.6072 | 56.2833 | 0.050655 |  | 62.069 | 100
19980529190000 | 1998-05-29 19:00 | 614.908 |  | 10.444 | 158.946 | 160.082 | 165.966 | 163.547 |  | 1473.876 | 1547.544 |  | 6.8521 | 7.0344 | 7.5806 | 7.2998 | 6.7939 | 6.6865 | 6.823 | 6.5376 | 55.6079 | 0.050047 |  | 62.069 | 100
19980529193000 | 1998-05-29 19:30 | 615.983 |  | 6.407 | 158.455 | 159.716 | 165.451 | 162.934 |  | 1478.959 | 1546.211 |  | 6.8345 | 7.01 | 7.5432 | 7.2717 | 6.7825 | 6.6614 | 6.7947 | 6.5042 | 55.4022 | 0.049862 |  | 62.069 | 100
19980529200000 | 1998-05-29 20:00 | 613.886 |  | 8.605 | 157.91 | 158.726 | 164.837 | 162.191 |  | 1476.959 | 1548.044 |  | 6.8923 | 7.0459 | 7.6111 | 7.3289 | 6.8391 | 6.7085 | 6.8428 | 6.54 | 55.8086 | 0.050228 |  | 62.069 | 100
19980529203000 | 1998-05-29 20:30 | 614.83 |  | 5.919 | 157.217 | 158.061 | 164.149 | 161.774 |  | 1484.543 | 1553.211 |  | 6.8984 | 7.0625 | 7.6111 | 7.3281 | 6.8406 | 6.7041 | 6.8352 | 6.54 | 55.82 | 0.050238 |  | 62.069 | 100
19980529210000 | 1998-05-29 21:00 | 615.774 |  | 9.095 | 156.79 | 158.009 | 163.585 | 161.722 |  | 1478.542 | 1547.211 |  | 6.865 | 7.0496 | 7.5784 | 7.3425 | 6.8237 | 6.6956 | 6.833 | 6.5437 | 55.7315 | 0.050158 |  | 62.069 | 100
19980529213000 | 1998-05-29 21:30 | 614.096 |  | 6.157 | 156.5 | 157.54 | 163.169 | 160.758 |  | 1474.292 | 1543.128 |  | 6.8679 | 7.0618 | 7.5837 | 7.3335 | 6.8154 | 6.7024 | 6.8435 | 6.543 | 55.7512 | 0.050176 |  | 62.069 | 100
19980529220000 | 1998-05-29 22:00 | 623.559 |  | 9.462 | 156.189 | 157.54 | 161.949 | 158.53 |  | 1481.292 | 1555.461 |  | 6.9038 | 7.1121 | 7.6187 | 7.3792 | 6.8481 | 6.7368 | 6.8811 | 6.5896 | 56.0694 | 0.050462 |  | 62.069 | 100
19980529223000 | 1998-05-29 22:30 | 619.653 |  | 7.013 | 155.842 | 156.472 | 159.647 | 156.72 |  | 1460.125 | 1530.544 |  | 6.8611 | 7.0625 | 7.5837 | 7.3425 | 6.813 | 6.7063 | 6.8489 | 6.5591 | 55.7771 | 0.050199 |  | 62.069 | 100
19980529230000 | 1998-05-29 23:00 | 615.013 |  | 10.449 | 154.97 | 158.101 | 158.436 | 158.101 |  | 1486.459 | 1559.878 |  | 6.894 | 7.0657 | 7.6074 | 7.3257 | 6.8306 | 6.7131 | 6.8489 | 6.5552 | 55.8406 | 0.050257 |  | 62.069 | 100
19980529233000 | 1998-05-29 23:30 | 616.219 |  | 5.915 | 156.533 | 157.699 | 159.814 | 158.441 |  | 1485.459 | 1555.295 |  | 6.9268 | 7.093 | 7.6516 | 7.3921 | 6.8811 | 6.7444 | 6.8855 | 6.5872 | 56.1617 | 0.050546 |  | 62.069 | 100
19980530000000 | 1998-05-30 | 618.631 |  | 8.851 | 156.286 | 157.854 | 159.594 | 156.864 |  | 1491.043 | 1565.045 |  | 6.875 | 7.061 | 7.5974 | 7.345 | 6.8276 | 6.7017 | 6.8367 | 6.5469 | 55.7913 | 0.050212 |  | 62.069 | 100
19980530003000 | 1998-05-30 00:30 | 617.556 |  | 6.162 | 155.853 | 157.215 | 159.119 | 157.957 |  | 1493.71 | 1569.962 |  | 6.9099 | 7.0854 | 7.6431 | 7.3562 | 6.8618 | 6.7322 | 6.8643 | 6.5759 | 56.0288 | 0.050426 |  | 62.069 | 100
19980530010000 | 1998-05-30 01:00 | 577.081 |  | 7.872 | 155.46 | 153.672 | 158.601 | 153.919 |  | 1416.707 | 1476.792 |  | 6.5688 | 6.7346 | 7.2 | 6.9214 | 6.52 | 6.3936 | 6.5271 | 6.241 | 53.1065 | 0.047796 |  | 62.069 | 100
19980530013000 | 1998-05-30 01:30 | 525.832 |  | 3.711 | 150.383 | 146.637 | 153.496 | 147.875 |  | 1248.703 | 1280.87 |  | 5.9556 | 6.1318 | 5.6077 | 6.1538 | 5.9563 | 5.8533 | 5.989 | 5.6938 | 47.3413 | 0.042607 |  | 62.069 | 100
19980530020000 | 1998-05-30 02:00 | 528.532 |  | 5.546 | 149.039 | 150.557 | 150.283 | 146.844 |  | 1239.119 | 1267.453 |  | 6.218 | 6.4041 | 3.5516 | 6.5034 | 6.1707 | 6.1409 | 6.2249 | 5.9312 | 47.1448 | 0.04243 |  | 62.069 | 100
19980530023000 | 1998-05-30 02:30 | 471.988 |  | 1.267 | 149.504 | 149.463 | 148.41 | 144.018 |  | 1138.199 | 1141.033 |  | 5.5505 | 5.7122 | 4.9783 | 5.5771 | 5.5161 | 5.4932 | 5.5916 | 5.2964 | 43.7154 | 0.039344 |  | 62.069 | 100
19980530030000 | 1998-05-30 03:00 | 472.277 |  | 2.984 | 150.029 | 150.897 | 146.632 | 145.204 |  | 1128.949 | 1130.282 |  | 5.4666 | 5.645 | 4.9011 | 5.519 | 5.4397 | 5.4604 | 5.561 | 5.2285 | 43.2213 | 0.038899 |  | 62.069 | 100
19980530033000 | 1998-05-30 03:30 | 472.145 |  | 1.143 | 150.579 | 150.649 | 147.867 | 146.194 |  | 1134.033 | 1135.533 |  | 5.5229 | 5.6619 | 4.9568 | 5.5366 | 5.4863 | 5.4688 | 5.5764 | 5.2322 | 43.4419 | 0.039098 |  | 62.069 | 100
19980530040000 | 1998-05-30 04:00 | 472.014 |  | 2.986 | 150.583 | 150.505 | 148.94 | 146.792 |  | 1130.782 | 1130.866 |  | 5.5183 | 5.6655 | 4.9492 | 5.5535 | 5.468 | 5.4658 | 5.5635 | 5.2239 | 43.4077 | 0.039067 |  | 62.069 | 100
19980530043000 | 1998-05-30 04:30 | 471.228 |  | 21.188 | 150.746 | 151.392 | 149.156 | 146.689 |  | 1139.366 | 1146.366 |  | 5.5542 | 5.6863 | 5.0034 | 5.5969 | 5.5039 | 5.4841 | 5.5916 | 5.2476 | 43.668 | 0.039301 |  | 62.069 | 100
19980530050000 | 1998-05-30 05:00 | 471.359 |  | 2.622 | 150.516 | 150.062 | 148.835 | 146.102 |  | 1134.116 | 1139.699 |  | 5.5146 | 5.6763 | 4.9622 | 5.5657 | 5.4824 | 5.4924 | 5.5833 | 5.2422 | 43.5191 | 0.039167 |  | 62.069 | 100
19980530053000 | 1998-05-30 05:30 | 473.063 |  | 1.145 | 150.283 | 149.633 | 148.375 | 145.921 |  | 1139.116 | 1143.616 |  | 5.5527 | 5.6794 | 4.9927 | 5.5581 | 5.5115 | 5.4795 | 5.5854 | 5.24 | 43.5993 | 0.039239 |  | 62.069 | 100
19980530060000 | 1998-05-30 06:00 | 473.037 |  | 3.599 | 150.186 | 150.01 | 148.499 | 146.792 |  | 1126.866 | 1129.782 |  | 5.5146 | 5.6572 | 4.9417 | 5.5313 | 5.468 | 5.4619 | 5.5574 | 5.2163 | 43.3484 | 0.039014 |  | 62.069 | 100
19980530063000 | 1998-05-30 06:30 | 472.617 |  | 1.393 | 150.464 | 152.511 | 148.669 | 149.046 |  | 1147.116 | 1155.116 |  | 5.5024 | 5.6787 | 4.937 | 5.5886 | 5.4641 | 5.4634 | 5.5725 | 5.2393 | 43.446 | 0.039101 |  | 62.069 | 100
19980530070000 | 1998-05-30 07:00 | 474.741 |  | 3.474 | 151.167 | 150.66 | 149.601 | 146.947 |  | 1143.199 | 1146.95 |  | 5.4939 | 5.6619 | 4.9424 | 5.5391 | 5.4658 | 5.4565 | 5.5505 | 5.2163 | 43.3264 | 0.038994 |  | 62.069 | 100
19980530073000 | 1998-05-30 07:30 | 524.679 |  | 2.25 | 150.24 | 152.537 | 148.646 | 147.834 |  | 1265.37 | 1307.371 |  | 6.0852 | 6.2378 | 5.5649 | 6.3293 | 6.0012 | 5.9875 | 6.1067 | 5.7717 | 48.0843 | 0.043276 |  | 62.069 | 100
19980530080000 | 1998-05-30 08:00 | 529.764 |  | 3.599 | 151.671 | 151.078 | 150.717 | 150.583 |  | 1282.87 | 1323.621 |  | 6.1089 | 6.2974 | 5.5854 | 6.363 | 6.054 | 6.0234 | 6.1333 | 5.8213 | 48.3867 | 0.043548 |  | 62.069 | 100
19980530083000 | 1998-05-30 08:30 | 584.552 |  | 4.82 | 151.202 | 151.625 | 153.032 | 153.605 |  | 1371.039 | 1428.624 |  | 6.6553 | 6.8635 | 6.2026 | 7.1016 | 6.6086 | 6.5408 | 6.6614 | 6.3552 | 52.989 | 0.04769 |  | 62.069 | 100
19980530090000 | 1998-05-30 09:00 | 584.631 |  | 18.274 | 150.307 | 151.181 | 154.613 | 152.666 |  | 1375.956 | 1428.791 |  | 6.5383 | 6.7368 | 7.1418 | 6.9124 | 6.4927 | 6.4163 | 6.5354 | 6.2532 | 53.0269 | 0.047724 |  | 62.069 | 100
19980530093000 | 1998-05-30 09:30 | 585.181 |  | 3.591 | 150.567 | 150.908 | 154.6 | 153.383 |  | 1370.123 | 1421.208 |  | 6.459 | 6.688 | 7.1199 | 6.8887 | 6.4302 | 6.3782 | 6.5017 | 6.2051 | 52.6708 | 0.047404 |  | 62.069 | 100
19980530100000 | 1998-05-30 10:00 | 589.087 |  | 6.527 | 150.626 | 151.351 | 155.207 | 154.074 |  | 1396.873 | 1460.625 |  | 6.614 | 6.8276 | 7.3135 | 7.0359 | 6.5728 | 6.5071 | 6.6248 | 6.324 | 53.8197 | 0.048438 |  | 62.069 | 100
19980530103000 | 1998-05-30 10:30 | 614.07 |  | 4.451 | 151.103 | 153.187 | 156.894 | 156.9 |  | 1441.958 | 1508.877 |  | 6.8542 | 7.0459 | 7.6111 | 7.3364 | 6.7939 | 6.6987 | 6.8252 | 6.5332 | 55.6986 | 0.050129 |  | 62.069 | 100
19980530110000 | 1998-05-30 11:00 | 585.784 |  | 6.652 | 152.561 | 152.29 | 159.024 | 156.003 |  | 1329.288 | 1377.456 |  | 6.4041 | 6.5706 | 7.0007 | 6.665 | 6.3333 | 6.2012 | 6.3423 | 6.0798 | 51.597 | 0.046437 |  | 62.069 | 100
19980530113000 | 1998-05-30 11:30 | 572.363 |  | 3.593 | 150.651 | 150.583 | 157.171 | 154.048 |  | 1337.205 | 1382.79 |  | 6.3416 | 6.5652 | 6.9573 | 6.6772 | 6.3027 | 6.2417 | 6.3706 | 6.0791 | 51.5354 | 0.046382 |  | 62.069 | 100
19980530120000 | 1998-05-30 12:00 | 569.374 |  | 5.794 | 150.42 | 150.531 | 155.814 | 153.501 |  | 1342.289 | 1387.707 |  | 6.3638 | 6.5652 | 6.9788 | 6.7153 | 6.3247 | 6.2439 | 6.3706 | 6.0884 | 51.6507 | 0.046486 |  | 62.069 | 100
19980530123000 | 1998-05-30 12:30 | 533.566 |  | 2.37 | 149.671 | 149.216 | 154.533 | 150.454 |  | 1251.453 | 1278.787 |  | 5.9585 | 6.1448 | 6.4446 | 6.1355 | 5.9365 | 5.854 | 5.9678 | 5.668 | 48.1097 | 0.043299 |  | 62.069 | 100
19980530130000 | 1998-05-30 13:00 | 532.832 |  | 3.96 | 149.893 | 150.649 | 152.579 | 150.154 |  | 1244.869 | 1274.703 |  | 5.9387 | 6.1135 | 6.4263 | 6.1172 | 5.9082 | 5.8364 | 5.967 | 5.6482 | 47.9555 | 0.04316 |  | 62.069 | 100
19980530133000 | 1998-05-30 13:30 | 528.847 |  | 2.25 | 150.553 | 150.428 | 152.466 | 150.428 |  | 1246.869 | 1279.953 |  | 5.9463 | 6.1294 | 6.446 | 6.1531 | 5.9319 | 5.8586 | 5.9785 | 5.6587 | 48.1025 | 0.043292 |  | 62.069 | 100
19980530140000 | 1998-05-30 14:00 | 528.585 |  | 3.592 | 150.88 | 150.949 | 152.766 | 151.196 |  | 1241.536 | 1272.036 |  | 5.9585 | 6.1243 | 6.4529 | 6.1318 | 5.9333 | 5.8496 | 5.98 | 5.6543 | 48.0847 | 0.043276 |  | 62.069 | 100
19980530143000 | 1998-05-30 14:30 | 530.184 |  | 1.878 | 151.09 | 151.562 | 153.99 | 153.542 |  | 1260.703 | 1299.454 |  | 5.9602 | 6.1218 | 6.4668 | 6.1135 | 5.9319 | 5.8464 | 5.9792 | 5.6504 | 48.0702 | 0.043263 |  | 62.069 | 100
19980530150000 | 1998-05-30 15:00 | 530.027 |  | 3.594 | 150.702 | 150.479 | 155.904 | 154.44 |  | 1263.453 | 1298.287 |  | 5.99 | 6.1494 | 6.4705 | 6.1516 | 5.9563 | 5.8723 | 5.9976 | 5.6748 | 48.2625 | 0.043436 |  | 62.069 | 100
19980530153000 | 1998-05-30 15:30 | 526.094 |  | 1.999 | 150.261 | 150.624 | 155.952 | 153.346 |  | 1258.203 | 1291.537 |  | 5.9685 | 6.1355 | 6.4607 | 6.1326 | 5.9495 | 5.8687 | 5.9998 | 5.6672 | 48.1825 | 0.043364 |  | 62.069 | 100
19980530160000 | 1998-05-30 16:00 | 525.99 |  | 2.983 | 150.576 | 150.964 | 155.762 | 153.934 |  | 1265.62 | 1304.037 |  | 5.9761 | 6.134 | 6.479 | 6.1516 | 5.9434 | 5.8723 | 5.99 | 5.6572 | 48.2036 | 0.043383 |  | 62.069 | 100
19980530163000 | 1998-05-30 16:30 | 526.016 |  | 2.493 | 150.292 | 149.633 | 156.116 | 153.594 |  | 1262.62 | 1296.704 |  | 5.9678 | 6.1416 | 6.4485 | 6.1433 | 5.9495 | 5.8708 | 6.0012 | 5.658 | 48.1807 | 0.043363 |  | 62.069 | 100
19980530170000 | 1998-05-30 17:00 | 579.441 |  | 7.385 | 150.899 | 155.146 | 156.13 | 157.621 |  | 1368.623 | 1421.874 |  | 6.4651 | 6.6743 | 7.126 | 6.855 | 6.4187 | 6.3591 | 6.4873 | 6.1738 | 52.5593 | 0.047303 |  | 62.069 | 100
19980530173000 | 1998-05-30 17:30 | 606.179 |  | 4.7 | 153.568 | 157.023 | 159.387 | 160.241 |  | 1473.376 | 1549.794 |  | 6.8574 | 7.0771 | 7.6211 | 7.3906 | 6.8154 | 6.7551 | 6.8909 | 6.5627 | 55.9703 | 0.050373 |  | 62.069 | 100
19980530180000 | 1998-05-30 18:00 | 618.29 |  | 8.363 | 156.166 | 159.978 | 162.428 | 162.949 |  | 1490.626 | 1564.795 |  | 6.894 | 7.1243 | 7.6516 | 7.4233 | 6.8467 | 6.7712 | 6.9124 | 6.6079 | 56.2314 | 0.050608 |  | 62.069 | 100
19980530183000 | 1998-05-30 18:30 | 611.029 |  | 4.451 | 157.927 | 160.433 | 164.214 | 160.68 |  | 1431.708 | 1504.043 |  | 6.6758 | 6.8628 | 7.3677 | 7.093 | 6.6162 | 6.4966 | 6.6345 | 6.3652 | 54.1118 | 0.048701 |  | 62.069 | 100
19980530190000 | 1998-05-30 19:00 | 585.024 |  | 24.846 | 155.187 | 152.826 | 159.009 | 152.826 |  | 1364.539 | 1416.874 |  | 6.4851 | 6.6682 | 7.1138 | 6.8047 | 6.4324 | 6.3271 | 6.4583 | 6.1685 | 52.4581 | 0.047212 |  | 62.069 | 100
19980530193000 | 1998-05-30 19:30 | 529.03 |  | 2.985 | 151.538 | 148.824 | 155.273 | 151.795 |  | 1249.369 | 1279.037 |  | 5.9731 | 6.1487 | 6.4805 | 6.144 | 5.9412 | 5.8579 | 5.99 | 5.6709 | 48.2063 | 0.043386 |  | 62.069 | 100
19980530200000 | 1998-05-30 20:00 | 526.802 |  | 4.083 | 150.078 | 150.258 | 153.643 | 150.505 |  | 1242.452 | 1271.786 |  | 5.9373 | 6.1233 | 6.4248 | 6.1096 | 5.9121 | 5.8503 | 5.9724 | 5.6526 | 47.9824 | 0.043184 |  | 62.069 | 100
19980530203000 | 1998-05-30 20:30 | 528.847 |  | 2.006 | 149.541 | 149.489 | 153.045 | 150.974 |  | 1228.785 | 1253.286 |  | 5.9333 | 6.1082 | 6.4233 | 6.106 | 5.8984 | 5.845 | 5.9656 | 5.6367 | 47.9165 | 0.043125 |  | 62.069 | 100
19980530210000 | 1998-05-30 21:00 | 531.783 |  | 3.721 | 149.191 | 149.515 | 153.039 | 150.505 |  | 1236.952 | 1263.12 |  | 5.9175 | 6.092 | 6.3965 | 6.0938 | 5.8984 | 5.8281 | 5.948 | 5.6313 | 47.8056 | 0.043025 |  | 62.069 | 100
19980530213000 | 1998-05-30 21:30 | 472.617 |  | 1.514 | 148.562 | 147.86 | 152.374 | 148.603 |  | 1138.533 | 1139.283 |  | 5.3757 | 5.5269 | 5.71 | 5.3848 | 5.3574 | 5.333 | 5.4482 | 5.0989 | 43.2349 | 0.038911 |  | 62.069 | 100
19980530220000 | 1998-05-30 22:00 | 469.55 |  | 2.621 | 148.245 | 149.268 | 150.479 | 147.783 |  | 1127.449 | 1123.282 |  | 5.3879 | 5.5168 | 5.7351 | 5.3779 | 5.3689 | 5.3215 | 5.4397 | 5.0928 | 43.2406 | 0.038917 |  | 62.069 | 100
19980530223000 | 1998-05-30 22:30 | 469.262 |  | 1.148 | 149.106 | 149.242 | 149.573 | 146.767 |  | 1128.866 | 1126.366 |  | 5.3948 | 5.5405 | 5.7466 | 5.4055 | 5.384 | 5.342 | 5.4565 | 5.1057 | 43.3756 | 0.039038 |  | 62.069 | 100
19980530230000 | 1998-05-30 23:00 | 474.269 |  | 2.622 | 149.191 | 149.098 | 149.182 | 146.375 |  | 1119.365 | 1116.532 |  | 5.3567 | 5.4741 | 5.6794 | 5.3086 | 5.3323 | 5.2932 | 5.4009 | 5.0569 | 42.9021 | 0.038612 |  | 62.069 | 100
19980530233000 | 1998-05-30 23:30 | 472.329 |  | 16.206 | 148.839 | 148.643 | 148.739 | 146.663 |  | 1124.282 | 1121.865 |  | 5.3796 | 5.4963 | 5.7053 | 5.3459 | 5.3352 | 5.3079 | 5.417 | 5.0667 | 43.0539 | 0.038749 |  | 62.069 | 100
19980531000000 | 1998-05-31 | 472.722 |  | 2.499 | 148.94 | 149.67 | 148.667 | 146.7 |  | 1123.949 | 1123.032 |  | 5.365 | 5.5 | 5.6953 | 5.3376 | 5.342 | 5.3147 | 5.4231 | 5.0652 | 43.0429 | 0.038739 |  | 62.069 | 100
19980531003000 | 1998-05-31 00:30 | 468.764 |  | 0.9 | 149.247 | 149.046 | 148.392 | 146.323 |  | 1131.366 | 1134.033 |  | 5.4023 | 5.5283 | 5.7542 | 5.3979 | 5.3657 | 5.3445 | 5.4512 | 5.1072 | 43.3513 | 0.039016 |  | 62.069 | 100
19980531010000 | 1998-05-31 01:00 | 422.863 |  | 1.148 | 148.749 | 147.468 | 147.773 | 144.003 |  | 1024.363 | 983.695 |  | 5.04 | 5.1772 | 5.2544 | 4.9036 | 5.0271 | 5.0308 | 5.1575 | 3.1632 | 38.7538 | 0.034878 |  | 62.069 | 100
19980531013000 | 1998-05-31 01:30 | 418.537 |  | 0.411 | 147.433 | 148.041 | 146.627 | 146.061 |  | 1013.862 | 975.611 |  | 4.8286 | 4.9622 | 5.0088 | 4.6997 | 4.802 | 4.8645 | 4.9575 | 4.5151 | 38.6384 | 0.034775 |  | 62.069 | 100
19980531020000 | 1998-05-31 02:00 | 419.56 |  | 1.762 | 148.435 | 149.123 | 147.932 | 146.648 |  | 1010.862 | 971.111 |  | 4.8303 | 4.9431 | 5.0042 | 4.6768 | 4.7998 | 4.8379 | 4.95 | 4.4946 | 38.5367 | 0.034683 |  | 62.069 | 100
19980531023000 | 1998-05-31 02:30 | 418.354 |  | 0.536 | 149.951 | 149.567 | 149.609 | 147.339 |  | 1029.946 | 995.779 |  | 4.8447 | 4.9514 | 5.0134 | 4.7058 | 4.8181 | 4.8738 | 4.9707 | 4.5181 | 38.696 | 0.034826 |  | 62.069 | 100
19980531030000 | 1998-05-31 03:00 | 418.328 |  | 2.011 | 149.14 | 148.148 | 149.043 | 146.416 |  | 1035.446 | 1003.445 |  | 4.8691 | 4.9851 | 5.0476 | 4.7327 | 4.8364 | 4.8835 | 4.9797 | 4.5342 | 38.8683 | 0.034981 |  | 62.069 | 100
19980531033000 | 1998-05-31 03:30 | 424.776 |  | 0.905 | 148.836 | 149.319 | 148.281 | 146.349 |  | 1033.446 | 1004.112 |  | 4.8799 | 5.0056 | 5.0979 | 4.751 | 4.8462 | 4.9065 | 5.0186 | 4.5625 | 39.0682 | 0.035161 |  | 62.069 | 100
19980531040000 | 1998-05-31 04:00 | 421.683 |  | 2.007 | 149.516 | 149.474 | 148.966 | 148.237 |  | 1048.363 | 1021.946 |  | 5.124 | 5.2361 | 5.3833 | 3.3174 | 5.0806 | 5.0964 | 5.2285 | 4.7532 | 39.2195 | 0.035298 |  | 62.069 | 100
19980531043000 | 1998-05-31 04:30 | 378.272 |  | 0.904 | 148.532 | 144.668 | 148.4 | 142.441 |  | 932.527 | 858.191 |  | 4.4275 | 4.6182 | 4.554 | 2.826 | 4.4556 | 4.5625 | 4.6724 | 4.1794 | 34.2956 | 0.030866 |  | 62.069 | 100
19980531050000 | 1998-05-31 05:00 | 348.178 |  | 1.27 | 147.115 | 148.979 | 146.429 | 146.504 |  | 916.193 | 825.107 |  | 0.0032 | 4.7607 | 4.8181 | 4.4153 | 4.6501 | 4.7905 | 4.8828 | 4.3572 | 32.6779 | 0.02941 |  | 62.069 | 100
19980531053000 | 1998-05-31 05:30 | 350.275 |  | 0.901 | 148.557 | 148.628 | 147.581 | 147.143 |  | 916.193 | 822.94 |  | 0.0032 | 4.7578 | 4.7776 | 4.3542 | 4.6311 | 4.7646 | 4.8379 | 4.3359 | 32.4623 | 0.029216 |  | 62.069 | 100
19980531060000 | 1998-05-31 06:00 | 351.298 |  | 1.52 | 148.96 | 149.057 | 148.446 | 147.572 |  | 922.776 | 832.274 |  | 0.0032 | 4.7546 | 4.7363 | 4.3428 | 4.6045 | 4.7729 | 4.8523 | 4.335 | 32.4016 | 0.029161 |  | 62.069 | 100
19980531063000 | 1998-05-31 06:30 | 351.796 |  | 0.537 | 149.342 | 148.994 | 148.899 | 148.004 |  | 921.943 | 831.524 |  | 0.0055 | 4.7883 | 4.7966 | 4.4031 | 4.6548 | 4.7754 | 4.8699 | 4.3655 | 32.6591 | 0.029393 |  | 62.069 | 100
19980531070000 | 1998-05-31 07:00 | 343.958 |  | 1.271 | 149.14 | 148.747 | 149.042 | 146.767 |  | 908.359 | 801.94 |  | 0.004 | 4.8486 | 4.9158 | 4.4907 | 4.7432 | 4.8469 | 4.9348 | 4.429 | 33.213 | 0.029892 |  | 62.069 | 100
19980531073000 | 1998-05-31 07:30 | 346.736 |  | 0.413 | 148.757 | 149.227 | 148.354 | 147.247 |  | 907.359 | 806.19 |  | 0.0032 | 4.8074 | 4.8494 | 4.4387 | 4.6768 | 4.7988 | 4.8965 | 4.4038 | 32.8746 | 0.029587 |  | 62.069 | 100
19980531080000 | 1998-05-31 08:00 | 418.826 |  | 1.64 | 149.388 | 151.795 | 149.066 | 150.062 |  | 1023.779 | 994.362 |  | 0.0047 | 5.7183 | 5.887 | 5.6099 | 5.4849 | 5.5229 | 5.6443 | 5.2002 | 39.0722 | 0.035165 |  | 62.069 | 100
19980531083000 | 1998-05-31 08:30 | 457.832 |  | 1.148 | 150.657 | 150.191 | 150.448 | 147.716 |  | 1143.116 | 1156.867 |  | 0.0032 | 6.4033 | 6.6841 | 6.5271 | 6.1311 | 6.1738 | 6.2813 | 5.8479 | 44.0518 | 0.039647 |  | 62.069 | 100
19980531090000 | 1998-05-31 09:00 | 507.613 |  | 3.97 | 150.785 | 150.49 | 150.472 | 148.015 |  | 1204.535 | 1227.035 |  | 0.0032 | 6.6643 | 7.0833 | 6.865 | 6.4148 | 6.3721 | 6.498 | 6.0974 | 45.9981 | 0.041398 |  | 62.069 | 100
19980531093000 | 1998-05-31 09:30 | 497.521 |  | 21.311 | 149.742 | 149.748 | 149.55 | 147.025 |  | 1207.118 | 1233.035 |  | 0.0032 | 6.7109 | 7.1335 | 6.9106 | 6.4644 | 6.3965 | 6.5217 | 6.1311 | 46.2719 | 0.041645 |  | 62.069 | 100
19980531100000 | 1998-05-31 10:00 | 500.378 |  | 2.38 | 149.527 | 149.877 | 149.112 | 147.154 |  | 1207.451 | 1234.785 |  | 0.0032 | 6.688 | 7.1289 | 6.9124 | 6.4661 | 6.3965 | 6.5186 | 6.1272 | 46.2409 | 0.041617 |  | 62.069 | 100
19980531103000 | 1998-05-31 10:30 | 503.917 |  | 1.643 | 148.989 | 148.562 | 148.841 | 146.582 |  | 1204.618 | 1233.702 |  | 0.0047 | 6.6621 | 7.0969 | 6.8848 | 6.4255 | 6.3491 | 6.4819 | 6.0989 | 46.0039 | 0.041404 |  | 62.069 | 100
19980531110000 | 1998-05-31 11:00 | 505.28 |  | 4.083 | 148.647 | 149.995 | 148.516 | 146.282 |  | 1201.201 | 1224.368 |  | 0.004 | 6.6392 | 7.0642 | 6.8384 | 6.4058 | 6.3308 | 6.4507 | 6.0708 | 45.8039 | 0.041224 |  | 62.069 | 100
19980531113000 | 1998-05-31 11:30 | 505.28 |  | 1.514 | 149.236 | 150.516 | 148.716 | 147.298 |  | 1202.618 | 1228.535 |  | 0.0032 | 6.636 | 7.0427 | 6.8306 | 6.3889 | 6.324 | 6.446 | 6.0762 | 45.7476 | 0.041173 |  | 62.069 | 100
19980531120000 | 1998-05-31 12:00 | 502.554 |  | 2.863 | 149.378 | 149.278 | 149.141 | 147.546 |  | 1201.868 | 1227.952 |  | 0.004 | 6.637 | 7.0527 | 6.8284 | 6.3911 | 6.3257 | 6.4539 | 6.0791 | 45.7719 | 0.041195 |  | 62.069 | 100
19980531123000 | 1998-05-31 12:30 | 503.314 |  | 1.27 | 148.738 | 148.928 | 149.205 | 146.947 |  | 1205.201 | 1233.369 |  | 0.0032 | 6.6621 | 7.0984 | 6.8604 | 6.427 | 6.3516 | 6.4819 | 6.0967 | 45.9813 | 0.041383 |  | 62.069 | 100
19980531130000 | 1998-05-31 13:00 | 501.322 |  | 2.375 | 148.791 | 148.902 | 149.151 | 146.922 |  | 1208.285 | 1238.702 |  | 0.0032 | 6.6765 | 7.0862 | 6.8765 | 6.4302 | 6.3721 | 6.4949 | 6.1218 | 46.0614 | 0.041455 |  | 62.069 | 100
19980531133000 | 1998-05-31 13:30 | 480.718 |  | 1.025 | 148.607 | 147.834 | 148.522 | 144.122 |  | 1139.033 | 1147.616 |  | 0.0032 | 6.3286 | 6.6934 | 6.4094 | 6.1143 | 6.0571 | 6.1768 | 5.7922 | 43.575 | 0.039217 |  | 62.069 | 100
19980531140000 | 1998-05-31 14:00 | 441.108 |  | 21.324 | 148.188 | 148.097 | 147.142 | 145.374 |  | 1055.447 | 1040.113 |  | 0.0032 | 5.8716 | 6.0952 | 5.8213 | 5.6755 | 5.6228 | 5.7502 | 5.3552 | 40.195 | 0.036175 |  | 62.069 | 100
19980531143000 | 1998-05-31 14:30 | 437.595 |  | 0.652 | 148.597 | 151.403 | 148.262 | 148.433 |  | 1095.031 | 1090.115 |  | 0.0032 | 6.0051 | 6.2302 | 6.0073 | 5.7754 | 5.7488 | 5.864 | 5.4763 | 41.1103 | 0.036999 |  | 62.069 | 100
19980531150000 | 1998-05-31 15:00 | 439.011 |  | 2.74 | 149.885 | 148.577 | 149.573 | 146.349 |  | 1091.698 | 1086.365 |  | 0.0017 | 5.957 | 6.2104 | 5.9563 | 5.748 | 5.7031 | 5.8296 | 5.4421 | 40.8482 | 0.036763 |  | 62.069 | 100
19980531153000 | 1998-05-31 15:30 | 440.531 |  | 0.534 | 148.638 | 149.319 | 148.29 | 146.844 |  | 1086.781 | 1081.614 |  | 0.0055 | 5.9387 | 6.1692 | 5.9106 | 5.7236 | 5.687 | 5.8159 | 5.4146 | 40.6651 | 0.036599 |  | 62.069 | 100
19980531160000 | 1998-05-31 16:00 | 438.958 |  | 3.474 | 148.848 | 149.711 | 148.471 | 147.236 |  | 1097.615 | 1090.198 |  | 0.0032 | 5.9646 | 6.1921 | 5.98 | 5.7534 | 5.7275 | 5.8486 | 5.4604 | 40.9298 | 0.036837 |  | 62.069 | 100
19980531163000 | 1998-05-31 16:30 | 440.269 |  | 6.53 | 149.359 | 149.345 | 149.044 | 146.375 |  | 1093.115 | 1090.531 |  | 0.0047 | 5.9663 | 6.1829 | 5.9534 | 5.7358 | 5.7229 | 5.845 | 5.449 | 40.86 | 0.036774 |  | 62.069 | 100
19980531170000 | 1998-05-31 17:00 | 453.691 |  | 2.377 | 148.802 | 149.944 | 148.215 | 146.973 |  | 1149.783 | 1167.95 |  | 0.004 | 6.3271 | 6.636 | 6.4705 | 6.106 | 6.0959 | 6.2202 | 5.8015 | 43.6612 | 0.039295 |  | 62.069 | 100
19980531173000 | 1998-05-31 17:30 | 485.908 |  | 2.253 | 149.721 | 150.062 | 149.697 | 147.834 |  | 1184.867 | 1212.368 |  | 5.5154 | 5.738 | 5.9121 | 5.6741 | 5.5078 | 5.5039 | 5.6184 | 5.2332 | 44.7029 | 0.040233 |  | 62.069 | 100
19980531180000 | 1998-05-31 18:00 | 528.716 |  | 3.479 | 150.101 | 150.165 | 150.53 | 150.413 |  | 1269.12 | 1320.038 |  | 5.9707 | 6.1921 | 6.5139 | 6.2927 | 5.97 | 5.9097 | 6.0471 | 5.6672 | 48.5634 | 0.043707 |  | 62.069 | 100
19980531183000 | 1998-05-31 18:30 | 547.616 |  | 4.575 | 149.76 | 150.114 | 152.654 | 152.341 |  | 1366.123 | 1433.041 |  | 6.3218 | 6.5544 | 6.9573 | 6.7139 | 6.3179 | 6.2874 | 6.4026 | 6.0083 | 51.5636 | 0.046407 |  | 62.069 | 100
19980531190000 | 1998-05-31 19:00 | 578.942 |  | 5.309 | 150.286 | 151.975 | 155.253 | 155.193 |  | 1393.457 | 1459.459 |  | 6.5332 | 6.7712 | 7.2395 | 7.0557 | 6.521 | 6.4446 | 6.5706 | 6.2112 | 53.347 | 0.048012 |  | 62.069 | 100
19980531193000 | 1998-05-31 19:30 | 584.421 |  | 5.436 | 151.291 | 153.213 | 157.044 | 156.679 |  | 1395.873 | 1459.792 |  | 6.5278 | 6.749 | 7.1924 | 6.991 | 6.4895 | 6.4216 | 6.5483 | 6.1853 | 53.1049 | 0.047794 |  | 62.069 | 100
19980531200000 | 1998-05-31 20:00 | 531.285 |  | 4.327 | 151.981 | 150.645 | 157.902 | 155.348 |  | 1273.37 | 1324.371 |  | 6.0195 | 6.2393 | 6.5759 | 6.2927 | 6.0066 | 5.925 | 6.0623 | 5.7007 | 48.822 | 0.04394 |  | 62.069 | 100
19980531203000 | 1998-05-31 20:30 | 534.064 |  | 3.722 | 149.185 | 149.304 | 155.457 | 152.027 |  | 1274.62 | 1319.204 |  | 6.0112 | 6.2202 | 6.5193 | 6.2585 | 5.9951 | 5.9204 | 6.0364 | 5.6838 | 48.6449 | 0.04378 |  | 62.069 | 100
19980531210000 | 1998-05-31 21:00 | 532.648 |  | 3.603 | 148.803 | 149.526 | 153.417 | 150.516 |  | 1270.286 | 1312.371 |  | 5.9983 | 6.2202 | 6.5217 | 6.2813 | 5.9854 | 5.9021 | 6.0342 | 5.6648 | 48.608 | 0.043747 |  | 62.069 | 100
19980531213000 | 1998-05-31 21:30 | 532.779 |  | 3.234 | 149.19 | 149.268 | 152.796 | 150.01 |  | 1263.87 | 1309.121 |  | 5.9602 | 6.1897 | 6.4712 | 6.2341 | 5.9358 | 5.8801 | 6.0022 | 5.6558 | 48.3291 | 0.043496 |  | 62.069 | 100
19980531220000 | 1998-05-31 22:00 | 579.808 |  | 6.415 | 149.386 | 150.908 | 152.915 | 153.878 |  | 1374.039 | 1437.125 |  | 6.4966 | 6.6941 | 7.1724 | 6.9443 | 6.4575 | 6.3782 | 6.5017 | 6.1379 | 52.7827 | 0.047504 |  | 62.069 | 100
19980531223000 | 1998-05-31 22:30 | 616.953 |  | 13.293 | 151.115 | 155.312 | 156.241 | 158.282 |  | 1479.292 | 1559.628 |  | 6.8894 | 7.1252 | 7.6614 | 7.4998 | 6.874 | 6.7642 | 6.9016 | 6.543 | 56.2586 | 0.050633 |  | 62.069 | 100
19980531230000 | 1998-05-31 23:00 | 620.623 |  | 6.534 | 154.027 | 155.704 | 159.854 | 159.417 |  | 1470.709 | 1545.378 |  | 6.9177 | 7.1182 | 7.6638 | 7.47 | 6.8801 | 6.7688 | 6.8848 | 6.5347 | 56.2381 | 0.050614 |  | 62.069 | 100
19980531233000 | 1998-05-31 23:30 | 621.672 |  | 6.532 | 154.663 | 155.755 | 160.745 | 158.973 |  | 1472.209 | 1547.294 |  | 6.9023 | 7.1084 | 7.6707 | 7.4875 | 6.8711 | 6.7368 | 6.8711 | 6.5383 | 56.1862 | 0.050568 |  | 62.069 | 100
19980901003000 | 1998-09-01 00:30 | 439.692 |  | 3.106 | 148.974 | 150.856 | 151.223 | 149.371 |  | 901.776 | 995.112 |  | 5.0347 | 5.2253 | 5.5039 | 5.0073 | 5.0195 | 5.0735 | 4.9736 | 4.8501 | 40.6879 | 0.036619 |  | 62.069 | 100
19980901010000 | 1998-09-01 01:00 | 442.445 |  | 1.509 | 148.657 | 151.758 | 151.342 | 149.035 |  | 912.026 | 1001.779 |  | 5.0415 | 5.2383 | 5.5215 | 5.0293 | 5.0232 | 5.0813 | 4.9912 | 4.8699 | 40.7962 | 0.036717 |  | 62.069 | 100
19980901013000 | 1998-09-01 01:30 | 443.1 |  | 2.001 | 149.005 | 151.351 | 151.431 | 149.866 |  | 908.026 | 997.029 |  | 5.0605 | 5.2437 | 5.519 | 5.002 | 5.0308 | 5.0759 | 4.9797 | 4.8721 | 40.7837 | 0.036705 |  | 62.069 | 100
19980901020000 | 1998-09-01 02:00 | 439.561 |  | 1.017 | 148.914 | 152.511 | 151.699 | 150.036 |  | 928.11 | 1022.279 |  | 5.1057 | 5.291 | 5.584 | 5.0867 | 5.0698 | 5.1133 | 5.0171 | 4.9226 | 41.1902 | 0.037071 |  | 62.069 | 100
19980901023000 | 1998-09-01 02:30 | 437.097 |  | 2.121 | 149.08 | 151.274 | 151.559 | 148.798 |  | 928.943 | 1021.863 |  | 5.1018 | 5.314 | 5.5908 | 5.124 | 5.0806 | 5.1423 | 5.0491 | 4.9316 | 41.3342 | 0.037201 |  | 62.069 | 100
19980901030000 | 1998-09-01 03:00 | 438.172 |  | 0.77 | 148.239 | 150.675 | 150.529 | 148.2 |  | 917.526 | 1011.612 |  | 5.0781 | 5.282 | 5.5671 | 5.0637 | 5.0605 | 5.1172 | 5.0171 | 4.9133 | 41.099 | 0.036989 |  | 62.069 | 100
19980901033000 | 1998-09-01 03:30 | 441.239 |  | 2.612 | 148.743 | 152.16 | 150.863 | 150.18 |  | 923.11 | 1015.862 |  | 5.0613 | 5.2468 | 5.5276 | 5.0278 | 5.0247 | 5.0698 | 4.9751 | 4.8821 | 40.8152 | 0.036734 |  | 62.069 | 100
19980901040000 | 1998-09-01 04:00 | 441.108 |  | 0.895 | 148.971 | 148.643 | 151.493 | 147.653 |  | 912.86 | 1001.695 |  | 5.1606 | 5.3589 | 5.6702 | 4.9453 | 5.1399 | 5.1704 | 5.0813 | 4.9729 | 41.4995 | 0.03735 |  | 62.069 | 100
19980901043000 | 1998-09-01 04:30 | 446.141 |  | 1.879 | 147.698 | 150.35 | 149.969 | 148.123 |  | 906.193 | 997.862 |  | 5.0645 | 5.2766 | 5.5488 | 5.0652 | 5.0422 | 5.0957 | 5.0049 | 4.8982 | 40.9961 | 0.036896 |  | 62.069 | 100
19980901050000 | 1998-09-01 05:00 | 443.388 |  | 1.02 | 148.515 | 151.47 | 150.864 | 149.984 |  | 898.109 | 989.612 |  | 5.0454 | 5.2529 | 5.5054 | 5.0049 | 5.0308 | 5.072 | 4.979 | 4.8699 | 40.7603 | 0.036684 |  | 62.069 | 100
19980901053000 | 1998-09-01 05:30 | 449.077 |  | 2 | 148.911 | 151.47 | 151.389 | 148.994 |  | 903.193 | 993.279 |  | 5.0522 | 5.2666 | 5.5176 | 5.0271 | 5.03 | 5.095 | 5.0042 | 4.895 | 40.8877 | 0.036799 |  | 62.069 | 100
19980901060000 | 1998-09-01 06:00 | 455.552 |  | 20.852 | 148.819 | 151.418 | 151.369 | 149.438 |  | 893.859 | 980.862 |  | 5.0195 | 5.23 | 5.4719 | 4.9988 | 5.0012 | 5.0562 | 4.9729 | 4.8516 | 40.6021 | 0.036542 |  | 62.069 | 100
19980901063000 | 1998-09-01 06:30 | 454.975 |  | 2.248 | 148.856 | 151.547 | 151.034 | 149.072 |  | 903.109 | 992.362 |  | 5.0652 | 5.272 | 5.5496 | 5.0393 | 3.5287 | 5.1208 | 5.0386 | 4.9126 | 39.5268 | 0.035574 |  | 62.069 | 100
19980901070000 | 1998-09-01 07:00 | 520.458 |  | 1.259 | 149.276 | 152.408 | 151.746 | 150.18 |  | 1027.946 | 1130.282 |  | 5.9219 | 6.1753 | 6.6216 | 6.1821 | 3.882 | 5.8687 | 5.7754 | 5.7563 | 46.1833 | 0.041565 |  | 62.069 | 100
19980901073000 | 1998-09-01 07:30 | 517.234 |  | 2.981 | 149.016 | 151.547 | 151.772 | 148.824 |  | 1031.696 | 1133.866 |  | 5.9426 | 6.1943 | 6.6536 | 6.2302 | 3.8965 | 5.8953 | 5.8076 | 5.7825 | 46.4026 | 0.041762 |  | 62.069 | 100
19980901080000 | 1998-09-01 08:00 | 521.428 |  | 1.509 | 148.642 | 151.48 | 151.116 | 149.005 |  | 1032.53 | 1134.283 |  | 5.9189 | 6.1685 | 6.6108 | 6.1904 | 3.8827 | 5.8564 | 5.7656 | 5.748 | 46.1413 | 0.041527 |  | 62.069 | 100
19980901083000 | 1998-09-01 08:30 | 597.161 |  | 2.98 | 148.841 | 153.631 | 151.292 | 149.423 |  | 1225.785 | 1343.539 |  | 6.791 | 7.1106 | 7.7561 | 7.3586 | 4.4854 | 6.7551 | 6.6658 | 6.6431 | 53.5657 | 0.048209 |  | 62.069 | 100
19980901090000 | 1998-09-01 09:00 | 631.633 |  | 2.975 | 150.28 | 152.692 | 152.87 | 149.227 |  | 1279.703 | 1403.124 |  | 7.0107 | 7.2983 | 8.0176 | 7.6179 | 4.6196 | 6.8984 | 6.8252 | 6.8147 | 55.1024 | 0.049592 |  | 62.069 | 100
19980901093000 | 1998-09-01 09:30 | 628.645 |  | 3.594 | 149.091 | 151.78 | 151.569 | 148.314 |  | 1257.369 | 1378.623 |  | 6.8374 | 7.126 | 7.8118 | 7.3853 | 6.678 | 6.7268 | 6.6353 | 6.6445 | 55.8451 | 0.050261 |  | 62.069 | 100
19980901100000 | 1998-09-01 10:00 | 630.218 |  | 2 | 148.793 | 151.377 | 151.236 | 148.159 |  | 1254.286 | 1375.539 |  | 6.7139 | 7.0259 | 7.6462 | 7.2473 | 6.6675 | 6.6377 | 6.5422 | 6.553 | 55.0337 | 0.04953 |  | 62.069 | 100
19980901103000 | 1998-09-01 10:30 | 630.821 |  | 2.976 | 148.393 | 151.713 | 150.96 | 148.495 |  | 1249.953 | 1369.623 |  | 6.73 | 7.0374 | 7.6592 | 7.2769 | 6.6926 | 6.6467 | 6.5559 | 6.553 | 55.1517 | 0.049637 |  | 62.069 | 100
19980901110000 | 1998-09-01 11:00 | 632.787 |  | 1.872 | 149.029 | 151.805 | 151.34 | 148.34 |  | 1259.036 | 1380.456 |  | 6.7681 | 7.0542 | 7.7188 | 7.29 | 6.7185 | 6.6658 | 6.575 | 6.5781 | 55.3685 | 0.049832 |  | 62.069 | 100
19980901113000 | 1998-09-01 11:30 | 631.922 |  | 4.571 | 148.852 | 151.805 | 151.34 | 148.588 |  | 1258.453 | 1376.623 |  | 6.749 | 7.0474 | 7.6882 | 7.2854 | 6.7153 | 6.7041 | 6.5728 | 6.5559 | 55.3181 | 0.049786 |  | 62.069 | 100
19980901120000 | 1998-09-01 12:00 | 633.468 |  | 21.753 | 148.651 | 151.78 | 151.026 | 148.067 |  | 1254.953 | 1375.873 |  | 6.7422 | 7.0327 | 7.6851 | 7.2549 | 6.7017 | 6.6948 | 6.5559 | 6.5505 | 55.2178 | 0.049696 |  | 62.069 | 100
19980901123000 | 1998-09-01 12:30 | 653.05 |  | 3.469 | 148.911 | 152.47 | 151.234 | 149.253 |  | 1299.787 | 1425.624 |  | 6.9709 | 7.2646 | 7.978 | 7.5532 | 6.9246 | 6.9099 | 6.7803 | 6.7695 | 57.151 | 0.051436 |  | 62.069 | 100
19980901130000 | 1998-09-01 13:00 | 653.05 |  | 2.488 | 148.954 | 151.599 | 151.508 | 147.886 |  | 1298.204 | 1425.874 |  | 6.9275 | 7.2366 | 7.9263 | 7.5081 | 6.8984 | 6.8855 | 6.7573 | 6.7529 | 56.8926 | 0.051203 |  | 62.069 | 100
19980901133000 | 1998-09-01 13:30 | 655.305 |  | 5.677 | 148.587 | 151.599 | 151.204 | 148.133 |  | 1299.204 | 1430.541 |  | 6.9619 | 7.2778 | 7.9697 | 7.5454 | 6.9207 | 6.9138 | 6.7734 | 6.7781 | 57.1408 | 0.051427 |  | 62.069 | 100
19980901140000 | 1998-09-01 14:00 | 651.504 |  | 2.121 | 148.699 | 152.419 | 151.294 | 148.211 |  | 1292.704 | 1418.041 |  | 6.9167 | 7.2205 | 7.9072 | 7.4792 | 6.884 | 6.8726 | 6.7368 | 6.7253 | 56.7423 | 0.051068 |  | 62.069 | 100
19980901143000 | 1998-09-01 14:30 | 653.234 |  | 3.466 | 148.913 | 151.676 | 151.174 | 148.211 |  | 1297.787 | 1425.791 |  | 6.9558 | 7.2563 | 7.9736 | 7.531 | 6.9282 | 6.9077 | 6.7764 | 6.7703 | 57.0993 | 0.051389 |  | 62.069 | 100
19980901150000 | 1998-09-01 15:00 | 654.885 |  | 1.626 | 148.608 | 151.872 | 151.022 | 148.407 |  | 1296.787 | 1424.624 |  | 6.9512 | 7.2646 | 7.959 | 7.5454 | 6.9282 | 6.9077 | 6.7764 | 6.7742 | 57.1067 | 0.051396 |  | 62.069 | 100
19980901153000 | 1998-09-01 15:30 | 521.481 |  | 3.708 | 147.885 | 149.304 | 149.934 | 146.087 |  | 999.029 | 1092.781 |  | 5.5635 | 5.7656 | 6.1692 | 5.6526 | 5.5298 | 5.5139 | 5.3948 | 5.3643 | 44.9537 | 0.040458 |  | 62.069 | 100
19980901160000 | 1998-09-01 16:00 | 471.674 |  | 1.01 | 146.556 | 150.361 | 148.669 | 146.896 |  | 922.693 | 1007.279 |  | 5.1392 | 5.3201 | 5.6152 | 5.1072 | 5.1147 | 5.1772 | 5.0583 | 4.9575 | 41.4894 | 0.03734 |  | 62.069 | 100
19980901163000 | 1998-09-01 16:30 | 440.4 |  | 3.342 | 148.345 | 151.47 | 150.697 | 148.499 |  | 893.692 | 978.861 |  | 4.9141 | 5.0806 | 5.3284 | 4.8188 | 4.8806 | 4.9912 | 4.8684 | 4.7295 | 39.6116 | 0.03565 |  | 62.069 | 100
19980901170000 | 1998-09-01 17:00 | 437.516 |  | 1.133 | 148.465 | 150.051 | 150.8 | 148.318 |  | 888.609 | 970.695 |  | 4.8774 | 5.0896 | 5.2971 | 4.8181 | 4.8477 | 4.9783 | 4.8538 | 4.7195 | 39.4815 | 0.035533 |  | 62.069 | 100
19980901173000 | 1998-09-01 17:30 | 434.764 |  | 2.731 | 148.433 | 151.211 | 150.804 | 148.736 |  | 888.442 | 971.111 |  | 4.9126 | 5.0789 | 5.323 | 4.7898 | 4.8691 | 4.9661 | 4.8447 | 4.7249 | 39.5091 | 0.035558 |  | 62.069 | 100
19980901180000 | 1998-09-01 18:00 | 440.295 |  | 1.011 | 149.061 | 151.082 | 151.376 | 150.092 |  | 896.359 | 981.528 |  | 4.9026 | 5.0881 | 5.3237 | 4.821 | 4.8501 | 4.9744 | 4.8494 | 4.7249 | 39.5342 | 0.035581 |  | 62.069 | 100
19980901183000 | 1998-09-01 18:30 | 473.43 |  | 1.381 | 148.466 | 150.531 | 150.963 | 147.808 |  | 948.611 | 1041.947 |  | 5.3125 | 5.5337 | 5.8755 | 5.3865 | 5.2781 | 5.356 | 5.2354 | 5.1338 | 43.1115 | 0.0388 |  | 62.069 | 100
19980901190000 | 1998-09-01 19:00 | 444.516 |  | 0.767 | 148.031 | 149.752 | 150.215 | 148.019 |  | 870.442 | 951.777 |  | 4.9026 | 5.0767 | 5.3298 | 4.8188 | 4.8569 | 4.9629 | 4.8433 | 4.7295 | 39.5205 | 0.035568 |  | 62.069 | 100
19980901193000 | 1998-09-01 19:30 | 442.418 |  | 2.24 | 148.407 | 151.196 | 150.663 | 148.968 |  | 872.025 | 956.611 |  | 4.8958 | 5.0735 | 5.3101 | 4.8066 | 4.8669 | 4.96 | 4.844 | 4.7126 | 39.4695 | 0.035523 |  | 62.069 | 100
19980901200000 | 1998-09-01 20:00 | 437.438 |  | 0.892 | 148.821 | 150.886 | 151.107 | 148.906 |  | 869.358 | 952.611 |  | 4.8416 | 5.0454 | 5.2864 | 4.8203 | 4.7927 | 4.9126 | 4.8074 | 4.6907 | 39.1971 | 0.035277 |  | 62.069 | 100
19980901203000 | 1998-09-01 20:30 | 441.711 |  | 21.337 | 148.654 | 150.938 | 150.988 | 149.453 |  | 865.692 | 947.027 |  | 4.8767 | 5.0652 | 5.342 | 4.8997 | 4.8325 | 4.9363 | 4.8232 | 4.7144 | 39.49 | 0.035541 |  | 62.069 | 100
19980901210000 | 1998-09-01 21:00 | 410.149 |  | 0.645 | 148.805 | 151.521 | 151.457 | 149.046 |  | 793.023 | 868.358 |  | 4.4832 | 4.6846 | 4.8264 | 4.3877 | 4.4641 | 4.5747 | 4.4724 | 4.3633 | 36.2564 | 0.032631 |  | 62.069 | 100
19980901213000 | 1998-09-01 21:30 | 404.382 |  | 2.364 | 148.389 | 150.154 | 150.572 | 148.917 |  | 807.107 | 881.775 |  | 4.5044 | 4.7036 | 4.8364 | 4.4175 | 4.467 | 4.6228 | 4.5173 | 4.3625 | 36.4315 | 0.032788 |  | 62.069 | 100
19980901220000 | 1998-09-01 22:00 | 408.654 |  | 0.77 | 148.268 | 151.315 | 150.678 | 149.582 |  | 806.857 | 879.859 |  | 4.522 | 4.7234 | 4.876 | 4.4556 | 4.4893 | 4.6448 | 4.5388 | 4.387 | 36.6369 | 0.032973 |  | 62.069 | 100
19980901223000 | 1998-09-01 22:30 | 389.125 |  | 1.507 | 148.612 | 151.81 | 151.457 | 149.829 |  | 762.105 | 836.607 |  | 4.3489 | 4.532 | 4.6462 | 4.1938 | 4.2908 | 4.4319 | 4.3313 | 4.2031 | 34.978 | 0.03148 |  | 62.069 | 100
19980901230000 | 1998-09-01 23:00 | 359.45 |  | 0.404 | 148.547 | 149.881 | 150.729 | 148.148 |  | 728.688 | 795.273 |  | 4.1016 | 4.2825 | 4.3281 | 3.9292 | 4.0764 | 4.2786 | 4.1787 | 3.978 | 33.1531 | 0.029838 |  | 62.069 | 100
19980901233000 | 1998-09-01 23:30 | 354.837 |  | 1.509 | 148.084 | 151.536 | 150.368 | 150.299 |  | 698.937 | 759.022 |  | 3.9041 | 4.0864 | 4.0613 | 3.65 | 3.8629 | 4.0703 | 3.9766 | 3.7736 | 31.3852 | 0.028247 |  | 62.069 | 100
19980902000000 | 1998-09-02 | 352.032 |  | 1.997 | 148.751 | 150.845 | 151.223 | 148.618 |  | 712.687 | 777.606 |  | 4.0596 | 4.2007 | 4.2512 | 3.8315 | 4.0115 | 4.1763 | 4.0925 | 3.8949 | 32.5182 | 0.029266 |  | 62.069 | 100
19980902003000 | 1998-09-02 00:30 | 340.786 |  | 4.204 | 148.656 | 150.923 | 151.033 | 149.933 |  | 678.269 | 739.188 |  | 3.901 | 4.0161 | 4.0229 | 3.5944 | 3.859 | 3.9949 | 3.9353 | 3.7324 | 31.056 | 0.02795 |  | 62.069 | 100
19980902010000 | 1998-09-02 01:00 | 337.928 |  | 0.277 | 148.344 | 151.026 | 151.137 | 149.293 |  | 683.853 | 743.105 |  | 3.8895 | 3.9865 | 4.0229 | 3.5577 | 3.8407 | 3.962 | 3.9376 | 3.7095 | 30.9064 | 0.027816 |  | 62.069 | 100
19980902013000 | 1998-09-02 01:30 | 336.382 |  | 3.349 | 148.647 | 151.429 | 150.754 | 149.201 |  | 681.27 | 738.605 |  | 3.9132 | 4.0344 | 4.0581 | 3.6165 | 3.882 | 3.9491 | 3.959 | 3.7522 | 31.1645 | 0.028048 |  | 62.069 | 100
19980902020000 | 1998-09-02 02:00 | 339.213 |  | 0.28 | 149.183 | 151.181 | 151.139 | 150.934 |  | 677.353 | 735.521 |  | 3.8857 | 4.001 | 4.0391 | 3.5829 | 3.8568 | 3.917 | 3.9376 | 3.724 | 30.9441 | 0.02785 |  | 62.069 | 100
19980902023000 | 1998-09-02 02:30 | 341.074 |  | 26.666 | 148.722 | 150.712 | 151.21 | 150.217 |  | 684.02 | 734.188 |  | 3.8995 | 3.9994 | 4.0437 | 3.5944 | 3.8621 | 3.9148 | 3.9338 | 3.7369 | 30.9846 | 0.027886 |  | 62.069 | 100
19980902030000 | 1998-09-02 03:00 | 336.565 |  | 0.079 | 148.958 | 150.387 | 151.516 | 149.892 |  | 702.854 | 750.522 |  | 3.9559 | 4.0857 | 4.1184 | 3.7034 | 3.9186 | 3.9758 | 4.0002 | 3.8003 | 31.5583 | 0.028402 |  | 62.069 | 100
19980902033000 | 1998-09-02 03:30 | 330.326 |  | 6.42 | 148.709 | 150.882 | 151.283 | 150.634 |  | 697.603 | 761.855 |  | 3.9155 | 4.0542 | 4.052 | 3.6324 | 3.8629 | 3.9399 | 3.9705 | 3.766 | 31.1934 | 0.028074 |  | 62.069 | 100
19980902040000 | 1998-09-02 04:00 | 336.277 |  | 0.077 | 148.936 | 151.429 | 151.576 | 150.191 |  | 701.187 | 730.104 |  | 3.8873 | 4.0032 | 4.0322 | 3.5874 | 3.8538 | 3.917 | 3.9407 | 3.7286 | 30.9502 | 0.027855 |  | 62.069 | 100
19980902043000 | 1998-09-02 04:30 | 339.501 |  | 4.456 | 148.928 | 150.217 | 151.037 | 149.227 |  | 695.187 | 731.104 |  | 3.8911 | 4.0107 | 4.0308 | 3.5928 | 3.8636 | 3.9048 | 3.9292 | 3.7286 | 30.9516 | 0.027856 |  | 62.069 | 100
19980902050000 | 1998-09-02 05:00 | 339.606 |  | 0.199 | 148.465 | 150.686 | 150.951 | 150.191 |  | 706.77 | 740.855 |  | 3.9407 | 4.0718 | 4.1069 | 3.6729 | 3.9078 | 3.9567 | 3.9811 | 3.7836 | 31.4215 | 0.028279 |  | 62.069 | 100
19980902053000 | 1998-09-02 05:30 | 337.955 |  | 4.085 | 148.522 | 151.011 | 151.109 | 149.773 |  | 695.02 | 728.854 |  | 3.9178 | 4.0581 | 4.0542 | 3.6409 | 3.8934 | 3.9559 | 3.9735 | 3.7751 | 31.2689 | 0.028142 |  | 62.069 | 100
19980902060000 | 1998-09-02 06:00 | 335.7 |  | 0.199 | 149.136 | 151.063 | 151.545 | 150.815 |  | 716.187 | 753.272 |  | 3.9475 | 4.0596 | 4.0857 | 3.6646 | 3.9178 | 3.9559 | 3.9697 | 3.7698 | 31.3706 | 0.028234 |  | 62.069 | 100
19980902063000 | 1998-09-02 06:30 | 335.333 |  | 3.592 | 148.807 | 150.764 | 151.116 | 150.021 |  | 712.52 | 748.855 |  | 3.917 | 4.075 | 4.0627 | 3.6752 | 3.885 | 3.962 | 3.9811 | 3.7858 | 31.3438 | 0.028209 |  | 62.069 | 100
19980902070000 | 1998-09-02 07:00 | 418.223 |  | 0.402 | 148.513 | 152.275 | 151.019 | 151.037 |  | 857.108 | 919.443 |  | 4.9104 | 5.1101 | 5.3521 | 4.9431 | 3.2343 | 4.895 | 4.8416 | 4.7632 | 38.0498 | 0.034245 |  | 62.069 | 100
19980902073000 | 1998-09-02 07:30 | 465.33 |  | 4.696 | 149.711 | 151.351 | 152.173 | 148.876 |  | 984.445 | 1075.698 |  | 5.5603 | 5.8228 | 6.176 | 5.8328 | 3.692 | 5.594 | 5.491 | 5.4314 | 43.6003 | 0.03924 |  | 62.069 | 100
19980902080000 | 1998-09-02 08:00 | 527.982 |  | 3.221 | 149.173 | 150.531 | 151.585 | 148.056 |  | 1067.531 | 1164.2 |  | 6.2715 | 6.582 | 7.1016 | 6.7483 | 4.1321 | 4.3313 | 6.1326 | 6.1279 | 47.4273 | 0.042685 |  | 62.069 | 100
19980902083000 | 1998-09-02 08:30 | 599.259 |  | 3.345 | 149.477 | 153.136 | 152.018 | 150.413 |  | 1194.118 | 1297.537 |  | 6.7476 | 7.051 | 7.6965 | 7.3044 | 4.4282 | 6.6499 | 6.5063 | 6.5544 | 52.9383 | 0.047644 |  | 62.069 | 100
19980902090000 | 1998-09-02 09:00 | 622.72 |  | 1.753 | 149.587 | 152.197 | 152.194 | 150.217 |  | 1240.702 | 1356.372 |  | 6.9573 | 7.2571 | 7.9604 | 7.5959 | 4.5869 | 6.8704 | 6.7544 | 6.7749 | 54.7573 | 0.049282 |  | 62.069 | 100
19980902093000 | 1998-09-02 09:30 | 576.793 |  | 5.8 | 148.856 | 150.361 | 151.09 | 146.401 |  | 1149.45 | 1251.453 |  | 6.5232 | 6.7986 | 7.4326 | 7.0405 | 4.2954 | 6.4346 | 6.3171 | 6.3469 | 51.1889 | 0.04607 |  | 62.069 | 100
19980902100000 | 1998-09-02 10:00 | 528.349 |  | 0.322 | 148.085 | 150.671 | 150.489 | 148.443 |  | 1048.03 | 1136.533 |  | 5.8022 | 6.0601 | 6.5186 | 6.1096 | 5.751 | 5.7434 | 5.6443 | 5.6497 | 47.2789 | 0.042551 |  | 62.069 | 100
19980902103000 | 1998-09-02 10:30 | 525.675 |  | 4.078 | 147.84 | 151.207 | 150.135 | 148.237 |  | 1051.947 | 1143.533 |  | 5.0447 | 6.0928 | 6.5505 | 6.1204 | 5.7893 | 5.771 | 5.6594 | 5.6748 | 46.7029 | 0.042033 |  | 62.069 | 100
19980902110000 | 1998-09-02 11:00 | 526.121 |  | 21.094 | 148.369 | 151.61 | 150.744 | 149.382 |  | 1041.613 | 1127.449 |  | 5.7092 | 5.9548 | 6.395 | 5.9692 | 5.655 | 5.6831 | 5.5703 | 5.5466 | 46.4832 | 0.041835 |  | 62.069 | 100
19980902113000 | 1998-09-02 11:30 | 523.447 |  | 4.935 | 148.942 | 151.506 | 151.418 | 149.031 |  | 1035.363 | 1128.449 |  | 5.7075 | 5.9463 | 6.4019 | 5.9541 | 5.6611 | 5.6672 | 5.5596 | 5.5383 | 46.436 | 0.041792 |  | 62.069 | 100
19980902120000 | 1998-09-02 12:00 | 520.275 |  | 1.009 | 148.836 | 150.893 | 151.337 | 148.913 |  | 1036.113 | 1126.866 |  | 5.7283 | 5.9656 | 6.4058 | 5.9792 | 5.6787 | 5.6848 | 5.5771 | 5.5618 | 46.5813 | 0.041923 |  | 62.069 | 100
19980902123000 | 1998-09-02 12:30 | 523.525 |  | 4.818 | 148.573 | 153.121 | 151.261 | 150.893 |  | 1058.697 | 1152.95 |  | 5.7075 | 5.9717 | 6.4141 | 5.9868 | 5.6655 | 5.6953 | 5.5825 | 5.5657 | 46.5891 | 0.04193 |  | 62.069 | 100
19980902130000 | 1998-09-02 13:00 | 556.844 |  | 1.997 | 149.366 | 152.47 | 151.741 | 148.758 |  | 1151.95 | 1259.536 |  | 6.2073 | 6.4668 | 7.0083 | 6.623 | 6.1257 | 6.1738 | 6.0562 | 6.0403 | 50.7014 | 0.045631 |  | 62.069 | 100
19980902133000 | 1998-09-02 13:30 | 577.317 |  | 4.57 | 149.426 | 151.65 | 152.029 | 148.185 |  | 1160.783 | 1266.703 |  | 6.2104 | 6.4553 | 7.0259 | 6.604 | 6.1257 | 6.1333 | 6.0266 | 6.0281 | 50.6093 | 0.045548 |  | 62.069 | 100
19980902140000 | 1998-09-02 14:00 | 572.756 |  | 1.606 | 148.613 | 151.728 | 151.259 | 148.51 |  | 1170.534 | 1270.62 |  | 6.2844 | 6.5393 | 7.0984 | 6.6909 | 6.1936 | 6.1882 | 6.0715 | 6.1013 | 51.1676 | 0.046051 |  | 62.069 | 100
19980902143000 | 1998-09-02 14:30 | 572.441 |  | 4.939 | 148.895 | 150.619 | 151.293 | 148.392 |  | 1175.867 | 1277.787 |  | 6.2852 | 6.5408 | 7.1289 | 6.7207 | 6.208 | 6.2051 | 6.0913 | 6.1172 | 51.2972 | 0.046167 |  | 62.069 | 100
19980902150000 | 1998-09-02 15:00 | 567.618 |  | 1.381 | 147.747 | 151.284 | 150.079 | 148.809 |  | 1092.281 | 1187.117 |  | 5.9875 | 6.2393 | 6.7124 | 6.3318 | 5.8953 | 5.8801 | 5.7703 | 5.8052 | 48.6219 | 0.04376 |  | 62.069 | 100
19980902153000 | 1998-09-02 15:30 | 480.272 |  | 2.981 | 147.793 | 149.345 | 150.015 | 145.88 |  | 967.528 | 1048.947 |  | 5.4207 | 5.6252 | 6.0417 | 5.5847 | 5.375 | 5.4131 | 5.3054 | 5.2415 | 44.0073 | 0.039607 |  | 62.069 | 100
19980902160000 | 1998-09-02 16:00 | 478.07 |  | 0.645 | 147.682 | 150.232 | 149.847 | 148.004 |  | 938.444 | 1013.446 |  | 5.2566 | 5.4666 | 5.8181 | 5.3499 | 5.2163 | 5.2659 | 5.1628 | 5.0928 | 42.629 | 0.038366 |  | 62.069 | 100
19980902163000 | 1998-09-02 16:30 | 443.074 |  | 2.366 | 148.163 | 151.95 | 150.612 | 149.969 |  | 842.941 | 907.859 |  | 4.7593 | 4.9607 | 5.1887 | 4.7151 | 4.7166 | 4.7676 | 4.6777 | 4.5967 | 38.3824 | 0.034544 |  | 62.069 | 100
19980902170000 | 1998-09-02 17:00 | 427.004 |  | 0.322 | 148.182 | 150.154 | 150.648 | 148.174 |  | 840.191 | 904.026 |  | 4.6875 | 4.8562 | 5.085 | 4.6516 | 4.6426 | 4.7295 | 4.6365 | 4.5388 | 37.8277 | 0.034045 |  | 62.069 | 100
19980902173000 | 1998-09-02 17:30 | 421.106 |  | 2.978 | 148.283 | 151.547 | 150.687 | 150.062 |  | 826.607 | 896.276 |  | 4.6777 | 4.8599 | 5.0491 | 4.6218 | 4.6265 | 4.7402 | 4.6433 | 4.5327 | 37.7512 | 0.033976 |  | 62.069 | 100
19980902180000 | 1998-09-02 18:00 | 453.376 |  | 0.648 | 148.594 | 151.954 | 151.303 | 148.983 |  | 929.693 | 1008.612 |  | 5.175 | 5.4109 | 5.7205 | 5.2827 | 5.1216 | 5.262 | 5.1499 | 4.9951 | 42.1177 | 0.037906 |  | 62.069 | 100
19980902183000 | 1998-09-02 18:30 | 524.181 |  | 5.183 | 150.087 | 152.774 | 152.338 | 150.299 |  | 1035.196 | 1125.282 |  | 5.6221 | 5.8608 | 6.2935 | 5.8687 | 5.5771 | 5.6252 | 5.51 | 5.468 | 45.8254 | 0.041243 |  | 62.069 | 100
19980902190000 | 1998-09-02 19:00 | 504.966 |  | 2.364 | 149.372 | 151.846 | 151.763 | 148.876 |  | 988.362 | 1070.947 |  | 5.3391 | 5.5505 | 5.9319 | 5.4475 | 5.262 | 5.2705 | 5.1797 | 5.1538 | 43.135 | 0.038821 |  | 62.069 | 100
19980902193000 | 1998-09-02 19:30 | 413.058 |  | 2.98 | 147.82 | 149.788 | 150.308 | 147.066 |  | 841.941 | 917.276 |  | 4.8394 | 5.0081 | 5.2644 | 4.8164 | 4.7805 | 4.876 | 4.7822 | 4.6724 | 39.0394 | 0.035135 |  | 62.069 | 100
19980902200000 | 1998-09-02 20:00 | 423.78 |  | 0.769 | 147.713 | 151.455 | 150.027 | 148.979 |  | 835.191 | 911.776 |  | 4.7119 | 4.8958 | 5.1025 | 4.6594 | 4.686 | 4.7607 | 4.6584 | 4.5625 | 38.0372 | 0.034233 |  | 62.069 | 100
19980902203000 | 1998-09-02 20:30 | 364.064 |  | 3.837 | 148.513 | 151.222 | 150.983 | 148.994 |  | 734.354 | 801.023 |  | 4.2839 | 4.4312 | 4.5625 | 4.103 | 4.2505 | 4.3809 | 4.2908 | 4.126 | 34.4288 | 0.030986 |  | 62.069 | 100
19980902210000 | 1998-09-02 21:00 | 355.806 |  | 0.08 | 148.031 | 151.248 | 150.42 | 149.763 |  | 704.687 | 757.688 |  | 4.0161 | 4.1536 | 4.1726 | 3.7805 | 3.9567 | 4.155 | 4.0627 | 3.8735 | 32.1707 | 0.028954 |  | 62.069 | 100
19980902213000 | 1998-09-02 21:30 | 344.298 |  | 12.527 | 148.279 | 151.196 | 150.934 | 149.711 |  | 676.936 | 740.605 |  | 3.9148 | 4.0613 | 4.0742 | 3.6554 | 3.8751 | 4.0635 | 3.9735 | 3.7775 | 31.3953 | 0.028256 |  | 62.069 | 100
19980902220000 | 1998-09-02 22:00 | 347.47 |  | 0.203 | 148.62 | 150.779 | 150.718 | 149.788 |  | 692.27 | 740.521 |  | 3.9254 | 4.0413 | 4.0635 | 3.6263 | 3.8674 | 4.0283 | 3.9521 | 3.7583 | 31.2626 | 0.028136 |  | 62.069 | 100
19980902223000 | 1998-09-02 22:30 | 337.325 |  | 13.631 | 148.566 | 151.078 | 151.152 | 149.345 |  | 702.854 | 734.021 |  | 3.9735 | 4.104 | 4.136 | 3.724 | 3.9231 | 4.0825 | 4.0161 | 3.8118 | 31.771 | 0.028594 |  | 62.069 | 100
19980902230000 | 1998-09-02 23:00 | 336.88 |  | 10.085 | 148.826 | 152.171 | 151.198 | 150.934 |  | 704.937 | 733.521 |  | 3.9674 | 4.0925 | 4.1406 | 3.7141 | 3.9323 | 4.0559 | 4.0193 | 3.8118 | 31.7339 | 0.028561 |  | 62.069 | 100
19980902233000 | 1998-09-02 23:30 | 343.827 |  | 10.455 | 148.618 | 151.702 | 151.435 | 150.712 |  | 697.853 | 723.187 |  | 3.9277 | 4.0742 | 4.0925 | 3.6637 | 3.8918 | 4.001 | 3.9811 | 3.7942 | 31.4262 | 0.028284 |  | 62.069 | 100
19980903000000 | 1998-09-03 | 342.227 |  | 0.937 | 149.006 | 151.377 | 151.156 | 149.149 |  | 707.854 | 732.521 |  | 3.9475 | 4.0535 | 4.103 | 3.6829 | 3.8956 | 3.9719 | 3.9689 | 3.782 | 31.4053 | 0.028265 |  | 62.069 | 100
19980903003000 | 1998-09-03 00:30 | 341.336 |  | 15.619 | 149.116 | 150.232 | 151.28 | 150.479 |  | 711.77 | 746.105 |  | 3.9872 | 4.1108 | 4.1794 | 3.7179 | 3.9491 | 3.9918 | 4.0146 | 3.8217 | 31.7725 | 0.028595 |  | 62.069 | 100
19980903010000 | 1998-09-03 01:00 | 336.355 |  | 0.571 | 149.101 | 151.872 | 151.748 | 150.634 |  | 731.854 | 759.772 |  | 4.0222 | 4.1443 | 4.2268 | 3.7705 | 3.988 | 4.0308 | 4.0527 | 3.8552 | 32.0905 | 0.028881 |  | 62.069 | 100
19980903013000 | 1998-09-03 01:30 | 336.696 |  | 29.805 | 148.939 | 150.753 | 151.537 | 149.763 |  | 715.521 | 751.522 |  | 3.9811 | 4.0764 | 4.1536 | 3.7209 | 3.9338 | 4.0032 | 4.0125 | 3.8179 | 31.6994 | 0.028529 |  | 62.069 | 100
19980903020000 | 1998-09-03 02:00 | 342.909 |  | 0.205 | 148.474 | 150.557 | 150.901 | 149.072 |  | 720.271 | 753.772 |  | 3.9674 | 4.0742 | 4.1138 | 3.6531 | 3.9109 | 3.9545 | 3.9742 | 3.7797 | 31.4278 | 0.028285 |  | 62.069 | 100
19980903023000 | 1998-09-03 02:30 | 342.83 |  | 12.651 | 148.5 | 151.392 | 151.034 | 150.402 |  | 721.521 | 763.855 |  | 4.0291 | 4.1292 | 4.1909 | 3.7461 | 3.9681 | 4.0115 | 4.0229 | 3.8446 | 31.9424 | 0.028748 |  | 62.069 | 100
19980903030000 | 1998-09-03 03:00 | 341.86 |  | 0.817 | 148.807 | 149.216 | 151.276 | 148.721 |  | 721.687 | 756.272 |  | 4.0193 | 4.1565 | 4.2122 | 3.7919 | 3.978 | 4.0405 | 4.0566 | 3.8674 | 32.1224 | 0.02891 |  | 62.069 | 100
19980903033000 | 1998-09-03 03:30 | 336.12 |  | 17.046 | 147.656 | 150.417 | 149.951 | 149.674 |  | 712.02 | 750.938 |  | 4.0247 | 4.1772 | 4.2236 | 3.8179 | 3.9933 | 4.0642 | 4.0771 | 3.8812 | 32.2592 | 0.029033 |  | 62.069 | 100
19980903040000 | 1998-09-03 04:00 | 337.168 |  | 0.77 | 148.357 | 151.665 | 151.102 | 150.675 |  | 707.937 | 741.771 |  | 3.9613 | 4.0955 | 4.1116 | 3.6942 | 3.9078 | 3.988 | 4.0032 | 3.8163 | 31.5779 | 0.02842 |  | 62.069 | 100
19980903043000 | 1998-09-03 04:30 | 345.557 |  | 11.794 | 148.762 | 151.433 | 151.242 | 150.938 |  | 697.437 | 735.021 |  | 3.9491 | 4.071 | 4.0986 | 3.6859 | 3.9041 | 3.9658 | 3.9766 | 3.7897 | 31.4408 | 0.028297 |  | 62.069 | 100
19980903050000 | 1998-09-03 05:00 | 348.073 |  | 0.325 | 148.965 | 150.288 | 151.386 | 149.545 |  | 724.937 | 757.855 |  | 3.9773 | 4.0847 | 4.1528 | 3.7019 | 3.9308 | 3.9949 | 4.0002 | 3.8285 | 31.6711 | 0.028504 |  | 62.069 | 100
19980903053000 | 1998-09-03 05:30 | 340.707 |  | 9.703 | 148.699 | 151.315 | 151.179 | 149.829 |  | 729.438 | 779.689 |  | 4.0315 | 4.1978 | 4.2329 | 3.8376 | 3.9902 | 4.0718 | 4.0786 | 3.8857 | 32.3261 | 0.029093 |  | 62.069 | 100
19980903060000 | 1998-09-03 06:00 | 337.273 |  | 0.402 | 148.839 | 152.212 | 151.318 | 150.974 |  | 733.854 | 768.189 |  | 4.0002 | 4.1755 | 4.187 | 3.7874 | 3.9613 | 4.0444 | 4.0559 | 3.8698 | 32.0815 | 0.028873 |  | 62.069 | 100
19980903063000 | 1998-09-03 06:30 | 342.149 |  | 10.204 | 148.673 | 151.119 | 150.85 | 149.633 |  | 705.687 | 746.021 |  | 4.0315 | 4.2268 | 4.2634 | 3.8857 | 2.8062 | 4.1177 | 4.1321 | 3.9277 | 31.3911 | 0.028252 |  | 62.069 | 100
19980903070000 | 1998-09-03 07:00 | 426.952 |  | 0.525 | 148.507 | 153.697 | 150.792 | 151.222 |  | 856.358 | 921.11 |  | 5.0073 | 5.2224 | 5.4658 | 5.0623 | 3.3418 | 4.9819 | 4.928 | 4.8569 | 38.8664 | 0.03498 |  | 62.069 | 100
19980903073000 | 1998-09-03 07:30 | 430.255 |  | 5.437 | 149.894 | 151.196 | 152.243 | 149.959 |  | 861.358 | 934.693 |  | 4.9927 | 5.2048 | 5.4429 | 5.0483 | 3.3174 | 4.9851 | 4.895 | 4.8257 | 38.7119 | 0.034841 |  | 62.069 | 100
19980903080000 | 1998-09-03 08:00 | 464.334 |  | 0.653 | 148.906 | 151.614 | 151.407 | 148.148 |  | 928.193 | 1004.112 |  | 5.3535 | 5.5779 | 5.9082 | 5.5215 | 3.5707 | 5.3291 | 5.2217 | 5.198 | 41.6806 | 0.037513 |  | 62.069 | 100
19980903083000 | 1998-09-03 08:30 | 565.232 |  | 9.465 | 149.569 | 153.775 | 151.882 | 151.547 |  | 1171.784 | 1278.953 |  | 6.408 | 6.6858 | 7.251 | 6.9214 | 4.2871 | 6.3552 | 6.2349 | 6.2546 | 50.398 | 0.045358 |  | 62.069 | 100
19980903090000 | 1998-09-03 09:00 | 578.916 |  | 1.882 | 150.294 | 152.171 | 152.877 | 149.696 |  | 1143.866 | 1246.702 |  | 6.4111 | 6.6826 | 7.2563 | 6.8794 | 4.2756 | 6.3103 | 6.1997 | 6.2324 | 50.2474 | 0.045223 |  | 62.069 | 100
19980903093000 | 1998-09-03 09:30 | 576.426 |  | 25.457 | 148.766 | 151.351 | 151.212 | 148.628 |  | 1157.7 | 1262.786 |  | 6.5767 | 6.813 | 7.4478 | 7.0664 | 4.3809 | 6.4431 | 6.3232 | 6.3599 | 51.411 | 0.04627 |  | 62.069 | 100
19980903100000 | 1998-09-03 10:00 | 572.599 |  | 2.742 | 148.391 | 151.31 | 150.85 | 148.588 |  | 1155.033 | 1256.786 |  | 6.3691 | 6.6636 | 7.229 | 5.6748 | 6.2988 | 6.2959 | 6.1714 | 6.2209 | 50.9235 | 0.045831 |  | 62.069 | 100
19980903103000 | 1998-09-03 10:30 | 573.044 |  | 8.863 | 148.338 | 152.6 | 151.06 | 149.134 |  | 1150.116 | 1250.619 |  | 6.2654 | 6.5332 | 7.0854 | 6.6414 | 6.1929 | 6.1692 | 6.0486 | 6.0815 | 51.0176 | 0.045916 |  | 62.069 | 100
19980903110000 | 1998-09-03 11:00 | 575.692 |  | 1.023 | 148.889 | 152.378 | 151.402 | 149.16 |  | 1149.2 | 1247.203 |  | 6.2288 | 6.4988 | 7.0581 | 6.6223 | 6.1616 | 6.1548 | 6.0356 | 6.0608 | 50.8208 | 0.045739 |  | 62.069 | 100
19980903113000 | 1998-09-03 11:30 | 577.343 |  | 10.454 | 148.744 | 152.079 | 151.331 | 149.356 |  | 1157.117 | 1257.786 |  | 6.2622 | 6.5498 | 7.106 | 6.6704 | 6.208 | 6.2043 | 6.0798 | 6.106 | 51.1865 | 0.046068 |  | 62.069 | 100
19980903120000 | 1998-09-03 12:00 | 577.894 |  | 0.779 | 148.832 | 151.259 | 151.351 | 148.783 |  | 1166.283 | 1259.286 |  | 6.2769 | 6.5605 | 7.1182 | 6.7063 | 6.2148 | 6.2119 | 6.0945 | 6.1165 | 51.2996 | 0.04617 |  | 62.069 | 100
19980903123000 | 1998-09-03 12:30 | 643.875 |  | 7.39 | 149.079 | 153.734 | 151.753 | 150.516 |  | 1292.12 | 1413.457 |  | 6.9551 | 7.2351 | 7.9614 | 7.5486 | 6.9185 | 6.8574 | 6.7354 | 6.7458 | 56.9573 | 0.051262 |  | 62.069 | 100
19980903130000 | 1998-09-03 13:00 | 655.069 |  | 1.632 | 149.635 | 152.249 | 152.229 | 148.783 |  | 1301.121 | 1430.208 |  | 6.9893 | 7.293 | 8.001 | 7.6074 | 6.9458 | 6.8887 | 6.7666 | 6.7932 | 57.285 | 0.051556 |  | 62.069 | 100
19980903133000 | 1998-09-03 13:30 | 651.504 |  | 10.205 | 148.743 | 152.027 | 151.248 | 148.314 |  | 1293.954 | 1420.457 |  | 6.9778 | 7.2998 | 8.0068 | 7.6257 | 6.9429 | 6.897 | 6.7817 | 6.8086 | 57.3403 | 0.051606 |  | 62.069 | 100
19980903140000 | 1998-09-03 14:00 | 575.482 |  | 0.565 | 148.184 | 150.372 | 150.362 | 146.907 |  | 1111.032 | 1208.285 |  | 6.1401 | 6.4033 | 6.9734 | 6.5017 | 6.0913 | 6.0356 | 5.9272 | 5.967 | 50.0396 | 0.045036 |  | 62.069 | 100
19980903143000 | 1998-09-03 14:30 | 493.956 |  | 9.117 | 146.87 | 150.124 | 148.955 | 147.154 |  | 935.36 | 1012.862 |  | 5.2537 | 5.4092 | 5.803 | 5.2651 | 5.207 | 5.156 | 5.0613 | 5.0271 | 42.1824 | 0.037964 |  | 62.069 | 100
19980903150000 | 1998-09-03 15:00 | 438.88 |  | 0.076 | 147.306 | 150.789 | 149.516 | 149.057 |  | 850.524 | 908.526 |  | 4.8157 | 4.9478 | 5.2505 | 4.7112 | 4.7783 | 4.7876 | 4.686 | 4.6067 | 38.5838 | 0.034725 |  | 62.069 | 100
19980903153000 | 1998-09-03 15:30 | 416.545 |  | 8.123 | 148.22 | 150.675 | 150.419 | 148.2 |  | 837.107 | 900.443 |  | 4.731 | 4.9377 | 5.1277 | 4.7097 | 4.7166 | 4.8013 | 4.7012 | 4.5801 | 38.3053 | 0.034475 |  | 62.069 | 100
19980903160000 | 1998-09-03 16:00 | 412.508 |  | 20.611 | 148.508 | 150.376 | 150.929 | 149.138 |  | 844.608 | 906.193 |  | 4.7126 | 4.9058 | 5.1111 | 4.699 | 4.6799 | 4.7944 | 4.689 | 4.5776 | 38.1694 | 0.034352 |  | 62.069 | 100
19980903163000 | 1998-09-03 16:30 | 368.022 |  | 31.96 | 148.699 | 150.845 | 151.409 | 149.608 |  | 756.188 | 794.856 |  | 4.2383 | 4.3777 | 4.5007 | 4.0405 | 4.2222 | 4.3457 | 4.2617 | 4.084 | 34.0708 | 0.030664 |  | 62.069 | 100
19980903170000 | 1998-09-03 17:00 | 367.55 |  | 0.199 | 148.073 | 150.402 | 150.364 | 148.669 |  | 769.189 | 806.44 |  | 4.1978 | 4.3313 | 4.4297 | 3.9597 | 4.1572 | 4.2922 | 4.1938 | 4.0186 | 33.5803 | 0.030222 |  | 62.069 | 100
19980903173000 | 1998-09-03 17:30 | 358.742 |  | 12.044 | 148.252 | 151.495 | 150.563 | 150.01 |  | 749.605 | 796.273 |  | 4.2168 | 4.3572 | 4.4563 | 4.0071 | 4.1946 | 4.3245 | 4.2336 | 4.0535 | 33.8436 | 0.030459 |  | 62.069 | 100
19980903180000 | 1998-09-03 18:00 | 470.625 |  | 1.387 | 149.278 | 152.929 | 151.624 | 151.691 |  | 982.112 | 1070.781 |  | 5.2742 | 5.5208 | 5.8564 | 5.426 | 5.2605 | 5.323 | 5.2124 | 5.1233 | 42.9966 | 0.038697 |  | 62.069 | 100
19980903183000 | 1998-09-03 18:30 | 475.973 |  | 8.733 | 149.801 | 151.351 | 152.252 | 149.866 |  | 943.11 | 1037.113 |  | 5.2109 | 5.4536 | 5.7922 | 5.3384 | 5.2017 | 5.2476 | 5.1445 | 5.0796 | 42.4685 | 0.038222 |  | 62.069 | 100
19980903190000 | 1998-09-03 19:00 | 435.445 |  | 0.077 | 148.456 | 150.675 | 151.298 | 149.438 |  | 843.024 | 906.526 |  | 4.7012 | 4.895 | 5.1057 | 4.6243 | 4.6616 | 4.6838 | 4.583 | 4.5151 | 37.7697 | 0.033993 |  | 62.069 | 100
19980903193000 | 1998-09-03 19:30 | 370.355 |  | 12.544 | 148.219 | 151.588 | 150.512 | 149.855 |  | 785.106 | 840.941 |  | 4.3755 | 4.5532 | 4.6846 | 4.2573 | 4.3618 | 4.4724 | 4.3816 | 4.2283 | 35.3147 | 0.031783 |  | 62.069 | 100
19980903200000 | 1998-09-03 20:00 | 371.981 |  | 0.199 | 148.135 | 150.494 | 150.597 | 149.504 |  | 772.105 | 824.524 |  | 4.2588 | 4.4465 | 4.5303 | 4.1274 | 4.2351 | 4.3855 | 4.2947 | 4.1375 | 34.4158 | 0.030974 |  | 62.069 | 100
19980903203000 | 1998-09-03 20:30 | 345.452 |  | 9.22 | 148.247 | 151.51 | 150.569 | 150.025 |  | 709.104 | 747.605 |  | 3.8972 | 4.0352 | 4.043 | 3.6088 | 3.8575 | 3.9872 | 3.9078 | 3.7172 | 31.0539 | 0.027949 |  | 62.069 | 100
19980903210000 | 1998-09-03 21:00 | 349.2 |  | 0.323 | 148.371 | 150.845 | 150.768 | 149.608 |  | 732.438 | 770.605 |  | 4.0261 | 4.1436 | 4.1672 | 3.7332 | 3.9667 | 4.1123 | 4.0215 | 3.8484 | 32.019 | 0.028817 |  | 62.069 | 100
19980903213000 | 1998-09-03 21:30 | 334.809 |  | 10.074 | 148.635 | 148.695 | 151.037 | 148.2 |  | 699.187 | 744.438 |  | 3.9628 | 4.1177 | 4.1116 | 3.7209 | 3.9323 | 4.1047 | 4.02 | 3.8254 | 31.7954 | 0.028616 |  | 62.069 | 100
19980903220000 | 1998-09-03 22:00 | 338.689 |  | 1.181 | 147.393 | 149.685 | 149.828 | 149.19 |  | 690.186 | 722.521 |  | 3.8857 | 4.0229 | 4.0176 | 3.576 | 3.8599 | 4.0139 | 3.9437 | 3.7347 | 31.0544 | 0.027949 |  | 62.069 | 100
19980903223000 | 1998-09-03 22:30 | 338.977 |  | 7.622 | 148.098 | 152.109 | 150.374 | 150.871 |  | 683.103 | 712.687 |  | 3.8629 | 3.9796 | 3.9895 | 3.5394 | 3.8254 | 3.9475 | 3.9033 | 3.6866 | 30.7342 | 0.027661 |  | 62.069 | 100
19980903230000 | 1998-09-03 23:00 | 335.543 |  | 0.323 | 148.841 | 150.949 | 151.384 | 150.206 |  | 694.103 | 718.604 |  | 3.9125 | 4.0581 | 4.0505 | 3.631 | 3.8789 | 3.9902 | 3.9636 | 3.7637 | 31.2485 | 0.028124 |  | 62.069 | 100
19980903233000 | 1998-09-03 23:30 | 331.427 |  | 13.149 | 148.563 | 151.119 | 151.205 | 150.624 |  | 689.27 | 720.687 |  | 3.901 | 4.0444 | 4.0542 | 3.6538 | 3.8766 | 3.9705 | 3.9712 | 3.7736 | 31.2453 | 0.028121 |  | 62.069 | 100
19980904000000 | 1998-09-04 | 327.259 |  | 20.695 | 148.92 | 151.758 | 151.266 | 150.52 |  | 692.437 | 714.354 |  | 3.8804 | 4.0229 | 4.0115 | 3.5905 | 3.8461 | 3.9285 | 3.9346 | 3.7339 | 30.9484 | 0.027854 |  | 62.069 | 100
19980904003000 | 1998-09-04 00:30 | 331.925 |  | 8.49 | 148.783 | 151.015 | 151.068 | 150.025 |  | 689.52 | 725.437 |  | 3.9231 | 4.0437 | 4.0735 | 3.6279 | 3.8942 | 3.9392 | 3.9491 | 3.7552 | 31.2059 | 0.028085 |  | 62.069 | 100
19980904010000 | 1998-09-04 01:00 | 330.903 |  | 0.323 | 148.823 | 150.989 | 151.16 | 150.247 |  | 701.77 | 729.604 |  | 3.9414 | 4.0542 | 4.1069 | 3.6432 | 3.9078 | 3.9545 | 3.9651 | 3.7728 | 31.3459 | 0.028211 |  | 62.069 | 100
19980904013000 | 1998-09-04 01:30 | 328.229 |  | 9.1 | 148.486 | 150.964 | 151.419 | 150.469 |  | 689.52 | 721.021 |  | 3.8499 | 4.0115 | 3.9902 | 3.5859 | 3.8247 | 3.9064 | 3.9139 | 3.7179 | 30.8004 | 0.02772 |  | 62.069 | 100
19980904020000 | 1998-09-04 02:00 | 334.704 |  | 0.199 | 148.736 | 151.64 | 151.394 | 150.402 |  | 704.52 | 719.687 |  | 3.9155 | 4.0237 | 4.0491 | 3.5974 | 3.8621 | 3.9193 | 3.9224 | 3.7324 | 31.0219 | 0.02792 |  | 62.069 | 100
19980904023000 | 1998-09-04 02:30 | 329.304 |  | 9.592 | 149.422 | 150.964 | 151.286 | 149.478 |  | 709.937 | 740.188 |  | 3.9399 | 4.0725 | 4.1162 | 3.6829 | 3.9155 | 3.9536 | 3.9651 | 3.7813 | 31.427 | 0.028284 |  | 62.069 | 100
19980904030000 | 1998-09-04 03:00 | 324.795 |  | 6.55 | 148.624 | 150.118 | 151.02 | 149.623 |  | 712.854 | 759.855 |  | 4.1558 | 4.2976 | 4.3518 | 3.9392 | 4.1001 | 4.1565 | 2.8894 | 3.9841 | 31.8745 | 0.028687 |  | 62.069 | 100
19980904033000 | 1998-09-04 03:30 | 329.54 |  | 16.725 | 149.044 | 151.067 | 151.36 | 150.572 |  | 695.937 | 744.105 |  | 4.0085 | 4.1611 | 4.2114 | 3.7958 | 3.9933 | 4.0505 | 2.8024 | 3.8674 | 30.8904 | 0.027801 |  | 62.069 | 100
19980904040000 | 1998-09-04 04:00 | 327.285 |  | 8.774 | 148.691 | 151.939 | 151.499 | 149.959 |  | 711.187 | 764.605 |  | 4.1223 | 4.2617 | 4.3411 | 3.9078 | 2.7566 | 4.1611 | 4.1726 | 3.9667 | 31.6899 | 0.028521 |  | 62.069 | 100
19980904043000 | 1998-09-04 04:30 | 331.296 |  | 3.465 | 149.09 | 150.206 | 151.265 | 149.959 |  | 711.77 | 751.355 |  | 4.0146 | 4.1702 | 3.5547 | 3.7988 | 3.9933 | 4.0559 | 4.0718 | 3.869 | 31.5283 | 0.028375 |  | 62.069 | 100
19980904050000 | 1998-09-04 05:00 | 327.731 |  | 0.445 | 148.413 | 150.923 | 151.082 | 150.428 |  | 698.27 | 764.605 |  | 3.9017 | 4.0681 | 4.0588 | 3.6493 | 3.8965 | 3.978 | 3.9742 | 3.7805 | 31.3071 | 0.028176 |  | 62.069 | 100
19980904053000 | 1998-09-04 05:30 | 331.113 |  | 7.639 | 148.556 | 151.392 | 151.028 | 150.154 |  | 695.103 | 760.272 |  | 3.9094 | 4.0574 | 4.0588 | 3.6416 | 3.8926 | 3.9545 | 3.9697 | 3.7675 | 31.2515 | 0.028126 |  | 62.069 | 100
19980904060000 | 1998-09-04 06:00 | 333.682 |  | 1.306 | 148.272 | 150.273 | 150.843 | 148.788 |  | 699.77 | 753.688 |  | 3.9071 | 4.1055 | 4.0635 | 3.7034 | 3.9003 | 3.9963 | 4.0107 | 3.8087 | 31.4955 | 0.028346 |  | 62.069 | 100
19980904063000 | 1998-09-04 06:30 | 333.262 |  | 25.01 | 148.552 | 152.109 | 150.952 | 150.624 |  | 691.02 | 726.604 |  | 3.8599 | 4.0063 | 3.9895 | 3.5829 | 3.8423 | 3.9102 | 3.9301 | 3.7125 | 30.8337 | 0.02775 |  | 62.069 | 100
19980904070000 | 1998-09-04 07:00 | 365.82 |  | 0.405 | 148.879 | 152.748 | 151.371 | 152.253 |  | 738.771 | 781.189 |  | 4.1672 | 4.3313 | 4.4128 | 3.959 | 4.1611 | 4.1833 | 4.1855 | 4.0078 | 33.408 | 0.030067 |  | 62.069 | 100
19980904073000 | 1998-09-04 07:30 | 498.386 |  | 7.869 | 149.599 | 154.182 | 151.89 | 151.954 |  | 1023.946 | 1138.949 |  | 5.5093 | 5.7893 | 6.167 | 5.7581 | 5.5061 | 5.5161 | 5.4702 | 5.3887 | 45.1048 | 0.040594 |  | 62.069 | 100
19980904080000 | 1998-09-04 08:00 | 525.36 |  | 0.403 | 150.622 | 152.083 | 153.267 | 150.103 |  | 1061.447 | 1179.951 |  | 5.8396 | 6.0898 | 6.5454 | 6.1365 | 5.8152 | 5.7739 | 5.6931 | 5.6611 | 47.5546 | 0.042799 |  | 62.069 | 100
19980904083000 | 1998-09-04 08:30 | 582.901 |  | 9.594 | 149.36 | 152.593 | 151.768 | 149.623 |  | 1176.117 | 1290.787 |  | 6.385 | 6.6636 | 7.2434 | 6.8413 | 6.3491 | 6.3118 | 6.2271 | 6.2012 | 52.2225 | 0.047 |  | 62.069 | 100
19980904090000 | 1998-09-04 09:00 | 588.511 |  | 0.282 | 149.239 | 151.691 | 151.847 | 148.968 |  | 1175.7 | 1291.454 |  | 6.3606 | 6.6392 | 7.1985 | 6.8191 | 6.3293 | 6.2769 | 6.2043 | 6.1929 | 52.0208 | 0.046819 |  | 62.069 | 100
19980904093000 | 1998-09-04 09:30 | 584.028 |  | 2.612 | 148.655 | 151.433 | 151.223 | 147.968 |  | 1167.7 | 1285.704 |  | 6.343 | 6.6238 | 7.1992 | 6.7896 | 6.3186 | 6.2654 | 6.1914 | 6.1799 | 51.9109 | 0.04672 |  | 62.069 | 100
19980904100000 | 1998-09-04 10:00 | 583.53 |  | 0.16 | 148.769 | 151.562 | 151.11 | 148.344 |  | 1167.867 | 1283.953 |  | 6.3333 | 6.6177 | 7.1641 | 6.7537 | 6.3049 | 6.2561 | 6.1714 | 6.1509 | 51.7521 | 0.046577 |  | 62.069 | 100
19980904103000 | 1998-09-04 10:30 | 585.444 |  | 1.755 | 148.849 | 151.887 | 151.107 | 148.669 |  | 1173.284 | 1292.704 |  | 6.3745 | 6.6399 | 7.2358 | 6.8062 | 6.3408 | 6.282 | 6.1975 | 6.186 | 52.0627 | 0.046856 |  | 62.069 | 100
19980904110000 | 1998-09-04 11:00 | 585.968 |  | 0.158 | 148.412 | 152.016 | 151.111 | 148.798 |  | 1176.534 | 1294.704 |  | 6.3691 | 6.6338 | 7.2053 | 6.804 | 6.3301 | 6.2744 | 6.1997 | 6.1746 | 51.991 | 0.046792 |  | 62.069 | 100
19980904113000 | 1998-09-04 11:30 | 588.144 |  | 1.872 | 148.959 | 151.536 | 151.172 | 148.071 |  | 1174.617 | 1288.537 |  | 6.3247 | 6.6079 | 7.1777 | 6.7673 | 6.2942 | 6.2524 | 6.1775 | 6.1677 | 51.7694 | 0.046592 |  | 62.069 | 100
19980904120000 | 1998-09-04 12:00 | 585.444 |  | 0.077 | 148.693 | 151.34 | 151.125 | 148.618 |  | 1171.367 | 1288.454 |  | 6.3186 | 6.6011 | 7.1687 | 6.7749 | 6.2974 | 6.2485 | 6.1638 | 6.1531 | 51.7261 | 0.046553 |  | 62.069 | 100
19980904123000 | 1998-09-04 12:30 | 587.619 |  | 1.503 | 148.671 | 151.758 | 151.11 | 148.293 |  | 1158.533 | 1276.453 |  | 6.302 | 6.5688 | 7.1565 | 6.739 | 6.2585 | 6.2173 | 6.1401 | 6.1272 | 51.5094 | 0.046358 |  | 62.069 | 100
19980904130000 | 1998-09-04 13:00 | 576.426 |  | 0.079 | 148.831 | 151.433 | 150.993 | 148.463 |  | 1129.699 | 1237.369 |  | 6.1074 | 6.3569 | 6.8718 | 6.4553 | 6.0562 | 5.9922 | 5.9158 | 5.9021 | 49.6577 | 0.044692 |  | 62.069 | 100
19980904133000 | 1998-09-04 13:30 | 541.928 |  | 1.878 | 147.892 | 151.03 | 150.175 | 147.318 |  | 1091.281 | 1199.868 |  | 5.9189 | 6.1096 | 6.6873 | 6.1548 | 5.8999 | 5.8191 | 5.79 | 5.7021 | 48.0817 | 0.043274 |  | 62.069 | 100
19980904140000 | 1998-09-04 14:00 | 541.587 |  | 12.256 | 148.517 | 151.825 | 150.704 | 148.854 |  | 1094.615 | 1199.868 |  | 6.0439 | 6.5017 | 6.8284 | 6.6238 | 5.9656 | 4.2825 | 5.9167 | 6.0654 | 48.228 | 0.043405 |  | 62.069 | 100
19980904143000 | 1998-09-04 14:30 | 490.102 |  | 12.347 | 148.816 | 149.752 | 150.969 | 147.772 |  | 968.111 | 1065.114 |  | 5.2239 | 5.6533 | 5.8594 | 5.5872 | 5.1682 | 5.3879 | 5.1614 | 5.2856 | 43.3269 | 0.038994 |  | 62.069 | 100
19980904150000 | 1998-09-04 15:00 | 440.583 |  | 0 | 147.31 | 150.144 | 149.579 | 147.668 |  | 893.942 | 983.195 |  | 4.8713 | 5.2964 | 5.4199 | 5.1277 | 4.8225 | 5.0874 | 4.8462 | 4.9302 | 40.4016 | 0.036361 |  | 62.069 | 100
19980904153000 | 1998-09-04 15:30 | 440.688 |  | 1.869 | 148.708 | 152.619 | 150.919 | 151.134 |  | 906.193 | 1006.112 |  | 4.8914 | 5.2476 | 5.4207 | 5.0745 | 4.8164 | 5.0347 | 4.8293 | 4.8721 | 40.1867 | 0.036168 |  | 62.069 | 100
19980904160000 | 1998-09-04 16:00 | 439.273 |  | 0 | 149.249 | 150.262 | 151.765 | 147.787 |  | 909.943 | 1006.196 |  | 4.908 | 5.2437 | 5.439 | 5.0667 | 4.8203 | 5.0347 | 4.8354 | 4.873 | 40.2208 | 0.036199 |  | 62.069 | 100
19980904163000 | 1998-09-04 16:30 | 440.636 |  | 2.24 | 148.252 | 150.469 | 150.604 | 148.488 |  | 907.776 | 1005.196 |  | 4.8943 | 5.2476 | 5.4321 | 5.0691 | 4.8188 | 5.0325 | 4.8372 | 4.8691 | 40.2007 | 0.036181 |  | 62.069 | 100
19980904170000 | 1998-09-04 17:00 | 437.045 |  | 0 | 148.509 | 151.758 | 150.858 | 150.025 |  | 911.526 | 1003.612 |  | 4.8835 | 5.2429 | 5.4253 | 5.0684 | 4.8135 | 5.04 | 4.8347 | 4.8652 | 40.1735 | 0.036156 |  | 62.069 | 100
19980904173000 | 1998-09-04 17:30 | 442.366 |  | 1.626 | 149.091 | 149.164 | 151.221 | 148.422 |  | 888.776 | 985.195 |  | 4.8843 | 5.2231 | 5.4146 | 5.0386 | 4.8074 | 5.0203 | 4.8149 | 4.8538 | 40.057 | 0.036051 |  | 62.069 | 100
19980904180000 | 1998-09-04 18:00 | 532.832 |  | 0.079 | 147.84 | 153.073 | 150.398 | 150.845 |  | 1079.781 | 1191.951 |  | 5.8181 | 6.2751 | 6.6108 | 6.3745 | 5.7258 | 5.9646 | 5.7251 | 5.8572 | 48.3512 | 0.043516 |  | 62.069 | 100
19980904183000 | 1998-09-04 18:30 | 631.004 |  | 2.364 | 150.741 | 153.635 | 153.448 | 150.664 |  | 1270.62 | 1398.123 |  | 6.6255 | 7.1694 | 7.6455 | 7.4524 | 6.5217 | 6.7559 | 6.4888 | 6.6895 | 55.3487 | 0.049814 |  | 62.069 | 100
19980904190000 | 1998-09-04 19:00 | 632.891 |  | 0.324 | 149.443 | 151.629 | 152.2 | 147.668 |  | 1270.536 | 1395.457 |  | 6.6003 | 7.1375 | 7.5974 | 7.4387 | 6.5095 | 6.7253 | 6.479 | 6.6467 | 55.1344 | 0.049621 |  | 62.069 | 100
19980904193000 | 1998-09-04 19:30 | 534.719 |  | 1.383 | 148.288 | 150.051 | 150.635 | 146.586 |  | 1061.614 | 1170.784 |  | 5.7976 | 6.2202 | 6.5681 | 6.2769 | 5.6794 | 5.8403 | 5.6299 | 5.7869 | 47.7993 | 0.043019 |  | 62.069 | 100
19980904200000 | 1998-09-04 20:00 | 530.079 |  | 0 | 147.401 | 151.366 | 149.465 | 148.148 |  | 1072.864 | 1176.7 |  | 5.7373 | 6.1853 | 6.5027 | 6.2471 | 5.6587 | 5.8608 | 5.6436 | 5.7717 | 47.6072 | 0.042846 |  | 62.069 | 100
19980904203000 | 1998-09-04 20:30 | 526.357 |  | 1.505 | 148.525 | 151.799 | 150.924 | 148.581 |  | 1072.031 | 1177.617 |  | 5.7039 | 6.1355 | 6.4392 | 6.1731 | 5.6145 | 5.8152 | 5.5962 | 5.7153 | 47.1929 | 0.042474 |  | 62.069 | 100
19980904210000 | 1998-09-04 21:00 | 523.657 |  | 20.644 | 148.872 | 151.459 | 151.327 | 148.736 |  | 1076.364 | 1178.284 |  | 5.738 | 6.1631 | 6.4722 | 6.2271 | 5.6526 | 5.8511 | 5.6321 | 5.7427 | 47.4789 | 0.042731 |  | 62.069 | 100
19980904213000 | 1998-09-04 21:30 | 525.675 |  | 1.873 | 148.453 | 151.943 | 151.115 | 148.23 |  | 1076.531 | 1181.867 |  | 5.7571 | 6.1936 | 6.53 | 6.2568 | 5.6755 | 5.8608 | 5.645 | 5.7649 | 47.6837 | 0.042915 |  | 62.069 | 100
19980904220000 | 1998-09-04 22:00 | 525.544 |  | 0 | 148.665 | 151.004 | 150.751 | 147.787 |  | 1065.197 | 1169.867 |  | 5.697 | 6.1082 | 6.4385 | 6.1426 | 5.6228 | 5.7961 | 5.5811 | 5.6938 | 47.0801 | 0.042372 |  | 62.069 | 100
19980904223000 | 1998-09-04 22:30 | 582.272 |  | 1.997 | 148.858 | 152.645 | 151.349 | 150.417 |  | 1165.033 | 1280.537 |  | 6.1814 | 6.675 | 7.0732 | 6.8574 | 6.0798 | 6.3013 | 6.0593 | 6.2234 | 51.4508 | 0.046306 |  | 62.069 | 100
19980904230000 | 1998-09-04 23:00 | 484.361 |  | 0 | 148.932 | 151.041 | 151.459 | 147.328 |  | 958.111 | 1047.947 |  | 5.2231 | 5.5894 | 5.864 | 5.4924 | 5.1865 | 5.3147 | 5.1133 | 5.2109 | 42.9943 | 0.038695 |  | 62.069 | 100
19980904233000 | 1998-09-04 23:30 | 476.759 |  | 1.506 | 147.643 | 150.051 | 149.469 | 148.071 |  | 926.693 | 1015.362 |  | 5.0347 | 5.4116 | 5.6138 | 5.2705 | 4.9622 | 5.1233 | 4.927 | 5.0012 | 41.3443 | 0.03721 |  | 62.069 | 100
19980905000000 | 1998-09-05 | 395.678 |  | 0 | 147.833 | 149.726 | 150.185 | 148.241 |  | 783.189 | 851.524 |  | 4.3191 | 4.6624 | 4.6777 | 4.3306 | 4.2732 | 4.4692 | 4.3091 | 4.2954 | 35.3367 | 0.031803 |  | 62.069 | 100
19980905003000 | 1998-09-05 00:30 | 336.906 |  | 2.12 | 147.746 | 148.947 | 150.128 | 148.452 |  | 703.687 | 762.855 |  | 3.8468 | 4.1108 | 4.0764 | 3.6829 | 3.8315 | 4.0818 | 3.9338 | 3.827 | 31.391 | 0.028252 |  | 62.069 | 100
19980905010000 | 1998-09-05 01:00 | 335.307 |  | 0 | 147.824 | 150.576 | 150.239 | 149.338 |  | 698.353 | 757.605 |  | 3.8636 | 4.0986 | 4.0559 | 3.6401 | 3.8254 | 4.0657 | 3.9148 | 3.7949 | 31.259 | 0.028133 |  | 62.069 | 100
19980905013000 | 1998-09-05 01:30 | 340.864 |  | 2.365 | 148.822 | 151.071 | 151.347 | 150.081 |  | 705.854 | 767.105 |  | 4.001 | 4.2947 | 2.4659 | 3.9376 | 3.9796 | 4.2336 | 4.0857 | 3.9895 | 30.9876 | 0.027889 |  | 62.069 | 100
19980905020000 | 1998-09-05 02:00 | 330.588 |  | 0 | 148.865 | 150.499 | 151.354 | 149.261 |  | 709.02 | 775.106 |  | 4.0071 | 4.281 | 3.4554 | 3.8987 | 3.9453 | 4.2251 | 4.0674 | 3.9728 | 31.8528 | 0.028668 |  | 62.069 | 100
19980905023000 | 1998-09-05 02:30 | 334.547 |  | 1.876 | 148.353 | 151.278 | 151.034 | 149.545 |  | 717.937 | 778.522 |  | 3.8743 | 4.2017 | 4.0391 | 3.827 | 3.84 | 4.1382 | 4.0039 | 3.8972 | 31.8214 | 0.028639 |  | 62.069 | 100
19980905030000 | 1998-09-05 03:00 | 339.108 |  | 0 | 148.412 | 150.783 | 151.104 | 149.05 |  | 714.187 | 786.939 |  | 3.9078 | 4.1985 | 4.0833 | 3.8102 | 3.8728 | 4.1162 | 3.9911 | 3.8888 | 31.8687 | 0.028682 |  | 62.069 | 100
19980905033000 | 1998-09-05 03:30 | 336.644 |  | 1.508 | 148.516 | 151.082 | 150.635 | 149.844 |  | 705.687 | 766.855 |  | 3.8766 | 4.1611 | 4.0481 | 3.7813 | 3.8484 | 4.0779 | 3.9758 | 3.866 | 31.6352 | 0.028472 |  | 62.069 | 100
19980905040000 | 1998-09-05 04:00 | 333.21 |  | 0 | 148.98 | 152.15 | 151.462 | 151.407 |  | 720.437 | 786.689 |  | 3.8804 | 4.1931 | 4.0359 | 3.8026 | 3.8385 | 4.0857 | 3.9888 | 3.8888 | 31.7138 | 0.028542 |  | 62.069 | 100
19980905043000 | 1998-09-05 04:30 | 331.113 |  | 2 | 149.308 | 150.886 | 151.797 | 148.906 |  | 719.271 | 783.022 |  | 3.9117 | 4.2236 | 4.0908 | 3.8484 | 3.8782 | 4.1077 | 4.0125 | 3.917 | 31.9899 | 0.028791 |  | 62.069 | 100
19980905050000 | 1998-09-05 05:00 | 335.019 |  | 20.694 | 148.304 | 151.108 | 150.741 | 149.623 |  | 719.437 | 785.939 |  | 3.9094 | 4.1895 | 4.0803 | 3.7958 | 3.8667 | 4.0588 | 3.9735 | 3.8812 | 31.7552 | 0.02858 |  | 62.069 | 100
19980905053000 | 1998-09-05 05:30 | 334.416 |  | 2.241 | 148.762 | 151.056 | 150.954 | 149.571 |  | 733.271 | 772.439 |  | 3.9117 | 4.2114 | 4.0901 | 3.8247 | 3.8789 | 4.075 | 4.0017 | 3.8956 | 31.8891 | 0.0287 |  | 62.069 | 100
19980905060000 | 1998-09-05 06:00 | 338.4 |  | 0 | 148.283 | 149.989 | 150.626 | 148.256 |  | 706.854 | 750.938 |  | 3.9261 | 4.1885 | 4.0833 | 3.8278 | 3.8636 | 4.0786 | 4.001 | 3.9109 | 31.8798 | 0.028692 |  | 62.069 | 100
19980905063000 | 1998-09-05 06:30 | 337.168 |  | 1.997 | 147.659 | 151.226 | 150.062 | 149.246 |  | 714.437 | 750.688 |  | 3.8812 | 4.1885 | 4.0664 | 3.8019 | 3.8514 | 4.0603 | 3.9766 | 3.8789 | 31.7052 | 0.028535 |  | 62.069 | 100
19980905070000 | 1998-09-05 07:00 | 341.389 |  | 0 | 149.158 | 150.783 | 151.224 | 151.03 |  | 719.521 | 756.605 |  | 3.8743 | 4.1992 | 4.0344 | 3.8179 | 3.8331 | 4.0437 | 3.9735 | 3.8812 | 31.6573 | 0.028492 |  | 62.069 | 100
19980905073000 | 1998-09-05 07:30 | 338.269 |  | 1.876 | 148.853 | 150.432 | 151.471 | 149.442 |  | 717.271 | 760.188 |  | 3.8773 | 4.1924 | 4.0535 | 3.8263 | 3.8538 | 4.0657 | 3.9918 | 3.8911 | 31.7519 | 0.028577 |  | 62.069 | 100
19980905080000 | 1998-09-05 08:00 | 479.512 |  | 0.157 | 149.254 | 153.676 | 151.524 | 151.2 |  | 1014.612 | 1104.198 |  | 5.4063 | 5.8303 | 6.0586 | 5.8357 | 5.3352 | 5.5237 | 5.3535 | 5.4192 | 44.7625 | 0.040286 |  | 62.069 | 100
19980905083000 | 1998-09-05 08:30 | 525.911 |  | 1.874 | 150.829 | 152.124 | 153.323 | 149.896 |  | 1083.114 | 1183.784 |  | 5.7129 | 6.1685 | 6.4729 | 6.2646 | 5.6497 | 5.832 | 5.6116 | 5.7305 | 47.4427 | 0.042698 |  | 62.069 | 100
19980905090000 | 1998-09-05 09:00 | 579.1 |  | 0.276 | 149.513 | 152.516 | 151.982 | 149.545 |  | 1193.284 | 1309.371 |  | 6.2271 | 6.7415 | 7.1365 | 6.9543 | 6.1477 | 6.3613 | 6.1135 | 6.2813 | 51.9632 | 0.046767 |  | 62.069 | 100
19980905093000 | 1998-09-05 09:30 | 575.404 |  | 1.629 | 149.564 | 151.928 | 151.993 | 149.205 |  | 1178.284 | 1294.787 |  | 6.1792 | 6.6858 | 7.0664 | 6.8665 | 6.0891 | 6.2959 | 6.0493 | 6.2324 | 51.4646 | 0.046318 |  | 62.069 | 100
19980905100000 | 1998-09-05 10:00 | 545.467 |  | 0 | 148.616 | 150.221 | 151.124 | 147.498 |  | 1122.449 | 1224.952 |  | 5.9028 | 6.3989 | 6.7102 | 6.5149 | 5.8252 | 6.0242 | 5.8137 | 5.9717 | 49.1616 | 0.044245 |  | 62.069 | 100
19980905103000 | 1998-09-05 10:30 | 547.852 |  | 1.629 | 148.06 | 151.81 | 150.558 | 148.344 |  | 1117.199 | 1220.785 |  | 5.8914 | 6.376 | 6.7024 | 6.5071 | 5.812 | 6.0212 | 5.7915 | 5.9434 | 49.045 | 0.04414 |  | 62.069 | 100
19980905110000 | 1998-09-05 11:00 | 509.134 |  | 0 | 148.583 | 150.402 | 150.83 | 146.937 |  | 1049.947 | 1141.116 |  | 5.5313 | 5.9312 | 6.218 | 5.929 | 5.4795 | 5.6497 | 5.4336 | 5.5222 | 45.6945 | 0.041125 |  | 62.069 | 100
19980905113000 | 1998-09-05 11:30 | 499.644 |  | 20.967 | 148.197 | 150.964 | 150.575 | 148.488 |  | 1032.78 | 1130.949 |  | 5.5413 | 5.9441 | 6.2485 | 5.9617 | 5.4956 | 5.655 | 5.439 | 5.533 | 45.8182 | 0.041236 |  | 62.069 | 100
19980905120000 | 1998-09-05 12:00 | 447.399 |  | 0 | 148.755 | 151.5 | 151.072 | 148.777 |  | 889.359 | 961.944 |  | 4.8462 | 5.2246 | 5.323 | 5.0049 | 4.8149 | 4.9783 | 4.8005 | 4.8469 | 39.8393 | 0.035855 |  | 62.069 | 100
19980905123000 | 1998-09-05 12:30 | 434.109 |  | 1.136 | 147.84 | 149.948 | 150.085 | 148.215 |  | 845.108 | 913.026 |  | 4.6045 | 4.9873 | 5.0454 | 4.6563 | 4.5647 | 4.7378 | 4.5715 | 4.6089 | 37.7764 | 0.033999 |  | 62.069 | 100
19980905130000 | 1998-09-05 13:00 | 397.828 |  | 0 | 148.197 | 150.443 | 150.661 | 148.463 |  | 833.941 | 894.192 |  | 4.4617 | 4.7708 | 4.8059 | 4.4937 | 4.406 | 4.6204 | 4.4351 | 4.4045 | 36.3981 | 0.032758 |  | 62.069 | 100
19980905133000 | 1998-09-05 13:30 | 393.319 |  | 1.504 | 148.46 | 151.655 | 150.588 | 148.684 |  | 831.941 | 889.442 |  | 4.4275 | 4.7546 | 4.7632 | 4.4709 | 4.3923 | 4.634 | 4.4556 | 4.4053 | 36.3034 | 0.032673 |  | 62.069 | 100
19980905140000 | 1998-09-05 14:00 | 391.091 |  | 0 | 148.703 | 150.454 | 151.239 | 149.711 |  | 836.274 | 897.942 |  | 4.4397 | 4.7676 | 4.7974 | 4.4922 | 4.4021 | 4.6357 | 4.4602 | 4.4204 | 36.4153 | 0.032774 |  | 62.069 | 100
19980905143000 | 1998-09-05 14:30 | 388.994 |  | 1.503 | 148.867 | 151.547 | 151.397 | 149.072 |  | 831.441 | 892.442 |  | 4.4397 | 4.7708 | 4.7998 | 4.5105 | 4.3999 | 4.6379 | 4.4595 | 4.4167 | 36.4348 | 0.032791 |  | 62.069 | 100
19980905150000 | 1998-09-05 15:00 | 391.248 |  | 0 | 148.582 | 150.269 | 150.992 | 148.783 |  | 834.274 | 894.609 |  | 4.4297 | 4.7668 | 4.7866 | 4.5212 | 4.3945 | 4.644 | 4.4656 | 4.4326 | 36.441 | 0.032797 |  | 62.069 | 100
19980905153000 | 1998-09-05 15:30 | 391.327 |  | 1.381 | 148.506 | 151.089 | 150.596 | 149.108 |  | 826.94 | 894.609 |  | 4.4243 | 4.7478 | 4.783 | 4.4854 | 4.3909 | 4.6211 | 4.4502 | 4.3992 | 36.3019 | 0.032672 |  | 62.069 | 100
19980905160000 | 1998-09-05 16:00 | 392.244 |  | 0 | 148.88 | 150.475 | 151.052 | 149.238 |  | 830.524 | 890.359 |  | 4.4236 | 4.7554 | 4.7754 | 4.4792 | 4.3884 | 4.6189 | 4.448 | 4.4021 | 36.291 | 0.032662 |  | 62.069 | 100
19980905163000 | 1998-09-05 16:30 | 388.234 |  | 1.505 | 148.451 | 152.012 | 151.145 | 150.032 |  | 839.441 | 902.109 |  | 4.4609 | 4.7517 | 4.8318 | 4.4824 | 4.4189 | 4.615 | 4.4397 | 4.4031 | 36.4035 | 0.032763 |  | 62.069 | 100
19980905170000 | 1998-09-05 17:00 | 394.184 |  | 0 | 149.038 | 151.074 | 151.581 | 149.588 |  | 830.857 | 884.109 |  | 4.4319 | 4.7571 | 4.7905 | 4.4861 | 4.4014 | 4.6272 | 4.4509 | 4.4045 | 36.3496 | 0.032715 |  | 62.069 | 100
19980905173000 | 1998-09-05 17:30 | 394.368 |  | 1.504 | 147.601 | 150.475 | 150.104 | 148.248 |  | 812.357 | 870.025 |  | 4.4397 | 4.7463 | 4.8081 | 4.4868 | 4.3984 | 4.6189 | 4.4458 | 4.4114 | 36.3554 | 0.03272 |  | 62.069 | 100
19980905180000 | 1998-09-05 18:00 | 394.761 |  | 0 | 148.623 | 151.92 | 150.851 | 150.682 |  | 857.108 | 921.026 |  | 4.6157 | 4.9683 | 5.0408 | 4.7561 | 4.5776 | 4.8408 | 4.6548 | 4.6174 | 38.0715 | 0.034264 |  | 62.069 | 100
19980905183000 | 1998-09-05 18:30 | 468.108 |  | 1.383 | 149.551 | 152.533 | 152.024 | 150.305 |  | 973.611 | 1049.78 |  | 5.1499 | 5.5466 | 5.7388 | 5.4802 | 5.0903 | 5.3003 | 5.0979 | 5.1538 | 42.5578 | 0.038302 |  | 62.069 | 100
19980905190000 | 1998-09-05 19:00 | 473.115 |  | 0 | 149.578 | 150.645 | 151.98 | 149.408 |  | 977.361 | 1060.114 |  | 5.1895 | 5.5725 | 5.8022 | 5.5061 | 5.1399 | 5.3254 | 5.1194 | 5.1865 | 42.8415 | 0.038557 |  | 62.069 | 100
19980905193000 | 1998-09-05 19:30 | 474.295 |  | 1.06 | 148.698 | 150.738 | 151.206 | 148.51 |  | 981.612 | 1066.614 |  | 5.2095 | 5.6245 | 5.8296 | 5.5786 | 5.1689 | 5.365 | 5.1599 | 5.2292 | 43.1652 | 0.038849 |  | 62.069 | 100
19980905200000 | 1998-09-05 20:00 | 476.287 |  | 0 | 148.511 | 150.464 | 151.06 | 147.742 |  | 968.278 | 1049.197 |  | 5.175 | 5.5786 | 5.7778 | 5.52 | 5.1377 | 5.3262 | 5.124 | 5.1965 | 42.8358 | 0.038552 |  | 62.069 | 100
19980905203000 | 1998-09-05 20:30 | 547.905 |  | 1.747 | 149.222 | 153.125 | 151.389 | 150.154 |  | 1107.032 | 1209.285 |  | 5.8479 | 6.3179 | 6.6628 | 6.4446 | 5.7937 | 5.9807 | 5.7397 | 5.8999 | 48.6872 | 0.043818 |  | 62.069 | 100
19980905210000 | 1998-09-05 21:00 | 545.336 |  | 0.077 | 149.46 | 150.819 | 151.917 | 148.344 |  | 1109.948 | 1211.285 |  | 5.8159 | 6.321 | 6.6384 | 6.4224 | 5.7671 | 5.9685 | 5.7336 | 5.8831 | 48.55 | 0.043695 |  | 62.069 | 100
19980905213000 | 1998-09-05 21:30 | 540.748 |  | 1.628 | 148.51 | 150.783 | 151.148 | 147.07 |  | 1116.115 | 1208.785 |  | 5.8289 | 6.321 | 6.6392 | 6.4446 | 5.7764 | 5.989 | 5.7527 | 5.9021 | 48.6539 | 0.043789 |  | 62.069 | 100
19980905220000 | 1998-09-05 22:00 | 540.172 |  | 0.078 | 148.736 | 153.243 | 151.039 | 149.53 |  | 1131.366 | 1232.535 |  | 5.8503 | 6.3301 | 6.6711 | 6.4514 | 5.8037 | 5.9976 | 5.7617 | 5.906 | 48.7719 | 0.043895 |  | 62.069 | 100
19980905223000 | 1998-09-05 22:30 | 542.111 |  | 1.75 | 149.496 | 151.175 | 151.721 | 148.204 |  | 1136.866 | 1234.952 |  | 5.8557 | 6.3308 | 6.6643 | 6.4446 | 5.8008 | 5.9961 | 5.7588 | 5.906 | 48.7571 | 0.043881 |  | 62.069 | 100
19980905230000 | 1998-09-05 23:00 | 537.943 |  | 0.078 | 148.58 | 150.458 | 151.148 | 148.478 |  | 1128.282 | 1228.202 |  | 5.8557 | 6.3203 | 6.6682 | 6.4202 | 5.7969 | 5.9846 | 5.7534 | 5.8923 | 48.6916 | 0.043822 |  | 62.069 | 100
19980905233000 | 1998-09-05 23:30 | 491.885 |  | 1.016 | 148.504 | 151.902 | 150.649 | 148.437 |  | 1009.362 | 1105.198 |  | 5.3298 | 5.7007 | 5.9456 | 5.6428 | 5.2566 | 5.4009 | 5.2063 | 5.3064 | 43.7891 | 0.03941 |  | 62.069 | 100
19980906000000 | 1998-09-06 | 474.662 |  | 0 | 148.18 | 150.092 | 150.266 | 147.864 |  | 1003.612 | 1092.281 |  | 5.3459 | 5.7671 | 5.9685 | 5.7495 | 5.3047 | 5.5054 | 5.2942 | 5.3682 | 44.3035 | 0.039873 |  | 62.069 | 100
19980906003000 | 1998-09-06 00:30 | 467.689 |  | 1.015 | 147.502 | 150.299 | 149.967 | 148.566 |  | 920.026 | 1001.612 |  | 4.8914 | 5.2688 | 5.4199 | 5.0759 | 4.8591 | 5.0002 | 4.8164 | 4.8782 | 40.2099 | 0.036189 |  | 62.069 | 100
19980906010000 | 1998-09-06 01:00 | 420.189 |  | 0 | 147.801 | 151.33 | 150.207 | 148.854 |  | 873.108 | 941.86 |  | 4.9248 | 5.3025 | 5.4253 | 5.1416 | 3.28 | 5.0911 | 4.8904 | 4.9104 | 38.9661 | 0.035069 |  | 62.069 | 100
19980906013000 | 1998-09-06 01:30 | 389.282 |  | 1.753 | 148.446 | 151.108 | 150.836 | 150.118 |  | 780.272 | 836.191 |  | 4.2419 | 4.5051 | 4.5632 | 4.1687 | 4.2749 | 4.3977 | 4.2305 | 4.2039 | 34.5859 | 0.031127 |  | 62.069 | 100
19980906020000 | 1998-09-06 02:00 | 339.003 |  | 0 | 147.938 | 149.349 | 150.518 | 147.617 |  | 719.521 | 760.438 |  | 3.8751 | 4.1389 | 4.0542 | 3.7545 | 3.9178 | 4.1436 | 3.9766 | 3.8629 | 31.7236 | 0.028551 |  | 62.069 | 100
19980906023000 | 1998-09-06 02:30 | 333.708 |  | 1.507 | 147.942 | 151.134 | 150.206 | 149.896 |  | 712.604 | 747.021 |  | 3.8438 | 4.1055 | 4.001 | 3.7202 | 3.9003 | 4.1199 | 3.9567 | 3.8324 | 31.4798 | 0.028332 |  | 62.069 | 100
19980906030000 | 1998-09-06 03:00 | 336.539 |  | 0 | 148.814 | 152.083 | 151.105 | 149.855 |  | 708.687 | 742.271 |  | 3.866 | 4.094 | 4.0359 | 3.7156 | 3.9155 | 4.0918 | 3.9414 | 3.8247 | 31.4849 | 0.028336 |  | 62.069 | 100
19980906033000 | 1998-09-06 03:30 | 336.251 |  | 1.385 | 148.759 | 151.351 | 150.902 | 149.123 |  | 717.687 | 761.272 |  | 3.9178 | 4.1436 | 4.0833 | 3.7775 | 3.9613 | 4.1299 | 3.9827 | 3.8766 | 31.8727 | 0.028685 |  | 62.069 | 100
19980906040000 | 1998-09-06 04:00 | 333.524 |  | 0 | 148.7 | 151.702 | 151.288 | 150.712 |  | 714.687 | 755.438 |  | 3.8773 | 4.1199 | 4.0527 | 3.7439 | 3.9125 | 4.094 | 3.9583 | 3.8484 | 31.607 | 0.028446 |  | 62.069 | 100
19980906043000 | 1998-09-06 04:30 | 336.67 |  | 1.751 | 148.864 | 150.32 | 151.421 | 150.073 |  | 711.77 | 749.522 |  | 3.8369 | 4.084 | 3.988 | 3.7141 | 3.8743 | 4.0481 | 3.9254 | 3.8224 | 31.2932 | 0.028164 |  | 62.069 | 100
19980906050000 | 1998-09-06 05:00 | 341.205 |  | 0 | 148.48 | 150.424 | 151.161 | 149.433 |  | 702.52 | 740.105 |  | 3.8263 | 4.0872 | 3.9918 | 3.7019 | 3.8873 | 4.0291 | 3.9178 | 3.8217 | 31.2631 | 0.028137 |  | 62.069 | 100
19980906053000 | 1998-09-06 05:30 | 337.456 |  | 1.997 | 148.898 | 151.713 | 150.568 | 149.98 |  | 717.271 | 753.938 |  | 3.885 | 4.1482 | 4.0696 | 3.7843 | 3.9261 | 4.0596 | 3.9613 | 3.8568 | 31.6909 | 0.028522 |  | 62.069 | 100
19980906060000 | 1998-09-06 06:00 | 330.143 |  | 0 | 149.639 | 151.022 | 151.996 | 150.279 |  | 733.188 | 776.772 |  | 3.901 | 4.1931 | 4.0857 | 3.84 | 3.962 | 4.1055 | 4.0115 | 3.9071 | 32.0059 | 0.028805 |  | 62.069 | 100
19980906063000 | 1998-09-06 06:30 | 332.843 |  | 1.384 | 148.659 | 150.579 | 151.491 | 149.836 |  | 722.854 | 766.689 |  | 3.856 | 4.1299 | 4.0254 | 3.7644 | 3.9033 | 4.033 | 3.9491 | 3.8491 | 31.5102 | 0.028359 |  | 62.069 | 100
19980906070000 | 1998-09-06 07:00 | 337.692 |  | 0 | 148.707 | 150.254 | 150.751 | 149.758 |  | 723.437 | 766.105 |  | 3.8667 | 4.1213 | 4.0222 | 3.7576 | 3.8995 | 4.0254 | 3.9407 | 3.8477 | 31.4811 | 0.028333 |  | 62.069 | 100
19980906073000 | 1998-09-06 07:30 | 372.636 |  | 1.503 | 148.882 | 150.63 | 151.242 | 149.393 |  | 793.023 | 858.691 |  | 4.2405 | 4.5532 | 4.564 | 4.3062 | 4.2961 | 4.3938 | 4.2871 | 4.2473 | 34.8882 | 0.031399 |  | 62.069 | 100
19980906080000 | 1998-09-06 08:00 | 449.234 |  | 0 | 148.768 | 151.074 | 151.276 | 149.588 |  | 961.361 | 1046.697 |  | 5.0369 | 5.4346 | 5.5969 | 5.3818 | 5.1064 | 5.2078 | 5.0447 | 5.0881 | 41.8972 | 0.037707 |  | 62.069 | 100
19980906083000 | 1998-09-06 08:30 | 575.194 |  | 2.731 | 150.056 | 154.554 | 152.507 | 152.079 |  | 1177.617 | 1289.704 |  | 6.1433 | 6.6108 | 7.0442 | 6.8276 | 6.1609 | 6.2646 | 6.0144 | 6.1707 | 51.2365 | 0.046113 |  | 62.069 | 100
19980906090000 | 1998-09-06 09:00 | 577.632 |  | 0.079 | 150.042 | 151.717 | 152.834 | 148.252 |  | 1191.368 | 1298.121 |  | 6.1394 | 6.6125 | 7.042 | 6.855 | 6.1775 | 6.2776 | 6.0327 | 6.1904 | 51.3271 | 0.046194 |  | 62.069 | 100
19980906093000 | 1998-09-06 09:30 | 646.156 |  | 2.362 | 149.35 | 152.748 | 151.887 | 149.53 |  | 1323.705 | 1456.875 |  | 6.7971 | 7.3274 | 7.8865 | 7.6973 | 6.8618 | 6.9465 | 6.6621 | 6.8779 | 57.0566 | 0.051351 |  | 62.069 | 100
19980906100000 | 1998-09-06 10:00 | 647.781 |  | 0.275 | 149.486 | 152.305 | 152.146 | 147.849 |  | 1318.788 | 1453.792 |  | 6.8916 | 7.3938 | 7.801 | 7.5981 | 6.9299 | 7.0107 | 6.72 | 6.9404 | 57.2855 | 0.051557 |  | 62.069 | 100
19980906103000 | 1998-09-06 10:30 | 651.215 |  | 1.871 | 148.827 | 151.64 | 151.272 | 148.669 |  | 1324.955 | 1457.208 |  | 6.8757 | 7.3877 | 7.8049 | 7.5935 | 6.9246 | 6.9939 | 6.7109 | 6.9207 | 57.2119 | 0.051491 |  | 62.069 | 100
19980906110000 | 1998-09-06 11:00 | 652.421 |  | 0.402 | 148.861 | 152.186 | 151.191 | 148.968 |  | 1329.705 | 1459.625 |  | 6.8679 | 7.3823 | 7.7773 | 7.5569 | 6.907 | 6.991 | 6.7085 | 6.9177 | 57.1086 | 0.051398 |  | 62.069 | 100
19980906113000 | 1998-09-06 11:30 | 649.223 |  | 1.751 | 148.74 | 152.031 | 151.33 | 147.576 |  | 1323.205 | 1453.958 |  | 6.897 | 7.3975 | 7.8096 | 7.5898 | 6.9299 | 7.0237 | 6.7361 | 6.939 | 57.3226 | 0.05159 |  | 62.069 | 100
19980906120000 | 1998-09-06 12:00 | 651.294 |  | 20.769 | 148.627 | 150.845 | 151.294 | 147.875 |  | 1313.704 | 1443.708 |  | 6.8909 | 7.3989 | 7.7859 | 7.5647 | 6.9192 | 7.0061 | 6.7275 | 6.929 | 57.2222 | 0.0515 |  | 62.069 | 100
19980906123000 | 1998-09-06 12:30 | 652.08 |  | 1.625 | 148.581 | 153.099 | 150.807 | 148.148 |  | 1316.954 | 1452.458 |  | 6.8596 | 7.3662 | 7.7744 | 7.5349 | 6.894 | 6.9924 | 6.7041 | 6.9084 | 57.034 | 0.051331 |  | 62.069 | 100
19980906130000 | 1998-09-06 13:00 | 651.871 |  | 0.273 | 149.274 | 151.407 | 151.419 | 148.684 |  | 1316.121 | 1448.125 |  | 6.8689 | 7.3792 | 7.7737 | 7.5464 | 6.8962 | 6.9978 | 6.7153 | 6.9253 | 57.1028 | 0.051393 |  | 62.069 | 100
19980906133000 | 1998-09-06 13:30 | 647.414 |  | 1.502 | 148.617 | 152.212 | 151.198 | 148.252 |  | 1324.288 | 1457.042 |  | 6.8872 | 7.386 | 7.8079 | 7.5715 | 6.9167 | 7.0144 | 6.7336 | 6.9329 | 57.2502 | 0.051525 |  | 62.069 | 100
19980906140000 | 1998-09-06 14:00 | 647.073 |  | 0.079 | 148.943 | 151.706 | 151.304 | 147.993 |  | 1324.538 | 1455.542 |  | 6.8984 | 7.4082 | 7.8171 | 7.5845 | 6.9375 | 7.0259 | 6.749 | 6.9429 | 57.3635 | 0.051627 |  | 62.069 | 100
19980906143000 | 1998-09-06 14:30 | 608.014 |  | 1.258 | 148.844 | 151.289 | 151.229 | 146.586 |  | 1245.286 | 1365.289 |  | 6.5361 | 7.0039 | 7.3396 | 7.0869 | 6.5566 | 6.6392 | 6.376 | 6.5605 | 54.0988 | 0.048689 |  | 62.069 | 100
19980906150000 | 1998-09-06 15:00 | 604.397 |  | 0.077 | 148.012 | 151.17 | 150.132 | 147.705 |  | 1239.036 | 1363.872 |  | 6.5239 | 7.0083 | 7.3145 | 7.0938 | 6.5598 | 6.6536 | 6.3936 | 6.5659 | 54.1134 | 0.048702 |  | 62.069 | 100
19980906153000 | 1998-09-06 15:30 | 609.744 |  | 1.382 | 148.433 | 152.046 | 150.885 | 148.333 |  | 1249.703 | 1379.873 |  | 6.6514 | 7.1487 | 7.4556 | 4.9768 | 6.6567 | 6.7947 | 6.5217 | 6.7056 | 52.9112 | 0.04762 |  | 62.069 | 100
19980906160000 | 1998-09-06 16:00 | 611.448 |  | 0.079 | 148.46 | 151.459 | 151.41 | 147.993 |  | 1252.369 | 1371.289 |  | 6.6858 | 7.1809 | 7.5188 | 5.0347 | 6.7085 | 6.8262 | 6.5408 | 6.7139 | 53.2096 | 0.047889 |  | 62.069 | 100
19980906163000 | 1998-09-06 16:30 | 614.306 |  | 0.442 | 148.313 | 151.226 | 150.846 | 146.276 |  | 1246.452 | 1366.873 |  | 6.5706 | 7.0366 | 7.3853 | 7.2244 | 6.585 | 6.6909 | 6.418 | 6.5767 | 54.4875 | 0.049039 |  | 62.069 | 100
19980906170000 | 1998-09-06 17:00 | 613.205 |  | 0.08 | 148.717 | 151.954 | 150.618 | 148.241 |  | 1239.036 | 1357.539 |  | 6.4553 | 6.907 | 7.2158 | 7.1641 | 6.4773 | 6.5835 | 6.321 | 6.4697 | 53.5937 | 0.048234 |  | 62.069 | 100
19980906173000 | 1998-09-06 17:30 | 646.706 |  | 1.991 | 149.468 | 152.294 | 151.955 | 148.581 |  | 1322.455 | 1456.458 |  | 6.8154 | 7.3242 | 7.7209 | 7.6919 | 6.8459 | 6.9626 | 6.6812 | 6.8589 | 56.901 | 0.051211 |  | 62.069 | 100
19980906180000 | 1998-09-06 18:00 | 646.864 |  | 0.08 | 149.142 | 151.954 | 151.605 | 147.993 |  | 1323.955 | 1456.708 |  | 6.781 | 7.3005 | 7.8552 | 7.8872 | 6.8291 | 6.9421 | 6.6697 | 6.8574 | 57.1222 | 0.05141 |  | 62.069 | 100
19980906183000 | 1998-09-06 18:30 | 643.194 |  | 1.625 | 148.772 | 151.928 | 151.026 | 147.225 |  | 1316.288 | 1445.625 |  | 6.804 | 7.325 | 7.8872 | 7.8958 | 6.8513 | 6.9641 | 6.6865 | 6.874 | 57.2879 | 0.051559 |  | 62.069 | 100
19980906190000 | 1998-09-06 19:00 | 645.946 |  | 0.077 | 148.645 | 151.433 | 150.791 | 147.473 |  | 1320.788 | 1448.792 |  | 6.8 | 7.3152 | 7.8872 | 7.8872 | 6.8467 | 6.9526 | 6.678 | 6.8596 | 57.2265 | 0.051504 |  | 62.069 | 100
19980906193000 | 1998-09-06 19:30 | 644.531 |  | 1.381 | 148.303 | 151.954 | 150.815 | 147.746 |  | 1313.121 | 1442.458 |  | 6.8269 | 7.2937 | 7.8933 | 7.8567 | 6.8459 | 6.9351 | 6.6665 | 6.8445 | 57.1626 | 0.051446 |  | 62.069 | 100
19980906200000 | 1998-09-06 20:00 | 646.313 |  | 0.15 | 148.794 | 151.706 | 151.105 | 147.993 |  | 1312.954 | 1442.041 |  | 6.8223 | 7.3167 | 7.9126 | 7.8972 | 6.8689 | 6.9551 | 6.6787 | 6.8628 | 57.3143 | 0.051583 |  | 62.069 | 100
19980906203000 | 1998-09-06 20:30 | 645.684 |  | 1.503 | 148.918 | 152.918 | 151.397 | 148.463 |  | 1317.788 | 1449.625 |  | 6.8008 | 7.29 | 7.8767 | 7.8552 | 6.855 | 6.926 | 6.6521 | 6.8359 | 57.0917 | 0.051383 |  | 62.069 | 100
19980906210000 | 1998-09-06 21:00 | 646.156 |  | 0.077 | 149.359 | 151.706 | 151.518 | 148.241 |  | 1317.621 | 1450.042 |  | 6.804 | 7.3052 | 7.8796 | 7.8645 | 6.8528 | 6.9307 | 6.665 | 6.8345 | 57.1363 | 0.051423 |  | 62.069 | 100
19980906213000 | 1998-09-06 21:30 | 647.834 |  | 1.873 | 148.778 | 152.109 | 151.086 | 147.653 |  | 1318.288 | 1448.292 |  | 6.8032 | 7.2876 | 7.8699 | 7.8484 | 6.8459 | 6.9207 | 6.6475 | 6.8359 | 57.0591 | 0.051353 |  | 62.069 | 100
19980906220000 | 1998-09-06 22:00 | 647.834 |  | 0.153 | 148.645 | 151.81 | 150.851 | 147.602 |  | 1312.871 | 1443.208 |  | 6.813 | 7.2891 | 7.8804 | 7.8394 | 6.8574 | 6.9321 | 6.6553 | 6.8359 | 57.1026 | 0.051392 |  | 62.069 | 100
19980906223000 | 1998-09-06 22:30 | 643.534 |  | 1.63 | 148.626 | 151.289 | 150.953 | 148.318 |  | 1315.621 | 1448.708 |  | 6.8223 | 7.3113 | 7.8926 | 7.8796 | 6.8765 | 6.9519 | 6.6772 | 6.855 | 57.2664 | 0.05154 |  | 62.069 | 100
19980906230000 | 1998-09-06 23:00 | 647.519 |  | 0.079 | 148.667 | 152.238 | 151.309 | 148.525 |  | 1317.538 | 1451.375 |  | 6.8184 | 7.3167 | 7.9026 | 7.9019 | 6.8711 | 6.9604 | 6.675 | 6.8596 | 57.3057 | 0.051575 |  | 62.069 | 100
19980906233000 | 1998-09-06 23:30 | 577.37 |  | 1.139 | 148.599 | 150.221 | 151.072 | 145.766 |  | 1169.867 | 1279.12 |  | 6.1768 | 6.5979 | 7.0176 | 6.9497 | 6.1746 | 6.2324 | 5.9839 | 6.1501 | 51.283 | 0.046155 |  | 62.069 | 100
19980907000000 | 1998-09-07 | 508.452 |  | 0 | 147.036 | 150.206 | 149.109 | 146.741 |  | 1055.864 | 1148.45 |  | 5.5962 | 5.9595 | 6.2783 | 6.1707 | 5.6367 | 5.7144 | 5.4963 | 5.5984 | 46.4505 | 0.041805 |  | 62.069 | 100
19980907003000 | 1998-09-07 00:30 | 517.155 |  | 1.263 | 147.803 | 151.366 | 150.14 | 148.643 |  | 1064.114 | 1160.533 |  | 5.6702 | 6.0334 | 6.3904 | 6.2524 | 5.7068 | 5.7937 | 5.5657 | 5.6436 | 47.0562 | 0.042351 |  | 62.069 | 100
19980907010000 | 1998-09-07 01:00 | 513.8 |  | 0 | 149.04 | 151.695 | 151.326 | 148.478 |  | 1072.364 | 1168.2 |  | 5.6497 | 5.9951 | 6.3638 | 6.2148 | 5.6899 | 5.7649 | 5.5352 | 5.6191 | 46.8325 | 0.042149 |  | 62.069 | 100
19980907013000 | 1998-09-07 01:30 | 471.883 |  | 1.26 | 148.527 | 149.102 | 151.095 | 146.379 |  | 993.612 | 1084.281 |  | 5.2759 | 5.6062 | 5.8418 | 5.6992 | 5.3132 | 5.4246 | 5.2078 | 5.2505 | 43.6192 | 0.039257 |  | 62.069 | 100
19980907020000 | 1998-09-07 02:00 | 467.925 |  | 0 | 147.968 | 151.185 | 150.255 | 147.968 |  | 996.195 | 1077.114 |  | 5.2781 | 5.5847 | 5.8679 | 5.6909 | 5.3147 | 5.4231 | 5.2041 | 5.2393 | 43.6028 | 0.039243 |  | 62.069 | 100
19980907023000 | 1998-09-07 02:30 | 473.22 |  | 21.388 | 148.503 | 150.406 | 150.924 | 148.178 |  | 983.278 | 1066.197 |  | 5.2544 | 5.6001 | 5.8303 | 5.7068 | 5.2979 | 5.4177 | 5.2034 | 5.2407 | 43.5513 | 0.039196 |  | 62.069 | 100
19980907030000 | 1998-09-07 03:00 | 472.565 |  | 0 | 148.373 | 152.856 | 150.797 | 149.885 |  | 1006.612 | 1088.281 |  | 5.2231 | 5.5588 | 5.7998 | 5.6511 | 5.2673 | 5.375 | 5.165 | 5.207 | 43.2471 | 0.038922 |  | 62.069 | 100
19980907033000 | 1998-09-07 03:30 | 471.936 |  | 1.385 | 149.508 | 151.577 | 151.752 | 149.349 |  | 1003.945 | 1090.115 |  | 5.217 | 5.5588 | 5.8076 | 5.6458 | 5.2637 | 5.3704 | 5.1621 | 5.2034 | 43.2288 | 0.038906 |  | 62.069 | 100
19980907040000 | 1998-09-07 04:00 | 469.026 |  | 0 | 148.951 | 149.911 | 151.148 | 147.683 |  | 999.695 | 1078.614 |  | 5.2339 | 5.584 | 5.8069 | 5.6672 | 5.2712 | 5.397 | 5.1919 | 5.2253 | 43.3774 | 0.03904 |  | 62.069 | 100
19980907043000 | 1998-09-07 04:30 | 414.186 |  | 1.263 | 148.19 | 149.375 | 150.556 | 147.147 |  | 909.109 | 979.028 |  | 4.8042 | 5.1079 | 5.2712 | 5.0544 | 4.8264 | 4.9797 | 4.7852 | 4.7761 | 39.6051 | 0.035645 |  | 62.069 | 100
19980907050000 | 1998-09-07 05:00 | 415.654 |  | 0 | 148.042 | 150.21 | 150.42 | 148.725 |  | 904.193 | 975.778 |  | 4.7944 | 5.0735 | 5.2529 | 4.988 | 4.8325 | 4.9485 | 4.7554 | 4.7417 | 39.3869 | 0.035448 |  | 62.069 | 100
19980907053000 | 1998-09-07 05:30 | 418.983 |  | 1.755 | 147.869 | 149.612 | 150.221 | 148.127 |  | 880.525 | 946.694 |  | 4.7615 | 5.0386 | 5.2131 | 4.9524 | 4.7876 | 4.9202 | 4.7227 | 4.7097 | 39.1058 | 0.035195 |  | 62.069 | 100
19980907060000 | 1998-09-07 06:00 | 421.028 |  | 0 | 148.301 | 150.901 | 150.659 | 149.664 |  | 880.109 | 945.527 |  | 4.7485 | 5.0239 | 5.1843 | 4.9348 | 4.783 | 4.9072 | 4.7219 | 4.6882 | 38.9918 | 0.035093 |  | 62.069 | 100
19980907063000 | 1998-09-07 06:30 | 431.041 |  | 1.511 | 148.821 | 151.566 | 151.38 | 150.329 |  | 873.025 | 939.61 |  | 4.7134 | 4.9905 | 4.5708 | 4.9011 | 4.7395 | 4.8752 | 4.6868 | 4.657 | 38.1343 | 0.034321 |  | 62.069 | 100
19980907070000 | 1998-09-07 07:00 | 479.197 |  | 0 | 148.564 | 151.267 | 151.317 | 148.792 |  | 984.112 | 1065.531 |  | 5.3308 | 5.71 | 5.0256 | 5.8784 | 5.3811 | 5.5459 | 5.3223 | 5.3765 | 43.5706 | 0.039214 |  | 62.069 | 100
19980907073000 | 1998-09-07 07:30 | 505.883 |  | 1.874 | 149.519 | 151.876 | 151.852 | 148.163 |  | 1067.447 | 1160.533 |  | 5.6282 | 6.0327 | 5.3223 | 6.26 | 5.6755 | 5.8037 | 5.5618 | 5.6458 | 45.93 | 0.041337 |  | 62.069 | 100
19980907080000 | 1998-09-07 08:00 | 523.866 |  | 0.079 | 149.426 | 151.758 | 152.093 | 149.283 |  | 1077.031 | 1162.95 |  | 5.6824 | 6.0754 | 5.3765 | 6.3118 | 5.7031 | 5.8289 | 5.5894 | 5.6855 | 46.253 | 0.041628 |  | 62.069 | 100
19980907083000 | 1998-09-07 08:30 | 577.265 |  | 2.483 | 149.056 | 152.165 | 151.54 | 148.204 |  | 1186.034 | 1291.287 |  | 6.2981 | 6.7681 | 6.0791 | 7.1792 | 6.3157 | 6.46 | 6.1799 | 6.3308 | 51.6109 | 0.04645 |  | 62.069 | 100
19980907090000 | 1998-09-07 09:00 | 626.207 |  | 20.603 | 150.061 | 152.541 | 152.55 | 149.323 |  | 1276.537 | 1399.54 |  | 6.6589 | 7.1206 | 6.4539 | 7.6287 | 6.6902 | 6.7695 | 6.4912 | 6.6711 | 54.4841 | 0.049036 |  | 62.069 | 100
19980907093000 | 1998-09-07 09:30 | 635.539 |  | 2.241 | 149.223 | 151.876 | 151.735 | 147.916 |  | 1289.704 | 1419.124 |  | 6.7979 | 7.2876 | 6.6338 | 7.8423 | 6.8435 | 6.9375 | 6.646 | 6.833 | 55.8216 | 0.050239 |  | 62.069 | 100
19980907100000 | 1998-09-07 10:00 | 649.905 |  | 0.199 | 149.055 | 151.64 | 151.553 | 147.927 |  | 1298.537 | 1427.791 |  | 6.8679 | 7.3799 | 6.6956 | 7.9622 | 6.9153 | 7.0161 | 6.7354 | 6.9314 | 56.5038 | 0.050853 |  | 62.069 | 100
19980907103000 | 1998-09-07 10:30 | 648.961 |  | 1.873 | 148.413 | 151.743 | 150.888 | 148.278 |  | 1297.871 | 1425.208 |  | 6.8711 | 7.3716 | 6.7131 | 7.9536 | 6.9221 | 6.9939 | 6.7117 | 6.9131 | 56.4502 | 0.050805 |  | 62.069 | 100
19980907110000 | 1998-09-07 11:00 | 645.501 |  | 0.077 | 148.895 | 152.656 | 150.946 | 149.19 |  | 1298.954 | 1431.791 |  | 6.8977 | 7.396 | 6.7268 | 7.9895 | 6.9404 | 7.0435 | 6.7512 | 6.939 | 56.6841 | 0.051016 |  | 62.069 | 100
19980907113000 | 1998-09-07 11:30 | 646.733 |  | 2.115 | 149.219 | 151.691 | 151.596 | 147.978 |  | 1304.871 | 1441.625 |  | 6.9214 | 7.3975 | 6.7383 | 7.9963 | 6.9451 | 7.0427 | 6.762 | 6.9587 | 56.762 | 0.051086 |  | 62.069 | 100
19980907120000 | 1998-09-07 12:00 | 632.289 |  | 0.074 | 148.719 | 150.454 | 151.086 | 146.741 |  | 1274.037 | 1400.457 |  | 6.6589 | 7.1167 | 7.5569 | 7.6484 | 6.6887 | 6.7803 | 6.4966 | 6.6765 | 55.623 | 0.050061 |  | 62.069 | 100
19980907123000 | 1998-09-07 12:30 | 647.388 |  | 1.382 | 148.312 | 152.124 | 150.643 | 148.411 |  | 1300.871 | 1429.208 |  | 6.7695 | 7.2305 | 7.8027 | 7.7927 | 6.8008 | 6.8887 | 6.6047 | 6.791 | 56.6806 | 0.051013 |  | 62.069 | 100
19980907130000 | 1998-09-07 13:00 | 641.935 |  | 0.074 | 149.093 | 151.51 | 151.506 | 148.293 |  | 1295.62 | 1429.374 |  | 6.7444 | 7.2053 | 7.7759 | 7.7507 | 6.7788 | 6.8611 | 6.5872 | 6.7573 | 56.4607 | 0.050815 |  | 62.069 | 100
19980907133000 | 1998-09-07 13:30 | 648.935 |  | 1.747 | 148.838 | 151.747 | 151.32 | 147.539 |  | 1310.038 | 1442.041 |  | 6.7451 | 7.209 | 7.7737 | 7.75 | 6.7834 | 6.8635 | 6.585 | 6.7642 | 56.4739 | 0.050827 |  | 62.069 | 100
19980907140000 | 1998-09-07 14:00 | 649.616 |  | 0.076 | 148.855 | 152.748 | 151.11 | 147.55 |  | 1300.037 | 1432.458 |  | 6.7368 | 7.1816 | 7.7546 | 7.7065 | 6.7712 | 6.8528 | 6.5688 | 6.7429 | 56.3152 | 0.050684 |  | 62.069 | 100
19980907143000 | 1998-09-07 14:30 | 644.95 |  | 1.993 | 148.721 | 152.423 | 151.184 | 147.72 |  | 1300.204 | 1430.291 |  | 6.7354 | 7.1899 | 7.7737 | 7.7705 | 6.7864 | 6.874 | 6.5881 | 6.7688 | 56.4868 | 0.050838 |  | 62.069 | 100
19980907150000 | 1998-09-07 15:00 | 648.437 |  | 0.075 | 148.639 | 151.902 | 151.185 | 147.199 |  | 1301.204 | 1430.624 |  | 6.7537 | 7.2158 | 7.7798 | 7.7651 | 6.7957 | 6.8787 | 6.5979 | 6.7781 | 56.5648 | 0.050908 |  | 62.069 | 100
19980907153000 | 1998-09-07 15:30 | 649.171 |  | 1.628 | 148.514 | 152.382 | 150.896 | 147.679 |  | 1298.287 | 1427.791 |  | 6.7505 | 7.2158 | 7.7996 | 7.7729 | 6.8047 | 6.8879 | 6.6101 | 6.7856 | 56.6271 | 0.050964 |  | 62.069 | 100
19980907160000 | 1998-09-07 16:00 | 646.523 |  | 0.075 | 148.989 | 152.031 | 151.033 | 148.318 |  | 1308.538 | 1436.708 |  | 6.7529 | 7.2236 | 7.7957 | 7.76 | 6.7986 | 6.8811 | 6.6011 | 6.7803 | 56.5933 | 0.050934 |  | 62.069 | 100
19980907163000 | 1998-09-07 16:30 | 651.871 |  | 1.501 | 148.691 | 152.645 | 151.391 | 148.437 |  | 1311.204 | 1442.708 |  | 6.7932 | 7.261 | 7.8523 | 7.8354 | 6.8352 | 6.9192 | 6.6392 | 6.8201 | 56.9556 | 0.05126 |  | 62.069 | 100
19980907170000 | 1998-09-07 17:00 | 649.039 |  | 20.899 | 149.105 | 151.747 | 151.193 | 147.044 |  | 1316.371 | 1444.458 |  | 6.7971 | 7.2671 | 7.8323 | 7.8096 | 6.8359 | 6.9038 | 6.6262 | 6.8115 | 56.8835 | 0.051195 |  | 62.069 | 100
19980907173000 | 1998-09-07 17:30 | 650.639 |  | 1.989 | 148.556 | 152.175 | 151.193 | 147.968 |  | 1315.621 | 1449.708 |  | 6.8018 | 7.2671 | 7.8315 | 7.8308 | 6.8291 | 6.9092 | 6.6338 | 6.8191 | 56.9224 | 0.05123 |  | 62.069 | 100
19980907180000 | 1998-09-07 18:00 | 651.189 |  | 0.273 | 149.126 | 150.819 | 151.142 | 147.602 |  | 1320.955 | 1455.292 |  | 6.7886 | 7.2595 | 7.8394 | 7.8157 | 6.8384 | 6.916 | 6.6299 | 6.8115 | 56.899 | 0.051209 |  | 62.069 | 100
19980907183000 | 1998-09-07 18:30 | 649.433 |  | 1.504 | 148.609 | 151.784 | 151.084 | 147.081 |  | 1321.788 | 1450.542 |  | 6.8108 | 7.2542 | 7.853 | 7.8193 | 6.8467 | 6.9116 | 6.627 | 6.8169 | 56.9395 | 0.051246 |  | 62.069 | 100
19980907190000 | 1998-09-07 19:00 | 648.725 |  | 0.075 | 148.751 | 151.81 | 150.845 | 147.354 |  | 1318.204 | 1448.625 |  | 6.8306 | 7.29 | 7.8904 | 7.856 | 6.8733 | 6.9404 | 6.665 | 6.8467 | 57.1924 | 0.051473 |  | 62.069 | 100
19980907193000 | 1998-09-07 19:30 | 640.336 |  | 1.747 | 148.535 | 153.295 | 150.89 | 148.839 |  | 1311.121 | 1446.542 |  | 6.7856 | 7.2449 | 7.8333 | 7.8096 | 6.8208 | 6.894 | 6.6079 | 6.7979 | 56.794 | 0.051115 |  | 62.069 | 100
19980907200000 | 1998-09-07 20:00 | 642.302 |  | 0.156 | 148.944 | 152.072 | 151.536 | 148.112 |  | 1319.955 | 1453.875 |  | 6.791 | 7.229 | 7.8103 | 7.7698 | 6.8115 | 6.8848 | 6.6155 | 6.7773 | 56.6892 | 0.05102 |  | 62.069 | 100
19980907203000 | 1998-09-07 20:30 | 640.598 |  | 1.874 | 148.611 | 151.85 | 150.952 | 147.147 |  | 1316.038 | 1448.792 |  | 6.7285 | 7.1924 | 7.75 | 7.7407 | 6.7764 | 6.8513 | 6.5842 | 6.7429 | 56.3664 | 0.05073 |  | 62.069 | 100
19980907210000 | 1998-09-07 21:00 | 645.343 |  | 0.152 | 148.543 | 151.835 | 150.84 | 148.37 |  | 1331.705 | 1465.209 |  | 6.7642 | 7.2419 | 7.7827 | 7.7974 | 6.8018 | 6.8833 | 6.6155 | 6.7917 | 56.6785 | 0.051011 |  | 62.069 | 100
19980907213000 | 1998-09-07 21:30 | 504.127 |  | 0.519 | 147.783 | 148.803 | 150.084 | 145.09 |  | 1023.279 | 1104.948 |  | 5.3711 | 5.6909 | 5.9517 | 5.8174 | 5.3948 | 5.4458 | 5.2393 | 5.3438 | 44.2548 | 0.039829 |  | 62.069 | 100
19980907220000 | 1998-09-07 22:00 | 473.876 |  | 0 | 146.689 | 150.443 | 148.643 | 147.968 |  | 970.361 | 1048.613 |  | 5.1782 | 5.4841 | 5.7068 | 5.5291 | 5.2178 | 5.3147 | 5.1033 | 5.146 | 42.68 | 0.038412 |  | 62.069 | 100
19980907223000 | 1998-09-07 22:30 | 472.46 |  | 1.262 | 148.1 | 151.222 | 150.356 | 148.994 |  | 978.195 | 1057.614 |  | 5.2148 | 5.5237 | 5.7603 | 5.5811 | 5.2529 | 5.3535 | 5.1467 | 5.1782 | 43.0112 | 0.03871 |  | 62.069 | 100
19980907230000 | 1998-09-07 23:00 | 473.692 |  | 0 | 148.631 | 151.067 | 151.122 | 148.839 |  | 973.861 | 1051.614 |  | 5.1636 | 5.4468 | 5.6824 | 5.4946 | 5.1926 | 5.2781 | 5.0745 | 5.105 | 42.4376 | 0.038194 |  | 62.069 | 100
19980907233000 | 1998-09-07 23:30 | 469.97 |  | 20.486 | 149.052 | 151.278 | 151.451 | 149.298 |  | 978.111 | 1062.114 |  | 5.1819 | 5.4773 | 5.696 | 5.5322 | 5.2009 | 5.3115 | 5.1025 | 5.1255 | 42.6278 | 0.038365 |  | 62.069 | 100
19980908000000 | 1998-09-08 | 436.494 |  | 0 | 148.138 | 149.859 | 150.596 | 146.889 |  | 855.191 | 919.943 |  | 4.6196 | 4.866 | 4.9995 | 4.696 | 4.615 | 4.7195 | 4.5435 | 4.5471 | 37.6062 | 0.033846 |  | 62.069 | 100
19980908003000 | 1998-09-08 00:30 | 425.956 |  | 1.241 | 147.366 | 151.211 | 149.573 | 147.993 |  | 863.191 | 931.693 |  | 4.6799 | 4.9758 | 5.0684 | 4.8569 | 4.709 | 4.8706 | 4.6777 | 4.644 | 38.4823 | 0.034634 |  | 62.069 | 100
19980908010000 | 1998-09-08 01:00 | 358.611 |  | 0 | 148.695 | 149.648 | 150.856 | 148.906 |  | 735.604 | 785.023 |  | 3.9926 | 4.229 | 4.1726 | 3.9315 | 4.0337 | 4.2366 | 4.0779 | 3.9742 | 32.6481 | 0.029383 |  | 62.069 | 100
19980908013000 | 1998-09-08 01:30 | 337.928 |  | 1.505 | 147.93 | 149.545 | 150.407 | 149.05 |  | 712.937 | 757.522 |  | 4.2756 | 4.5869 | 4.554 | 4.3359 | 4.3274 | 0.0017 | 4.3716 | 4.2717 | 30.7248 | 0.027652 |  | 62.069 | 100
19980908020000 | 1998-09-08 02:00 | 335.333 |  | 0 | 148.089 | 150.561 | 150.563 | 148.828 |  | 713.687 | 756.938 |  | 3.8979 | 4.1489 | 4.0588 | 3.8315 | 3.9498 | 4.165 | 4.0071 | 3.8705 | 31.9295 | 0.028737 |  | 62.069 | 100
19980908023000 | 1998-09-08 02:30 | 337.221 |  | 1.872 | 148.821 | 150.901 | 151.039 | 150.159 |  | 702.854 | 751.355 |  | 3.9735 | 4.2268 | 4.1543 | 3.8918 | 4.0115 | 2.9169 | 4.0681 | 3.9399 | 31.1828 | 0.028065 |  | 62.069 | 100
19980908030000 | 1998-09-08 03:00 | 337.823 |  | 0 | 148.812 | 149.468 | 151.393 | 149.468 |  | 708.604 | 751.938 |  | 4.0742 | 4.2932 | 4.2786 | 3.988 | 4.113 | 2.8672 | 4.1162 | 3.9941 | 31.7245 | 0.028552 |  | 62.069 | 100
19980908033000 | 1998-09-08 03:30 | 335.386 |  | 1.63 | 148.768 | 150.262 | 151.087 | 149.767 |  | 702.02 | 748.771 |  | 4.0107 | 4.2336 | 4.2 | 3.9109 | 4.0459 | 2.8131 | 4.071 | 3.9414 | 31.2266 | 0.028104 |  | 62.069 | 100
19980908040000 | 1998-09-08 04:00 | 334.887 |  | 0 | 148.425 | 150.86 | 151.252 | 150.118 |  | 707.604 | 750.522 |  | 3.9926 | 4.2451 | 4.1763 | 3.9026 | 4.0193 | 2.8009 | 4.0603 | 3.9277 | 31.1248 | 0.028012 |  | 62.069 | 100
19980908043000 | 1998-09-08 04:30 | 341.834 |  | 1.138 | 148.898 | 151.381 | 151.467 | 149.648 |  | 715.437 | 763.272 |  | 4.0552 | 4.2542 | 4.2542 | 3.9453 | 4.0674 | 2.8162 | 4.0674 | 3.9597 | 31.4196 | 0.028278 |  | 62.069 | 100
19980908050000 | 1998-09-08 05:00 | 336.329 |  | 0 | 148.739 | 150.69 | 151.236 | 149.948 |  | 719.104 | 766.105 |  | 4.0796 | 4.2922 | 4.28 | 3.975 | 4.1055 | 2.8336 | 4.1047 | 3.9865 | 31.6571 | 0.028491 |  | 62.069 | 100
19980908053000 | 1998-09-08 05:30 | 336.408 |  | 1.627 | 148.753 | 151.093 | 151.249 | 149.855 |  | 712.77 | 757.605 |  | 4.0383 | 4.2473 | 4.2297 | 3.9254 | 4.0642 | 2.8009 | 4.0696 | 3.9414 | 31.3168 | 0.028185 |  | 62.069 | 100
19980908060000 | 1998-09-08 06:00 | 336.355 |  | 0 | 148.516 | 151.706 | 151.29 | 150.221 |  | 725.854 | 767.939 |  | 4.0413 | 4.2886 | 4.2344 | 3.9697 | 4.0718 | 2.842 | 4.0969 | 3.9941 | 31.5388 | 0.028385 |  | 62.069 | 100
19980908063000 | 1998-09-08 06:30 | 340.838 |  | 1.627 | 149.237 | 150.454 | 151.548 | 149.711 |  | 724.604 | 770.022 |  | 4.0603 | 4.2939 | 4.2847 | 3.9705 | 4.1008 | 2.8413 | 4.0933 | 3.9865 | 31.6313 | 0.028468 |  | 62.069 | 100
19980908070000 | 1998-09-08 07:00 | 340.786 |  | 0 | 148.401 | 150.572 | 151.099 | 148.344 |  | 724.104 | 769.105 |  | 4.2373 | 4.5166 | 4.4922 | 4.239 | 4.2542 | 2.9749 | 4.2656 | 2.8245 | 31.8043 | 0.028624 |  | 62.069 | 100
19980908073000 | 1998-09-08 07:30 | 445.538 |  | 22.007 | 148.567 | 153.346 | 150.543 | 150.376 |  | 984.195 | 1072.197 |  | 5.281 | 5.6421 | 5.8289 | 5.7754 | 5.2827 | 3.7301 | 5.2253 | 5.3125 | 42.078 | 0.03787 |  | 62.069 | 100
19980908080000 | 1998-09-08 08:00 | 604.03 |  | 0.647 | 150.992 | 153.779 | 153.303 | 151.304 |  | 1277.62 | 1403.207 |  | 6.5422 | 6.9985 | 7.4875 | 6.4316 | 6.5469 | 6.6826 | 6.395 | 6.5918 | 53.6761 | 0.048308 |  | 62.069 | 100
19980908083000 | 1998-09-08 08:30 | 647.86 |  | 1.747 | 149.999 | 151.928 | 152.932 | 148.71 |  | 1314.204 | 1444.125 |  | 6.7612 | 7.2419 | 7.7844 | 7.8279 | 6.7773 | 6.9077 | 6.6086 | 6.8147 | 56.7237 | 0.051051 |  | 62.069 | 100
19980908090000 | 1998-09-08 09:00 | 646.785 |  | 0.522 | 149.242 | 151.485 | 151.75 | 149.257 |  | 1302.704 | 1432.625 |  | 6.7375 | 7.2007 | 7.7424 | 7.7896 | 6.7498 | 6.874 | 6.5674 | 6.7749 | 56.4363 | 0.050793 |  | 62.069 | 100
19980908093000 | 1998-09-08 09:30 | 642.748 |  | 1.506 | 148.828 | 151.691 | 151.092 | 147.236 |  | 1299.621 | 1431.041 |  | 6.8367 | 7.3037 | 7.876 | 7.9133 | 6.8628 | 6.9802 | 6.6765 | 6.8787 | 57.3279 | 0.051595 |  | 62.069 | 100
19980908100000 | 1998-09-08 10:00 | 646.418 |  | 0.076 | 148.781 | 151.717 | 150.953 | 148.252 |  | 1300.871 | 1430.624 |  | 6.8062 | 7.2625 | 7.8315 | 7.8401 | 6.8398 | 6.9429 | 6.6299 | 6.8474 | 57.0003 | 0.0513 |  | 62.069 | 100
19980908103000 | 1998-09-08 10:30 | 646.942 |  | 1.261 | 148.797 | 152.005 | 151.239 | 148.788 |  | 1301.621 | 1430.874 |  | 6.7756 | 7.2373 | 7.7996 | 7.8438 | 6.7925 | 6.9045 | 6.6033 | 6.8154 | 56.772 | 0.051095 |  | 62.069 | 100
19980908110000 | 1998-09-08 11:00 | 651.949 |  | 0.152 | 148.674 | 151.717 | 151.322 | 148.252 |  | 1303.704 | 1432.625 |  | 6.749 | 7.2068 | 7.7546 | 7.7834 | 6.7666 | 6.8833 | 6.5803 | 6.7864 | 56.5104 | 0.050859 |  | 62.069 | 100
19980908113000 | 1998-09-08 11:30 | 647.388 |  | 2.117 | 148.87 | 152.29 | 150.954 | 148.329 |  | 1299.621 | 1433.458 |  | 6.7422 | 7.1899 | 7.7507 | 7.7607 | 6.7634 | 6.8711 | 6.5674 | 6.7659 | 56.4113 | 0.05077 |  | 62.069 | 100
19980908120000 | 1998-09-08 12:00 | 645.422 |  | 0.155 | 148.624 | 151.237 | 151.104 | 148.019 |  | 1300.204 | 1432.625 |  | 6.7642 | 7.2021 | 7.7737 | 7.7827 | 6.7712 | 6.9001 | 6.5979 | 6.8008 | 56.5927 | 0.050933 |  | 62.069 | 100
19980908123000 | 1998-09-08 12:30 | 646.864 |  | 1.385 | 148.619 | 152.29 | 151.287 | 148.082 |  | 1300.371 | 1431.708 |  | 6.762 | 7.2319 | 7.7722 | 7.8179 | 6.7903 | 6.9106 | 6.6047 | 6.8147 | 56.7043 | 0.051034 |  | 62.069 | 100
19980908130000 | 1998-09-08 13:00 | 647.624 |  | 0.153 | 149.004 | 151.665 | 151.344 | 148.448 |  | 1297.121 | 1428.708 |  | 6.7397 | 7.2175 | 7.7485 | 7.7759 | 6.7703 | 6.8887 | 6.5864 | 6.7917 | 56.5187 | 0.050867 |  | 62.069 | 100
19980908133000 | 1998-09-08 13:30 | 595.379 |  | 1.504 | 148.183 | 150.221 | 150.631 | 146.013 |  | 1203.701 | 1314.538 |  | 6.3552 | 6.7673 | 7.2319 | 7.2334 | 6.3591 | 6.4614 | 6.189 | 6.3735 | 52.9708 | 0.047674 |  | 62.069 | 100
19980908140000 | 1998-09-08 14:00 | 588.117 |  | 20.41 | 148.083 | 151.237 | 150.135 | 147.772 |  | 1203.201 | 1311.871 |  | 6.4417 | 6.8521 | 7.3372 | 7.3281 | 6.4492 | 6.5605 | 6.2805 | 6.4492 | 53.6985 | 0.048329 |  | 62.069 | 100
19980908143000 | 1998-09-08 14:30 | 632.996 |  | 2.119 | 149.453 | 153.945 | 151.728 | 150.479 |  | 1307.704 | 1439.958 |  | 6.6514 | 7.0786 | 7.6233 | 7.6111 | 6.6658 | 6.7856 | 6.4827 | 6.6711 | 55.5696 | 0.050013 |  | 62.069 | 100
19980908150000 | 1998-09-08 15:00 | 636.955 |  | 0.155 | 149.858 | 152.15 | 152.527 | 147.447 |  | 1318.621 | 1453.125 |  | 6.7788 | 7.2449 | 7.7881 | 7.8455 | 6.8093 | 6.9299 | 6.6284 | 6.8237 | 56.8486 | 0.051164 |  | 62.069 | 100
19980908153000 | 1998-09-08 15:30 | 649.485 |  | 1.627 | 148.916 | 151.954 | 151.199 | 148.241 |  | 1342.372 | 1479.292 |  | 6.8345 | 7.3167 | 7.8904 | 7.9102 | 6.8696 | 6.9932 | 6.688 | 6.894 | 57.3966 | 0.051657 |  | 62.069 | 100
19980908160000 | 1998-09-08 16:00 | 646.392 |  | 0.156 | 148.492 | 151.902 | 151.184 | 147.199 |  | 1348.039 | 1482.209 |  | 6.7939 | 7.3145 | 7.8218 | 7.9055 | 6.8323 | 6.991 | 6.6589 | 6.8818 | 57.1997 | 0.05148 |  | 62.069 | 100
19980908163000 | 1998-09-08 16:30 | 646.444 |  | 1.628 | 148.937 | 150.613 | 151.019 | 147.89 |  | 1337.372 | 1479.626 |  | 6.8237 | 7.2656 | 7.8477 | 7.8477 | 6.8452 | 6.9451 | 6.6406 | 6.8467 | 57.0623 | 0.051356 |  | 62.069 | 100
19980908170000 | 1998-09-08 17:00 | 654.204 |  | 0.079 | 147.962 | 151.876 | 150.416 | 147.668 |  | 1319.955 | 1452.375 |  | 6.823 | 7.2861 | 7.856 | 7.8735 | 6.8643 | 6.9688 | 6.6621 | 6.8672 | 57.201 | 0.051481 |  | 62.069 | 100
19980908173000 | 1998-09-08 17:30 | 650.612 |  | 1.508 | 148.461 | 152.501 | 151.087 | 148.54 |  | 1321.121 | 1457.708 |  | 6.8337 | 7.3091 | 7.8699 | 7.8958 | 6.8718 | 6.9832 | 6.6797 | 6.8887 | 57.3319 | 0.051599 |  | 62.069 | 100
19980908180000 | 1998-09-08 18:00 | 651.53 |  | 0.078 | 148.605 | 152.516 | 151.247 | 147.07 |  | 1323.121 | 1455.208 |  | 6.8306 | 7.2944 | 7.8699 | 7.8782 | 6.8596 | 6.9702 | 6.6804 | 6.8765 | 57.2598 | 0.051534 |  | 62.069 | 100
19980908183000 | 1998-09-08 18:30 | 650.376 |  | 1.629 | 148.632 | 152.15 | 150.835 | 147.199 |  | 1321.371 | 1455.958 |  | 6.8208 | 7.2891 | 7.8552 | 7.8926 | 6.8567 | 6.9727 | 6.6758 | 6.8733 | 57.2362 | 0.051513 |  | 62.069 | 100
19980908190000 | 1998-09-08 19:00 | 648.908 |  | 0 | 148.643 | 151.459 | 150.991 | 147.498 |  | 1327.121 | 1457.375 |  | 6.8123 | 7.2976 | 7.843 | 7.8933 | 6.8528 | 6.9634 | 6.6682 | 6.874 | 57.2046 | 0.051484 |  | 62.069 | 100
19980908193000 | 1998-09-08 19:30 | 647.283 |  | 1.628 | 148.641 | 152.397 | 150.932 | 147.694 |  | 1325.121 | 1460.125 |  | 6.8108 | 7.28 | 7.8667 | 7.8889 | 6.855 | 6.9802 | 6.6873 | 6.8765 | 57.2454 | 0.051521 |  | 62.069 | 100
19980908200000 | 1998-09-08 20:00 | 644.216 |  | 0 | 148.513 | 154.027 | 150.857 | 149.076 |  | 1342.539 | 1473.542 |  | 6.804 | 7.29 | 7.8262 | 7.8621 | 6.8428 | 6.9634 | 6.6758 | 6.8765 | 57.1408 | 0.051427 |  | 62.069 | 100
19980908203000 | 1998-09-08 20:30 | 649.433 |  | 1.753 | 149.527 | 152.386 | 151.843 | 147.436 |  | 1340.372 | 1475.126 |  | 6.8337 | 7.3098 | 7.8674 | 7.917 | 6.8574 | 6.9832 | 6.6919 | 6.8955 | 57.3559 | 0.05162 |  | 62.069 | 100
19980908210000 | 1998-09-08 21:00 | 652.369 |  | 0.159 | 148.504 | 150.989 | 151.002 | 147.277 |  | 1334.538 | 1463.792 |  | 6.8062 | 7.2937 | 7.8516 | 7.9094 | 6.8474 | 6.9717 | 6.6865 | 6.8787 | 57.2452 | 0.051521 |  | 62.069 | 100
19980908213000 | 1998-09-08 21:30 | 552.361 |  | 1.753 | 147.616 | 150.757 | 149.576 | 146.302 |  | 1165.7 | 1268.12 |  | 6.0022 | 6.4011 | 6.7917 | 6.7444 | 6.0059 | 6.1433 | 5.906 | 6.031 | 50.0256 | 0.045023 |  | 62.069 | 100
19980908220000 | 1998-09-08 22:00 | 554.642 |  | 0 | 148.302 | 151.422 | 150.283 | 148.699 |  | 1161.117 | 1261.953 |  | 5.9685 | 6.3469 | 6.7505 | 6.6895 | 5.97 | 6.1089 | 5.8647 | 5.9778 | 49.6768 | 0.044709 |  | 62.069 | 100
19980908223000 | 1998-09-08 22:30 | 561.169 |  | 1.753 | 147.984 | 150.964 | 150.222 | 147.746 |  | 1128.782 | 1223.868 |  | 5.9731 | 6.3545 | 6.7307 | 6.6873 | 5.9707 | 6.1135 | 5.8679 | 5.9846 | 49.6823 | 0.044714 |  | 62.069 | 100
19980908230000 | 1998-09-08 23:00 | 452.144 |  | 0 | 148.274 | 149.623 | 150.466 | 147.395 |  | 895.526 | 960.944 |  | 4.873 | 5.1072 | 5.2864 | 5.0508 | 4.8645 | 4.9539 | 4.7676 | 4.8027 | 39.7061 | 0.035735 |  | 62.069 | 100
19980908233000 | 1998-09-08 23:30 | 343.224 |  | 1.388 | 146.786 | 148.958 | 149.02 | 147.72 |  | 697.52 | 730.188 |  | 3.785 | 3.9712 | 3.8461 | 3.6127 | 3.7888 | 4.0139 | 3.8606 | 3.7125 | 30.5908 | 0.027532 |  | 62.069 | 100
19980909000000 | 1998-09-09 | 333.577 |  | 0 | 147.092 | 150.025 | 149.372 | 148.293 |  | 694.187 | 772.856 |  | 3.8728 | 4.0908 | 4.0046 | 3.769 | 3.9094 | 4.1597 | 3.988 | 3.8308 | 31.6251 | 0.028463 |  | 62.069 | 100
19980909003000 | 1998-09-09 00:30 | 329.12 |  | 1.631 | 148.312 | 150.258 | 150.551 | 149.763 |  | 667.936 | 749.522 |  | 3.7782 | 3.9559 | 3.869 | 3.6012 | 3.8094 | 4.0376 | 3.8735 | 3.7012 | 30.626 | 0.027563 |  | 62.069 | 100
19980909010000 | 1998-09-09 01:00 | 333.655 |  | 0 | 148.369 | 152.223 | 151.145 | 150.49 |  | 654.769 | 742.938 |  | 3.705 | 3.8796 | 3.7637 | 3.4845 | 3.7278 | 3.9453 | 3.8071 | 3.6332 | 29.9462 | 0.026952 |  | 62.069 | 100
19980909013000 | 1998-09-09 01:30 | 335.621 |  | 1.995 | 148.62 | 150.919 | 151.177 | 148.938 |  | 662.186 | 751.605 |  | 3.6927 | 3.9193 | 3.7775 | 3.5653 | 3.7003 | 3.927 | 3.8247 | 3.6584 | 30.0652 | 0.027059 |  | 62.069 | 100
19980909020000 | 1998-09-09 02:00 | 334.311 |  | 0 | 148.756 | 150.749 | 150.857 | 149.511 |  | 667.936 | 755.105 |  | 3.7362 | 3.9834 | 3.8156 | 3.6179 | 3.7592 | 3.9323 | 3.8514 | 3.7019 | 30.3979 | 0.027358 |  | 62.069 | 100
19980909023000 | 1998-09-09 02:30 | 329.907 |  | 0.693 | 148.613 | 152.26 | 151.207 | 150.527 |  | 662.686 | 755.522 |  | 3.7164 | 3.9323 | 3.785 | 3.566 | 3.7362 | 3.8949 | 3.8461 | 3.6866 | 30.1635 | 0.027147 |  | 62.069 | 100
19980909030000 | 1998-09-09 03:00 | 332.161 |  | 0 | 148.7 | 151.125 | 151.253 | 149.145 |  | 663.436 | 755.605 |  | 3.6973 | 3.9423 | 3.7667 | 3.5599 | 3.7134 | 3.8796 | 3.824 | 3.6798 | 30.063 | 0.027057 |  | 62.069 | 100
19980909033000 | 1998-09-09 03:30 | 336.015 |  | 1.875 | 148.496 | 151.007 | 150.909 | 150.017 |  | 665.436 | 757.188 |  | 3.7095 | 3.9521 | 3.7858 | 3.5852 | 3.7263 | 3.8881 | 3.8224 | 3.6965 | 30.1659 | 0.027149 |  | 62.069 | 100
19980909040000 | 1998-09-09 04:00 | 328.727 |  | 0 | 148.786 | 151.92 | 151.305 | 149.939 |  | 669.686 | 747.105 |  | 3.7385 | 3.9667 | 3.8339 | 3.6042 | 3.7629 | 3.8956 | 3.8285 | 3.7073 | 30.3376 | 0.027304 |  | 62.069 | 100
19980909043000 | 1998-09-09 04:30 | 328.753 |  | 20.501 | 148.419 | 150.734 | 150.752 | 149.248 |  | 683.853 | 710.77 |  | 3.6996 | 3.9331 | 3.7897 | 3.5874 | 3.7195 | 3.8773 | 3.808 | 3.6813 | 30.0959 | 0.027086 |  | 62.069 | 100
19980909050000 | 1998-09-09 05:00 | 332.109 |  | 0 | 149.267 | 151.254 | 151.294 | 150.264 |  | 700.603 | 730.021 |  | 1.7015 | 4.3123 | 4.2634 | 4.0559 | 4.0908 | 4.2061 | 4.1353 | 4.0337 | 30.799 | 0.027719 |  | 62.069 | 100
19980909053000 | 1998-09-09 05:30 | 335.254 |  | 2.122 | 149.139 | 150.759 | 151.514 | 148.532 |  | 726.604 | 760.022 |  | 3.9735 | 4.1794 | 4.1313 | 3.882 | 4.001 | 4.1001 | 4.0071 | 3.9071 | 32.1815 | 0.028963 |  | 62.069 | 100
19980909060000 | 1998-09-09 06:00 | 425.615 |  | 0 | 149.154 | 152.61 | 151.712 | 151.125 |  | 865.608 | 927.11 |  | 4.8447 | 4.9241 | 5.0034 | 4.8059 | 4.6472 | 4.7571 | 4.6128 | 4.6035 | 38.1987 | 0.034379 |  | 62.069 | 100
19980909063000 | 1998-09-09 06:30 | 520.065 |  | 2.735 | 149.755 | 154.137 | 152.37 | 150.919 |  | 1084.531 | 1173.367 |  | 5.9219 | 4.1152 | 6.2837 | 6.2737 | 5.6604 | 5.7847 | 5.5444 | 5.6572 | 45.2412 | 0.040717 |  | 62.069 | 100
19980909070000 | 1998-09-09 07:00 | 527.064 |  | 0.078 | 150.218 | 151.104 | 152.882 | 148.381 |  | 1079.698 | 1165.95 |  | 6.1096 | 4.0642 | 6.4927 | 6.5042 | 5.8069 | 5.9402 | 5.6848 | 5.8274 | 46.43 | 0.041787 |  | 62.069 | 100
19980909073000 | 1998-09-09 07:30 | 523.735 |  | 2.489 | 149.078 | 150.845 | 151.234 | 147.132 |  | 1075.281 | 1167.367 |  | 5.9983 | 6.0684 | 5.3308 | 6.3257 | 5.7161 | 5.8235 | 5.5825 | 5.7168 | 46.5621 | 0.041906 |  | 62.069 | 100
19980909080000 | 1998-09-09 08:00 | 521.9 |  | 0.079 | 148.527 | 151.056 | 150.892 | 148.333 |  | 1075.114 | 1156.45 |  | 6.0029 | 6.0967 | 5.3276 | 6.3638 | 5.7283 | 5.854 | 5.6023 | 5.7319 | 46.7075 | 0.042037 |  | 62.069 | 100
19980909083000 | 1998-09-09 08:30 | 524.679 |  | 2.489 | 148.565 | 151.887 | 151.342 | 148.422 |  | 1077.614 | 1160.283 |  | 6.0403 | 6.1096 | 5.3657 | 6.3828 | 5.7449 | 5.854 | 5.6145 | 5.7458 | 46.8576 | 0.042172 |  | 62.069 | 100
19980909090000 | 1998-09-09 09:00 | 523.368 |  | 0.082 | 148.844 | 151.913 | 151.242 | 148.943 |  | 1078.031 | 1161.2 |  | 6.0457 | 6.105 | 5.3635 | 6.3796 | 5.748 | 5.8564 | 5.6055 | 5.7458 | 46.8495 | 0.042165 |  | 62.069 | 100
19980909093000 | 1998-09-09 09:30 | 526.304 |  | 2.121 | 148.861 | 151.758 | 151.111 | 148.788 |  | 1085.198 | 1173.2 |  | 6.0378 | 6.1279 | 5.3682 | 6.3896 | 5.752 | 5.8625 | 5.6177 | 5.7542 | 46.9099 | 0.042219 |  | 62.069 | 100
19980909100000 | 1998-09-09 10:00 | 525.098 |  | 0.08 | 148.782 | 150.856 | 151.088 | 148.133 |  | 1084.031 | 1166.033 |  | 6.0334 | 6.105 | 5.384 | 6.3569 | 5.7502 | 5.8547 | 5.6084 | 5.7305 | 46.8231 | 0.042141 |  | 62.069 | 100
19980909103000 | 1998-09-09 10:30 | 571.34 |  | 2.488 | 148.582 | 153.997 | 151.022 | 150.531 |  | 1188.784 | 1295.787 |  | 6.5332 | 6.6536 | 5.8708 | 7.0596 | 6.2148 | 6.3469 | 6.0798 | 6.2478 | 51.0065 | 0.045906 |  | 62.069 | 100
19980909110000 | 1998-09-09 11:00 | 577.815 |  | 0.157 | 150.034 | 152.434 | 152.463 | 148.226 |  | 1202.035 | 1309.288 |  | 6.5566 | 6.6528 | 5.8906 | 7.0459 | 6.2432 | 6.3469 | 6.0852 | 6.2546 | 51.0758 | 0.045968 |  | 62.069 | 100
19980909113000 | 1998-09-09 11:30 | 575.744 |  | 2.614 | 148.53 | 151.129 | 150.798 | 148.159 |  | 1199.118 | 1310.704 |  | 6.5239 | 6.6353 | 5.8557 | 7.032 | 6.2004 | 6.3218 | 6.0601 | 6.2271 | 50.8563 | 0.045771 |  | 62.069 | 100
19980909120000 | 1998-09-09 12:00 | 571.183 |  | 0.158 | 148.711 | 151.093 | 150.955 | 148.865 |  | 1197.451 | 1303.621 |  | 6.4478 | 6.5217 | 6.9106 | 6.884 | 6.1348 | 6.2349 | 5.9731 | 6.1387 | 51.2456 | 0.046121 |  | 62.069 | 100
19980909123000 | 1998-09-09 12:30 | 574.329 |  | 1.431 | 148.903 | 150.845 | 151.309 | 148.37 |  | 1201.701 | 1316.038 |  | 6.4514 | 6.5332 | 6.9214 | 6.9055 | 6.1448 | 6.2485 | 5.9807 | 6.1433 | 51.3288 | 0.046196 |  | 62.069 | 100
19980909130000 | 1998-09-09 13:00 | 577.134 |  | 0.16 | 148.183 | 151.665 | 151 | 147.458 |  | 1203.201 | 1311.788 |  | 6.4407 | 6.5278 | 6.9299 | 6.884 | 6.1348 | 6.2371 | 5.9761 | 6.1333 | 51.2637 | 0.046137 |  | 62.069 | 100
19980909133000 | 1998-09-09 13:30 | 576.19 |  | 2.496 | 148.582 | 151.795 | 150.868 | 148.577 |  | 1197.201 | 1301.787 |  | 6.4041 | 6.488 | 6.8604 | 6.8313 | 6.0928 | 6.2051 | 5.938 | 6.0974 | 50.9171 | 0.045825 |  | 62.069 | 100
19980909140000 | 1998-09-09 14:00 | 575.325 |  | 0.157 | 148.698 | 151.444 | 151.148 | 148.226 |  | 1195.118 | 1300.537 |  | 6.3857 | 6.479 | 6.8367 | 6.8452 | 6.0708 | 6.1875 | 5.9326 | 6.0823 | 50.8198 | 0.045738 |  | 62.069 | 100
19980909143000 | 1998-09-09 14:30 | 573.7 |  | 1.879 | 149.151 | 151.676 | 151.518 | 148.458 |  | 1200.451 | 1313.538 |  | 6.4377 | 6.5239 | 6.9207 | 6.8901 | 6.1204 | 6.2363 | 5.9724 | 6.1287 | 51.2302 | 0.046107 |  | 62.069 | 100
19980909150000 | 1998-09-09 15:00 | 577.92 |  | 0 | 148.456 | 148.994 | 150.988 | 146.272 |  | 1176.034 | 1277.953 |  | 6.4363 | 6.5139 | 6.9275 | 6.9001 | 6.1355 | 6.2485 | 5.98 | 6.1287 | 51.2705 | 0.046143 |  | 62.069 | 100
19980909153000 | 1998-09-09 15:30 | 577.737 |  | 1.876 | 147.719 | 151.588 | 150.101 | 147.875 |  | 1184.117 | 1292.87 |  | 6.4141 | 6.5156 | 6.9063 | 6.8757 | 6.1182 | 6.2317 | 5.9761 | 6.1204 | 51.1581 | 0.046042 |  | 62.069 | 100
19980909160000 | 1998-09-09 16:00 | 580.673 |  | 0.082 | 149.057 | 152.094 | 151.376 | 148.876 |  | 1186.534 | 1288.37 |  | 6.4521 | 6.5354 | 6.9404 | 6.8826 | 6.147 | 6.26 | 5.9907 | 6.1387 | 51.3469 | 0.046212 |  | 62.069 | 100
19980909163000 | 1998-09-09 16:30 | 623.218 |  | 2.489 | 149.294 | 152.537 | 151.935 | 149.814 |  | 1279.203 | 1410.124 |  | 6.8611 | 6.9688 | 7.4365 | 7.4829 | 6.5239 | 6.6521 | 6.3745 | 6.5552 | 54.855 | 0.04937 |  | 62.069 | 100
19980909170000 | 1998-09-09 17:00 | 629.536 |  | 0.157 | 149.159 | 152.016 | 151.737 | 148.303 |  | 1289.954 | 1416.207 |  | 6.9131 | 6.9961 | 7.5127 | 7.5098 | 6.582 | 6.6833 | 6.3911 | 6.5828 | 55.1709 | 0.049654 |  | 62.069 | 100
19980909173000 | 1998-09-09 17:30 | 646.103 |  | 2.247 | 148.803 | 152.434 | 151.376 | 148.226 |  | 1338.955 | 1477.126 |  | 7.1687 | 7.261 | 7.8071 | 7.8699 | 6.8201 | 6.9465 | 6.6431 | 6.8428 | 57.3592 | 0.051623 |  | 62.069 | 100
19980909180000 | 1998-09-09 18:00 | 652.474 |  | 0.402 | 149.092 | 151.614 | 151.596 | 147.158 |  | 1336.288 | 1466.959 |  | 7.1228 | 7.2327 | 7.7554 | 7.8157 | 6.7703 | 6.8994 | 6.6101 | 6.8 | 57.0064 | 0.051306 |  | 62.069 | 100
19980909183000 | 1998-09-09 18:30 | 618.526 |  | 1.756 | 148.202 | 152.563 | 150.59 | 147.86 |  | 1229.369 | 1350.872 |  | 6.7458 | 6.8306 | 7.2991 | 7.3022 | 6.3965 | 6.4895 | 6.2234 | 6.4119 | 53.699 | 0.048329 |  | 62.069 | 100
19980909190000 | 1998-09-09 19:00 | 607.726 |  | 19.931 | 148.285 | 151.052 | 150.122 | 147.834 |  | 1235.035 | 1354.456 |  | 6.7178 | 6.8054 | 7.28 | 7.2769 | 6.408 | 6.5088 | 6.2302 | 6.4041 | 53.6312 | 0.048268 |  | 62.069 | 100
19980909193000 | 1998-09-09 19:30 | 607.935 |  | 1.997 | 148.48 | 151.795 | 150.896 | 147.834 |  | 1239.202 | 1364.539 |  | 6.7078 | 6.7817 | 7.2419 | 7.2297 | 6.3843 | 6.4888 | 6.2097 | 6.3828 | 53.4267 | 0.048084 |  | 62.069 | 100
19980909200000 | 1998-09-09 20:00 | 608.512 |  | 0.079 | 148.861 | 152.186 | 151.116 | 148.226 |  | 1234.202 | 1352.705 |  | 6.6887 | 6.7695 | 7.2205 | 7.2244 | 6.3652 | 6.4773 | 6.2043 | 6.3699 | 53.3198 | 0.047988 |  | 62.069 | 100
19980909203000 | 1998-09-09 20:30 | 575.115 |  | 1.51 | 148.666 | 151.093 | 150.882 | 147.132 |  | 1170.95 | 1275.12 |  | 6.4155 | 6.4834 | 6.8923 | 6.8574 | 6.1067 | 6.2112 | 5.9509 | 6.0945 | 51.0119 | 0.045911 |  | 62.069 | 100
19980909210000 | 1998-09-09 21:00 | 577.16 |  | 0 | 148.342 | 151.289 | 150.543 | 148.566 |  | 1173.034 | 1277.537 |  | 6.4216 | 6.5278 | 6.9238 | 6.9023 | 6.1326 | 6.2576 | 5.9944 | 6.1409 | 51.301 | 0.046171 |  | 62.069 | 100
19980909213000 | 1998-09-09 21:30 | 530.105 |  | 1.881 | 148.624 | 151.495 | 151.199 | 148.525 |  | 1061.114 | 1150.616 |  | 5.7563 | 5.7961 | 6.1013 | 5.9875 | 5.4856 | 5.5557 | 5.3391 | 5.4673 | 45.4889 | 0.04094 |  | 62.069 | 100
19980909220000 | 1998-09-09 22:00 | 525.229 |  | 0 | 147.847 | 150.923 | 150.288 | 147.458 |  | 1058.53 | 1149.7 |  | 5.8342 | 5.9006 | 6.1807 | 6.1121 | 5.5725 | 5.6816 | 5.4497 | 5.5488 | 46.2802 | 0.041652 |  | 62.069 | 100
19980909223000 | 1998-09-09 22:30 | 479.774 |  | 1.635 | 148.348 | 151.418 | 150.722 | 148.695 |  | 939.11 | 1014.696 |  | 5.2759 | 5.3467 | 5.5139 | 5.3413 | 5.0684 | 5.165 | 4.9614 | 5.0178 | 41.6904 | 0.037521 |  | 62.069 | 100
19980909230000 | 1998-09-09 23:00 | 426.742 |  | 0 | 147.935 | 150.649 | 150.218 | 148.422 |  | 871.108 | 937.194 |  | 4.8989 | 4.9844 | 5.0537 | 4.8752 | 4.7104 | 4.8813 | 4.6838 | 4.6724 | 38.7601 | 0.034884 |  | 62.069 | 100
19980909233000 | 1998-09-09 23:30 | 394.394 |  | 1.757 | 147.71 | 151.64 | 150.05 | 149.164 |  | 777.439 | 837.191 |  | 4.3945 | 4.4397 | 4.4702 | 4.168 | 4.1863 | 4.3374 | 4.1572 | 4.1267 | 34.28 | 0.030852 |  | 62.069 | 100
19980910000000 | 1998-09-10 | 346.631 |  | 0 | 147.965 | 149.896 | 150.423 | 147.668 |  | 723.104 | 762.605 |  | 4.0337 | 4.071 | 3.9644 | 3.7195 | 3.869 | 4.1274 | 3.9506 | 3.8132 | 31.5488 | 0.028394 |  | 62.069 | 100
19980910003000 | 1998-09-10 00:30 | 338.453 |  | 1.761 | 147.872 | 150.077 | 150.336 | 149.582 |  | 719.437 | 761.772 |  | 4.0115 | 4.0513 | 3.9353 | 3.7026 | 3.8461 | 4.1123 | 3.9323 | 3.7843 | 31.3757 | 0.028238 |  | 62.069 | 100
19980910010000 | 1998-09-10 01:00 | 333.944 |  | 0 | 148.5 | 151.732 | 150.809 | 149.257 |  | 707.104 | 745.855 |  | 3.9705 | 3.9941 | 3.8911 | 3.6279 | 3.7988 | 4.0481 | 3.8843 | 3.7324 | 30.9472 | 0.027852 |  | 62.069 | 100
19980910013000 | 1998-09-10 01:30 | 335.019 |  | 2.004 | 148.41 | 151.226 | 150.73 | 149.989 |  | 711.854 | 755.855 |  | 3.975 | 4.001 | 3.885 | 3.6637 | 3.8247 | 4.0452 | 3.8843 | 2.6871 | 29.966 | 0.026969 |  | 62.069 | 100
19980910020000 | 1998-09-10 02:00 | 333.865 |  | 0 | 148.693 | 150.809 | 151.275 | 149.819 |  | 702.687 | 739.021 |  | 4.4404 | 4.5425 | 4.4915 | 4.2473 | 4.261 | 4.4312 | 4.2886 | 0.0032 | 30.7057 | 0.027635 |  | 62.069 | 100
19980910023000 | 1998-09-10 02:30 | 331.427 |  | 2.127 | 148.942 | 151.943 | 151.314 | 149.468 |  | 707.437 | 741.355 |  | 3.9926 | 4.0879 | 3.9132 | 3.705 | 3.8132 | 4.0186 | 3.8904 | 3.6829 | 31.1038 | 0.027993 |  | 62.069 | 100
19980910030000 | 1998-09-10 03:00 | 331.034 |  | 0 | 149.333 | 150.458 | 151.644 | 149.468 |  | 722.521 | 760.605 |  | 4.0071 | 4.0276 | 3.9536 | 3.6897 | 3.8423 | 3.9994 | 3.8812 | 3.7507 | 31.1516 | 0.028036 |  | 62.069 | 100
19980910033000 | 1998-09-10 03:30 | 328.177 |  | 2.25 | 148.86 | 151.252 | 151.347 | 149.272 |  | 734.854 | 783.356 |  | 4.0391 | 4.0994 | 4.0208 | 3.801 | 3.8942 | 4.0444 | 3.9369 | 3.8171 | 31.6529 | 0.028488 |  | 62.069 | 100
19980910040000 | 1998-09-10 04:00 | 321.544 |  | 0 | 149.038 | 151.185 | 151.225 | 149.948 |  | 728.104 | 768.522 |  | 4.0444 | 4.0703 | 4.0093 | 3.7629 | 3.8789 | 4.0186 | 3.9094 | 3.8033 | 31.4971 | 0.028347 |  | 62.069 | 100
19980910043000 | 1998-09-10 04:30 | 324.166 |  | 1.882 | 148.575 | 150.458 | 150.919 | 148.725 |  | 739.605 | 784.356 |  | 4.0559 | 4.1184 | 4.0322 | 3.8346 | 3.9003 | 4.0566 | 3.9697 | 3.8354 | 31.8031 | 0.028623 |  | 62.069 | 100
19980910050000 | 1998-09-10 05:00 | 338.4 |  | 20.711 | 149.075 | 152.438 | 151.281 | 150.705 |  | 757.355 | 804.273 |  | 4.313 | 4.3306 | 4.3572 | 4.1191 | 4.1284 | 4.2419 | 4.113 | 2.6697 | 32.2729 | 0.029046 |  | 62.069 | 100
19980910053000 | 1998-09-10 05:30 | 335.412 |  | 2.249 | 148.977 | 150.21 | 151.553 | 148.478 |  | 755.272 | 799.106 |  | 4.1497 | 4.1909 | 4.1367 | 3.9216 | 3.9597 | 4.123 | 4.0115 | 3.9056 | 32.3987 | 0.029159 |  | 62.069 | 100
19980910060000 | 1998-09-10 06:00 | 335.097 |  | 0 | 148.124 | 151.396 | 150.754 | 149.911 |  | 765.855 | 814.857 |  | 4.2649 | 4.3672 | 4.3037 | 3.4204 | 4.1016 | 4.2588 | 4.1284 | 2.8367 | 31.6817 | 0.028514 |  | 62.069 | 100
19980910063000 | 1998-09-10 06:30 | 368.756 |  | 2.986 | 148.636 | 151.525 | 151.428 | 148.308 |  | 842.358 | 904.776 |  | 4.593 | 4.686 | 4.7524 | 4.5547 | 4.4336 | 4.5601 | 4.4236 | 4.271 | 36.2744 | 0.032647 |  | 62.069 | 100
19980910070000 | 1998-09-10 07:00 | 521.009 |  | 0.406 | 149.425 | 152.464 | 151.475 | 149.989 |  | 1124.282 | 1219.118 |  | 6.0173 | 6.1372 | 6.4294 | 6.4492 | 5.7458 | 5.8823 | 5.6489 | 5.7258 | 48.0359 | 0.043232 |  | 62.069 | 100
19980910073000 | 1998-09-10 07:30 | 631.24 |  | 1.262 | 150.908 | 154.078 | 153.513 | 150.365 |  | 1294.954 | 1432.041 |  | 7.0474 | 7.1328 | 7.6096 | 7.6309 | 6.6858 | 6.8191 | 6.5254 | 6.678 | 56.129 | 0.050516 |  | 62.069 | 100
19980910080000 | 1998-09-10 08:00 | 645.815 |  | 0.284 | 150.115 | 152.212 | 152.836 | 148.252 |  | 1312.788 | 1444.458 |  | 7.0847 | 7.168 | 7.6624 | 7.7134 | 6.6995 | 6.8298 | 6.5286 | 6.7261 | 56.4125 | 0.050771 |  | 62.069 | 100
19980910083000 | 1998-09-10 08:30 | 646.287 |  | 2.489 | 148.869 | 151.769 | 151.312 | 147.561 |  | 1316.454 | 1451.708 |  | 7.1038 | 7.1877 | 7.7095 | 7.7698 | 6.7246 | 6.8506 | 6.553 | 6.7559 | 56.6549 | 0.050989 |  | 62.069 | 100
19980910090000 | 1998-09-10 09:00 | 648.935 |  | 0.402 | 148.68 | 151.861 | 151.079 | 147.158 |  | 1313.871 | 1445.708 |  | 7.0747 | 7.1885 | 7.6882 | 7.7615 | 6.7207 | 6.8445 | 6.5515 | 6.759 | 56.5886 | 0.05093 |  | 62.069 | 100
19980910093000 | 1998-09-10 09:30 | 650.272 |  | 20.739 | 148.481 | 151.041 | 150.654 | 147.576 |  | 1313.788 | 1446.542 |  | 7.1077 | 7.1824 | 7.7263 | 7.7568 | 6.7361 | 6.8384 | 6.5361 | 6.7483 | 56.6321 | 0.050969 |  | 62.069 | 100
19980910100000 | 1998-09-10 10:00 | 645.081 |  | 0.199 | 148.654 | 153.032 | 151.057 | 148.082 |  | 1312.038 | 1447.125 |  | 7.0955 | 7.1853 | 7.7546 | 7.7759 | 6.739 | 6.8557 | 6.553 | 6.7688 | 56.7278 | 0.051055 |  | 62.069 | 100
19980910103000 | 1998-09-10 10:30 | 645.474 |  | 2 | 149.174 | 151.444 | 151.545 | 148.226 |  | 1313.371 | 1448.625 |  | 7.0854 | 7.1792 | 7.6599 | 7.7188 | 6.7354 | 6.8506 | 6.5537 | 6.739 | 56.522 | 0.05087 |  | 62.069 | 100
19980910110000 | 1998-09-10 11:00 | 645.736 |  | 0.161 | 148.655 | 151.495 | 151.18 | 148.278 |  | 1312.621 | 1445.208 |  | 7.1106 | 7.1968 | 7.7051 | 7.7378 | 6.7476 | 6.8679 | 6.5674 | 6.7537 | 56.6869 | 0.051018 |  | 62.069 | 100
19980910113000 | 1998-09-10 11:30 | 645.579 |  | 2.122 | 148.582 | 151.702 | 151.114 | 147.742 |  | 1313.621 | 1453.458 |  | 7.126 | 7.2014 | 7.718 | 7.7446 | 6.762 | 6.8757 | 6.572 | 6.7673 | 56.767 | 0.05109 |  | 62.069 | 100
19980910120000 | 1998-09-10 12:00 | 644.452 |  | 0.163 | 148.64 | 152.46 | 151.107 | 147.509 |  | 1313.621 | 1446.125 |  | 7.1199 | 7.2 | 7.7163 | 7.7507 | 6.7559 | 6.874 | 6.5713 | 6.7688 | 56.7569 | 0.051081 |  | 62.069 | 100
19980910123000 | 1998-09-10 12:30 | 646.418 |  | 2.369 | 149.009 | 151.248 | 151.278 | 148.03 |  | 1315.788 | 1453.958 |  | 7.1243 | 7.1946 | 7.7065 | 7.7346 | 6.7498 | 6.8657 | 6.562 | 6.7627 | 56.7002 | 0.05103 |  | 62.069 | 100
19980910130000 | 1998-09-10 13:00 | 647.965 |  | 0.157 | 148.481 | 152.238 | 151.248 | 147.535 |  | 1311.871 | 1451.208 |  | 7.145 | 7.2388 | 7.7485 | 7.7913 | 6.7864 | 6.9077 | 6.6101 | 6.7986 | 57.0264 | 0.051324 |  | 62.069 | 100
19980910133000 | 1998-09-10 13:30 | 650.088 |  | 2.125 | 148.752 | 151.274 | 151.201 | 147.313 |  | 1308.371 | 1443.791 |  | 7.1182 | 7.196 | 7.7102 | 7.7568 | 6.7512 | 6.8779 | 6.572 | 6.7673 | 56.7496 | 0.051075 |  | 62.069 | 100
19980910140000 | 1998-09-10 14:00 | 648.043 |  | 0.406 | 148.474 | 152.434 | 151.007 | 147.236 |  | 1315.204 | 1446.125 |  | 7.0815 | 7.1694 | 7.676 | 7.6997 | 6.7207 | 6.8496 | 6.5491 | 6.7397 | 56.4857 | 0.050837 |  | 62.069 | 100
19980910143000 | 1998-09-10 14:30 | 646.811 |  | 2.123 | 148.809 | 151.599 | 150.856 | 147.143 |  | 1309.204 | 1440.125 |  | 7.103 | 7.1809 | 7.6897 | 7.7378 | 6.7444 | 6.8787 | 6.5674 | 6.7642 | 56.6661 | 0.050999 |  | 62.069 | 100
19980910150000 | 1998-09-10 15:00 | 644.452 |  | 0.16 | 148.855 | 152.305 | 150.917 | 147.849 |  | 1314.038 | 1444.208 |  | 7.113 | 7.2 | 7.7051 | 7.7393 | 6.7512 | 6.8811 | 6.5828 | 6.772 | 56.7445 | 0.05107 |  | 62.069 | 100
19980910153000 | 1998-09-10 15:30 | 642.905 |  | 2.493 | 149.037 | 151.573 | 151.476 | 148.108 |  | 1312.871 | 1449.542 |  | 7.1228 | 7.2 | 7.6951 | 7.7393 | 6.7681 | 6.8765 | 6.5803 | 6.7659 | 56.748 | 0.051073 |  | 62.069 | 100
19980910160000 | 1998-09-10 16:00 | 609.036 |  | 0.076 | 148.485 | 150.428 | 150.866 | 146.22 |  | 1238.286 | 1351.122 |  | 6.7329 | 6.8269 | 7.2549 | 7.2815 | 6.3958 | 6.5332 | 6.2463 | 6.4155 | 53.687 | 0.048318 |  | 62.069 | 100
19980910163000 | 1998-09-10 16:30 | 577.553 |  | 1.758 | 147.589 | 151.104 | 149.684 | 147.638 |  | 1167.867 | 1266.62 |  | 6.3516 | 6.437 | 6.7849 | 6.7666 | 6.0371 | 6.167 | 5.915 | 6.0327 | 50.4919 | 0.045443 |  | 62.069 | 100
19980910170000 | 1998-09-10 17:00 | 574.276 |  | 0.078 | 148.062 | 151.248 | 150.39 | 148.03 |  | 1149.533 | 1245.702 |  | 6.2837 | 6.3843 | 6.7048 | 6.6956 | 5.9685 | 6.1279 | 5.8701 | 5.9792 | 50.0141 | 0.045013 |  | 62.069 | 100
19980910173000 | 1998-09-10 17:30 | 573.752 |  | 1.998 | 149.178 | 151.691 | 151.249 | 148.968 |  | 1163.95 | 1272.87 |  | 6.3477 | 6.4507 | 6.8018 | 6.7864 | 6.0364 | 6.2012 | 5.9387 | 6.0457 | 50.6086 | 0.045548 |  | 62.069 | 100
19980910180000 | 1998-09-10 18:00 | 643.534 |  | 0.163 | 149.645 | 153.099 | 152.348 | 149.386 |  | 1311.704 | 1444.375 |  | 7.0955 | 7.1885 | 7.6858 | 7.7217 | 6.7361 | 6.8794 | 6.5803 | 6.7468 | 56.6341 | 0.050971 |  | 62.069 | 100
19980910183000 | 1998-09-10 18:30 | 645.081 |  | 2.614 | 149.39 | 152.083 | 151.972 | 148.123 |  | 1307.704 | 1442.458 |  | 7.1084 | 7.1946 | 7.6843 | 7.7249 | 6.7437 | 6.8794 | 6.5759 | 6.762 | 56.6732 | 0.051006 |  | 62.069 | 100
19980910190000 | 1998-09-10 19:00 | 642.591 |  | 0.078 | 148.442 | 151.47 | 151.103 | 147.509 |  | 1318.288 | 1452.042 |  | 7.1282 | 7.238 | 7.7241 | 7.8079 | 6.7773 | 6.9246 | 6.6201 | 6.8086 | 57.0288 | 0.051326 |  | 62.069 | 100
19980910193000 | 1998-09-10 19:30 | 641.385 |  | 21.892 | 148.831 | 151.861 | 151.028 | 147.653 |  | 1311.121 | 1449.125 |  | 7.1045 | 7.2151 | 7.6814 | 7.7576 | 6.7422 | 6.8962 | 6.5979 | 6.7886 | 56.7835 | 0.051105 |  | 62.069 | 100
19980910200000 | 1998-09-10 20:00 | 606.966 |  | 0 | 148.499 | 151.026 | 150.919 | 146.323 |  | 1236.952 | 1355.539 |  | 6.7375 | 6.813 | 7.2463 | 7.2603 | 6.3928 | 6.5186 | 6.2402 | 6.4026 | 53.6113 | 0.04825 |  | 62.069 | 100
19980910203000 | 1998-09-10 20:30 | 606.52 |  | 2.001 | 147.928 | 151.588 | 150.134 | 147.875 |  | 1230.369 | 1350.205 |  | 6.6658 | 6.7688 | 7.1702 | 7.2021 | 6.344 | 6.4744 | 6.1975 | 6.3599 | 53.1827 | 0.047864 |  | 62.069 | 100
19980910210000 | 1998-09-10 21:00 | 608.093 |  | 0.079 | 148.332 | 152.145 | 151.13 | 147.938 |  | 1233.285 | 1352.039 |  | 6.6682 | 6.7842 | 7.177 | 7.2205 | 6.3501 | 6.4912 | 6.2104 | 6.3752 | 53.2768 | 0.047949 |  | 62.069 | 100
19980910213000 | 1998-09-10 21:30 | 527.877 |  | 2.126 | 147.895 | 150.299 | 150.229 | 145.596 |  | 1078.281 | 1168.784 |  | 5.9595 | 6.0066 | 6.3035 | 6.2356 | 5.6838 | 5.7815 | 5.5344 | 5.6245 | 47.1294 | 0.042416 |  | 62.069 | 100
19980910220000 | 1998-09-10 22:00 | 524.758 |  | 0 | 148.721 | 151.547 | 150.795 | 149.567 |  | 1091.281 | 1177.867 |  | 5.9167 | 5.9846 | 6.2715 | 6.1965 | 5.6533 | 5.771 | 5.5237 | 5.5984 | 46.9157 | 0.042224 |  | 62.069 | 100
19980910223000 | 1998-09-10 22:30 | 478.463 |  | 2.005 | 148.983 | 150.598 | 151.474 | 147.132 |  | 972.945 | 1049.03 |  | 5.3162 | 5.3665 | 5.51 | 5.3467 | 5.0591 | 5.1697 | 4.9653 | 5.0088 | 41.7423 | 0.037568 |  | 62.069 | 100
19980910230000 | 1998-09-10 23:00 | 472.381 |  | 0 | 147.705 | 150.52 | 149.918 | 147.798 |  | 994.529 | 1072.781 |  | 5.4023 | 5.4756 | 5.6199 | 5.5283 | 5.1721 | 5.3223 | 5.0964 | 5.1094 | 42.7263 | 0.038454 |  | 62.069 | 100
19980910233000 | 1998-09-10 23:30 | 365.453 |  | 1.881 | 148.11 | 148.788 | 150.478 | 147.055 |  | 807.607 | 869.025 |  | 4.3992 | 4.4387 | 4.3938 | 4.1665 | 4.2114 | 4.4365 | 4.2505 | 4.123 | 34.4196 | 0.030978 |  | 62.069 | 100
19980911000000 | 1998-09-11 | 371.089 |  | 20.538 | 146.729 | 148.396 | 149.087 | 146.168 |  | 742.938 | 783.106 |  | 4.1091 | 4.1519 | 4.0918 | 3.8514 | 3.9742 | 4.165 | 3.9773 | 3.856 | 32.1767 | 0.028959 |  | 62.069 | 100
19980911003000 | 1998-09-11 00:30 | 339.58 |  | 2.617 | 147.267 | 149.323 | 149.529 | 148.581 |  | 722.104 | 755.855 |  | 4.0527 | 4.0857 | 3.9667 | 3.6965 | 3.8926 | 4.1245 | 3.9445 | 3.7988 | 31.562 | 0.028406 |  | 62.069 | 100
19980911010000 | 1998-09-11 01:00 | 341.965 |  | 0 | 147.943 | 150.458 | 150.493 | 148.478 |  | 715.437 | 745.355 |  | 4.1223 | 4.158 | 4.0674 | 3.1991 | 3.9681 | 4.2031 | 4.0276 | 3.8538 | 31.5994 | 0.028439 |  | 62.069 | 100
19980911013000 | 1998-09-11 01:30 | 338.951 |  | 2.495 | 148.954 | 151.263 | 151.019 | 150.273 |  | 719.604 | 753.522 |  | 4.0825 | 4.0764 | 4.0107 | 3.7179 | 3.8942 | 4.1108 | 3.9484 | 3.7949 | 31.6358 | 0.028472 |  | 62.069 | 100
19980911020000 | 1998-09-11 02:00 | 335.674 |  | 0 | 148.802 | 150.587 | 151.2 | 148.607 |  | 729.271 | 763.605 |  | 4.1016 | 4.1145 | 4.0193 | 3.7576 | 3.9301 | 4.1267 | 3.9689 | 3.8247 | 31.8434 | 0.028659 |  | 62.069 | 100
19980911023000 | 1998-09-11 02:30 | 330.457 |  | 2.126 | 148.714 | 150.901 | 151.002 | 149.664 |  | 729.521 | 768.022 |  | 4.084 | 4.1274 | 3.9888 | 3.7606 | 3.9109 | 4.1047 | 3.959 | 3.8263 | 31.7617 | 0.028586 |  | 62.069 | 100
19980911030000 | 1998-09-11 03:00 | 339.37 |  | 0 | 148.92 | 152.294 | 151.319 | 151.056 |  | 735.938 | 776.272 |  | 4.1414 | 4.1885 | 4.1047 | 3.8209 | 3.9651 | 4.145 | 4.0032 | 3.8949 | 32.2637 | 0.029037 |  | 62.069 | 100
19980911033000 | 1998-09-11 03:30 | 334.887 |  | 2.251 | 148.749 | 150.834 | 151.268 | 149.844 |  | 731.438 | 776.772 |  | 4.1199 | 4.1748 | 4.071 | 3.8446 | 3.9529 | 4.1353 | 3.9888 | 3.8728 | 32.1601 | 0.028944 |  | 62.069 | 100
19980911040000 | 1998-09-11 04:00 | 336.434 |  | 0 | 148.645 | 150.794 | 151.114 | 149.556 |  | 736.104 | 775.606 |  | 4.1353 | 4.1694 | 4.1055 | 3.8552 | 3.9636 | 4.1313 | 3.9895 | 3.8712 | 32.221 | 0.028999 |  | 62.069 | 100
19980911043000 | 1998-09-11 04:30 | 334.599 |  | 2.373 | 148.646 | 150.509 | 151.158 | 149.024 |  | 729.354 | 768.939 |  | 4.0864 | 4.1436 | 4.0391 | 3.8071 | 3.9186 | 4.104 | 3.9674 | 3.843 | 31.9092 | 0.028718 |  | 62.069 | 100
19980911050000 | 1998-09-11 05:00 | 333 |  | 0 | 149.069 | 151.81 | 151.716 | 150.324 |  | 748.021 | 789.523 |  | 4.0908 | 4.1772 | 4.0359 | 3.84 | 3.9216 | 4.1199 | 3.985 | 3.8735 | 32.0439 | 0.02884 |  | 62.069 | 100
19980911053000 | 1998-09-11 05:30 | 394.341 |  | 2.988 | 149.078 | 152.33 | 151.457 | 150.35 |  | 854.275 | 913.943 |  | 4.6868 | 4.7966 | 4.8188 | 4.6479 | 4.4968 | 4.6128 | 4.458 | 4.4358 | 36.9535 | 0.033258 |  | 62.069 | 100
19980911060000 | 1998-09-11 06:00 | 408.025 |  | 0 | 149.226 | 150.69 | 151.678 | 149.7 |  | 869.775 | 930.11 |  | 4.7715 | 4.8264 | 4.8958 | 4.6975 | 4.5586 | 4.6899 | 4.509 | 4.4968 | 37.4455 | 0.033701 |  | 62.069 | 100
19980911063000 | 1998-09-11 06:30 | 404.198 |  | 2.374 | 148.998 | 152.15 | 151.49 | 148.932 |  | 873.942 | 938.027 |  | 4.7478 | 4.8447 | 4.8494 | 4.7058 | 4.5525 | 4.7073 | 4.5242 | 4.4968 | 37.4285 | 0.033686 |  | 62.069 | 100
19980911070000 | 1998-09-11 07:00 | 418.773 |  | 0 | 148.589 | 149.035 | 150.979 | 146.56 |  | 890.609 | 954.027 |  | 4.8867 | 4.9844 | 5.0178 | 4.9119 | 4.7051 | 4.8782 | 4.6899 | 4.644 | 38.718 | 0.034846 |  | 62.069 | 100
19980911073000 | 1998-09-11 07:30 | 556.005 |  | 3.114 | 148.78 | 153.934 | 151.063 | 152.201 |  | 1164.367 | 1268.036 |  | 6.3843 | 6.4758 | 6.8384 | 6.8696 | 6.0693 | 6.2141 | 5.9441 | 6.0632 | 50.8588 | 0.045773 |  | 62.069 | 100
19980911080000 | 1998-09-11 08:00 | 616.167 |  | 0.408 | 150.617 | 152.671 | 153.228 | 149.453 |  | 1289.037 | 1417.874 |  | 6.9045 | 7.0229 | 7.4441 | 7.5806 | 6.5688 | 6.7275 | 6.4331 | 6.6162 | 55.2977 | 0.049768 |  | 62.069 | 100
19980911083000 | 1998-09-11 08:30 | 645.736 |  | 2.619 | 150.198 | 152.315 | 152.791 | 149.345 |  | 1333.705 | 1470.959 |  | 7.167 | 7.2488 | 7.7461 | 7.8293 | 6.7886 | 6.9199 | 6.6155 | 6.8269 | 57.1421 | 0.051428 |  | 62.069 | 100
19980911090000 | 1998-09-11 09:00 | 648.201 |  | 0.406 | 149.338 | 151.64 | 151.776 | 147.184 |  | 1326.371 | 1461.875 |  | 7.1343 | 7.2251 | 7.7385 | 7.7996 | 6.7742 | 6.9055 | 6.5933 | 6.8093 | 56.9798 | 0.051282 |  | 62.069 | 100
19980911093000 | 1998-09-11 09:30 | 648.227 |  | 2.127 | 148.704 | 151.758 | 151.21 | 148.045 |  | 1329.621 | 1466.125 |  | 7.1541 | 7.2488 | 7.7615 | 7.824 | 6.7939 | 6.9199 | 6.6187 | 6.8252 | 57.1461 | 0.051431 |  | 62.069 | 100
19980911100000 | 1998-09-11 10:00 | 645.841 |  | 20.912 | 148.954 | 152.005 | 151.377 | 147.55 |  | 1331.288 | 1468.375 |  | 7.1816 | 7.2664 | 7.792 | 7.8628 | 6.8062 | 6.9558 | 6.6506 | 6.8506 | 57.366 | 0.051629 |  | 62.069 | 100
19980911103000 | 1998-09-11 10:30 | 650.665 |  | 2.125 | 148.651 | 151.913 | 151.343 | 147.458 |  | 1331.122 | 1466.125 |  | 7.1633 | 7.2686 | 7.769 | 7.8599 | 6.813 | 6.9543 | 6.6421 | 6.8374 | 57.3076 | 0.051577 |  | 62.069 | 100
19980911110000 | 1998-09-11 11:00 | 647.729 |  | 0.163 | 148.652 | 151.51 | 151.221 | 147.55 |  | 1323.121 | 1455.208 |  | 7.126 | 7.2395 | 7.7339 | 7.8071 | 6.7795 | 6.9229 | 6.6216 | 6.8176 | 57.0481 | 0.051343 |  | 62.069 | 100
19980911113000 | 1998-09-11 11:30 | 651.399 |  | 2.373 | 148.45 | 151.222 | 150.708 | 146.272 |  | 1314.954 | 1449.958 |  | 7.1213 | 7.2402 | 7.7195 | 7.811 | 6.762 | 6.9238 | 6.6108 | 6.8169 | 57.0055 | 0.051305 |  | 62.069 | 100
19980911120000 | 1998-09-11 12:00 | 647.467 |  | 0.159 | 148.747 | 152.526 | 151.244 | 148.813 |  | 1335.788 | 1469.959 |  | 7.126 | 7.2449 | 7.7339 | 7.8416 | 6.7688 | 6.9382 | 6.6299 | 6.8352 | 57.1185 | 0.051407 |  | 62.069 | 100
19980911123000 | 1998-09-11 12:30 | 646.497 |  | 1.145 | 148.894 | 151.16 | 151.407 | 147.199 |  | 1333.622 | 1464.542 |  | 7.1152 | 7.2244 | 7.718 | 7.8149 | 6.7559 | 6.9314 | 6.623 | 6.8298 | 57.0126 | 0.051311 |  | 62.069 | 100
19980911130000 | 1998-09-11 13:00 | 646.444 |  | 0.167 | 148.645 | 151.614 | 151.06 | 147.901 |  | 1327.121 | 1463.709 |  | 7.1069 | 7.2373 | 7.7058 | 7.8096 | 6.7498 | 6.9099 | 6.6133 | 6.813 | 56.9456 | 0.051251 |  | 62.069 | 100
19980911133000 | 1998-09-11 13:30 | 642.696 |  | 2.497 | 148.765 | 151.355 | 151.21 | 148.385 |  | 1340.455 | 1476.542 |  | 7.1235 | 7.2402 | 7.7173 | 7.8027 | 6.7634 | 6.9199 | 6.6169 | 6.8147 | 56.9986 | 0.051299 |  | 62.069 | 100
19980911140000 | 1998-09-11 14:00 | 648.437 |  | 0.162 | 148.363 | 149.545 | 150.976 | 145.585 |  | 1313.538 | 1443.875 |  | 7.1191 | 7.2351 | 7.7126 | 7.8103 | 6.752 | 6.9153 | 6.6116 | 6.8154 | 56.9714 | 0.051274 |  | 62.069 | 100
19980911143000 | 1998-09-11 14:30 | 648.62 |  | 21.239 | 147.912 | 151.577 | 150.145 | 146.874 |  | 1311.704 | 1445.542 |  | 7.1045 | 7.2236 | 7.7363 | 7.8079 | 6.7566 | 6.9138 | 6.6133 | 6.8108 | 56.9668 | 0.05127 |  | 62.069 | 100
19980911150000 | 1998-09-11 15:00 | 648.672 |  | 0.164 | 148.956 | 152.32 | 151.014 | 147.369 |  | 1319.121 | 1456.875 |  | 7.1121 | 7.2244 | 7.7095 | 7.7996 | 6.7498 | 6.9077 | 6.6018 | 6.804 | 56.9089 | 0.051218 |  | 62.069 | 100
19980911153000 | 1998-09-11 15:30 | 577.134 |  | 2.13 | 148.328 | 149.571 | 150.702 | 145.858 |  | 1184.034 | 1298.621 |  | 6.4392 | 6.5322 | 6.897 | 6.9031 | 6.1182 | 6.2654 | 6.0012 | 6.1318 | 51.2881 | 0.046159 |  | 62.069 | 100
19980911160000 | 1998-09-11 16:00 | 573.857 |  | 0.162 | 147.661 | 150.824 | 149.968 | 146.863 |  | 1175.95 | 1273.453 |  | 6.3552 | 6.4355 | 6.7986 | 6.7932 | 6.0295 | 6.1904 | 5.9297 | 6.0432 | 50.5753 | 0.045518 |  | 62.069 | 100
19980911163000 | 1998-09-11 16:30 | 577.239 |  | 2.256 | 148.501 | 151.943 | 150.836 | 148.725 |  | 1164.533 | 1272.536 |  | 6.3416 | 6.4355 | 6.7917 | 6.7703 | 6.0212 | 6.1965 | 5.938 | 6.0396 | 50.5344 | 0.045481 |  | 62.069 | 100
19980911170000 | 1998-09-11 17:00 | 572.415 |  | 0.08 | 149.319 | 151.566 | 151.657 | 148.843 |  | 1190.367 | 1298.121 |  | 6.3896 | 6.4858 | 6.8506 | 6.8574 | 6.0723 | 6.2363 | 5.9692 | 6.0791 | 50.9403 | 0.045846 |  | 62.069 | 100
19980911173000 | 1998-09-11 17:30 | 572.389 |  | 2.622 | 149.155 | 151.489 | 151.721 | 147.528 |  | 1191.451 | 1303.704 |  | 6.3584 | 6.4392 | 6.8162 | 6.7864 | 6.0493 | 6.2119 | 5.9412 | 6.0525 | 50.6551 | 0.04559 |  | 62.069 | 100
19980911180000 | 1998-09-11 18:00 | 634.674 |  | 0.41 | 149.236 | 152.531 | 151.777 | 148.075 |  | 1306.537 | 1439.041 |  | 6.9534 | 7.0686 | 7.5073 | 7.5959 | 6.6033 | 6.7666 | 6.4607 | 6.6338 | 55.5896 | 0.050031 |  | 62.069 | 100
19980911183000 | 1998-09-11 18:30 | 641.28 |  | 1.885 | 149.322 | 152.412 | 151.969 | 147.462 |  | 1338.455 | 1469.542 |  | 7.0847 | 7.1968 | 7.6746 | 7.7271 | 6.7329 | 6.8855 | 6.5803 | 6.7688 | 56.6507 | 0.050986 |  | 62.069 | 100
19980911190000 | 1998-09-11 19:00 | 642.198 |  | 0.081 | 148.763 | 149.896 | 151.088 | 146.678 |  | 1301.787 | 1429.458 |  | 7.0557 | 7.1648 | 7.6675 | 7.7209 | 6.707 | 6.8704 | 6.5552 | 6.7512 | 56.4927 | 0.050843 |  | 62.069 | 100
19980911193000 | 1998-09-11 19:30 | 642.066 |  | 2.01 | 147.635 | 151.252 | 150.027 | 147.539 |  | 1302.787 | 1435.875 |  | 7.1191 | 7.1968 | 7.7095 | 7.7644 | 6.7605 | 6.9092 | 6.5972 | 6.7834 | 56.8401 | 0.051156 |  | 62.069 | 100
19980911200000 | 1998-09-11 20:00 | 615.485 |  | 0.083 | 148.243 | 151.525 | 150.525 | 147.07 |  | 1245.369 | 1360.872 |  | 6.7734 | 6.8689 | 7.3127 | 7.3335 | 6.4431 | 6.5789 | 6.2859 | 6.4478 | 54.0442 | 0.04864 |  | 62.069 | 100
19980911203000 | 1998-09-11 20:30 | 611.658 |  | 2.009 | 148.724 | 152.19 | 151.224 | 148.478 |  | 1251.536 | 1370.123 |  | 6.7803 | 6.8596 | 7.2976 | 7.3318 | 6.4346 | 6.5767 | 6.2866 | 6.4468 | 54.014 | 0.048613 |  | 62.069 | 100
19980911210000 | 1998-09-11 21:00 | 609.325 |  | 0 | 148.913 | 151.85 | 151.348 | 147.89 |  | 1253.869 | 1370.789 |  | 6.7871 | 6.8718 | 7.2969 | 7.3647 | 6.4492 | 6.5972 | 6.3049 | 6.4644 | 54.1362 | 0.048723 |  | 62.069 | 100
19980911213000 | 1998-09-11 21:30 | 608.774 |  | 2.009 | 148.749 | 150.757 | 151.084 | 147.292 |  | 1249.203 | 1369.623 |  | 6.7971 | 6.8811 | 7.3159 | 7.3623 | 6.4507 | 6.604 | 6.3118 | 6.4736 | 54.1965 | 0.048777 |  | 62.069 | 100
19980911220000 | 1998-09-11 22:00 | 611.527 |  | 0.083 | 148.329 | 151.2 | 150.733 | 147.983 |  | 1248.036 | 1367.956 |  | 6.7703 | 6.8643 | 7.2922 | 7.3411 | 6.4385 | 6.5925 | 6.2981 | 6.4568 | 54.0538 | 0.048648 |  | 62.069 | 100
19980911223000 | 1998-09-11 22:30 | 638.737 |  | 2.009 | 149.186 | 152.386 | 151.629 | 148.178 |  | 1319.538 | 1452.708 |  | 7.1375 | 7.1914 | 7.7371 | 7.7661 | 6.7681 | 6.8994 | 6.5933 | 6.7749 | 56.8678 | 0.051181 |  | 62.069 | 100
19980911230000 | 1998-09-11 23:00 | 637.82 |  | 0.084 | 148.82 | 150.783 | 151.338 | 146.575 |  | 1305.121 | 1432.374 |  | 7.093 | 7.1724 | 7.6875 | 7.7134 | 6.7407 | 6.8811 | 6.5713 | 6.7581 | 56.6175 | 0.050956 |  | 62.069 | 100
19980911233000 | 1998-09-11 23:30 | 643.377 |  | 2.132 | 148.432 | 151.474 | 150.682 | 148.008 |  | 1299.954 | 1431.874 |  | 7.0969 | 7.1479 | 7.6958 | 7.7241 | 6.7383 | 6.8618 | 6.5566 | 6.7444 | 56.5658 | 0.050909 |  | 62.069 | 100
19980912000000 | 1998-09-12 | 568.955 |  | 0 | 148.68 | 150.066 | 150.887 | 146.106 |  | 1151.866 | 1243.452 |  | 6.3979 | 6.4661 | 6.8711 | 6.8413 | 6.0723 | 6.1843 | 5.915 | 6.0708 | 50.8188 | 0.045737 |  | 62.069 | 100
19980912003000 | 1998-09-12 00:30 | 470.599 |  | 22.153 | 146.868 | 148.854 | 148.928 | 146.132 |  | 970.195 | 1038.78 |  | 5.3879 | 5.4146 | 5.6077 | 5.4834 | 5.156 | 5.2888 | 5.0637 | 5.0767 | 42.4788 | 0.038231 |  | 62.069 | 100
19980912010000 | 1998-09-12 01:00 | 468.03 |  | 0 | 147.148 | 149.571 | 149.247 | 148.581 |  | 964.111 | 1030.113 |  | 5.3665 | 5.4192 | 5.5764 | 5.4712 | 5.1162 | 5.2896 | 5.0562 | 5.0752 | 42.3705 | 0.038133 |  | 62.069 | 100
19980912013000 | 1998-09-12 01:30 | 371.928 |  | 2.008 | 147.92 | 148.441 | 150.392 | 147.203 |  | 789.773 | 834.441 |  | 4.4495 | 4.4814 | 4.4792 | 4.2175 | 4.2588 | 4.4868 | 4.2976 | 4.1841 | 34.8549 | 0.031369 |  | 62.069 | 100
19980912020000 | 1998-09-12 02:00 | 372.243 |  | 0 | 148.002 | 152.675 | 150.19 | 150.942 |  | 806.94 | 848.691 |  | 4.4351 | 4.4426 | 4.4465 | 4.1604 | 4.2505 | 4.4519 | 4.2512 | 4.1238 | 34.562 | 0.031106 |  | 62.069 | 100
19980912023000 | 1998-09-12 02:30 | 374.812 |  | 2.252 | 149.562 | 150.318 | 151.891 | 148.585 |  | 810.273 | 857.108 |  | 4.4785 | 4.4832 | 4.5327 | 4.2261 | 4.303 | 4.4846 | 4.29 | 4.168 | 34.9661 | 0.031469 |  | 62.069 | 100
19980912030000 | 1998-09-12 03:00 | 369.674 |  | 0 | 148.425 | 150.122 | 151.143 | 148.884 |  | 814.273 | 862.108 |  | 4.4648 | 4.5259 | 4.5313 | 4.2922 | 4.303 | 4.5266 | 4.3313 | 4.2068 | 35.1819 | 0.031664 |  | 62.069 | 100
19980912033000 | 1998-09-12 03:30 | 367.708 |  | 2.377 | 148.455 | 152.154 | 150.768 | 150.174 |  | 803.523 | 855.941 |  | 4.4236 | 4.4807 | 4.4526 | 4.2122 | 4.2444 | 4.4792 | 4.2893 | 4.1604 | 34.7424 | 0.031268 |  | 62.069 | 100
19980912040000 | 1998-09-12 04:00 | 370.591 |  | 0 | 149.162 | 150.004 | 151.522 | 149.013 |  | 814.523 | 863.608 |  | 4.4319 | 4.4937 | 4.4839 | 4.2512 | 4.2505 | 4.4763 | 4.2976 | 4.1841 | 34.8692 | 0.031382 |  | 62.069 | 100
19980912043000 | 1998-09-12 04:30 | 371.587 |  | 2.376 | 147.72 | 149.457 | 150.139 | 148.219 |  | 792.273 | 836.357 |  | 4.4426 | 4.4731 | 4.4824 | 4.21 | 4.2466 | 4.4656 | 4.2771 | 4.1543 | 34.7517 | 0.031277 |  | 62.069 | 100
19980912050000 | 1998-09-12 05:00 | 372.977 |  | 20.54 | 148.259 | 151.071 | 150.584 | 149.586 |  | 792.773 | 836.607 |  | 4.4397 | 4.4685 | 4.4839 | 4.2214 | 4.2588 | 4.457 | 4.2756 | 4.1489 | 34.7538 | 0.031278 |  | 62.069 | 100
19980912053000 | 1998-09-12 05:30 | 372.374 |  | 2.505 | 148.411 | 150.994 | 151.398 | 150.004 |  | 793.523 | 841.024 |  | 4.4868 | 3.2106 | 4.5159 | 4.3259 | 4.2915 | 4.5303 | 4.3572 | 4.2358 | 33.954 | 0.030559 |  | 62.069 | 100
19980912060000 | 1998-09-12 06:00 | 369.49 |  | 0 | 148.655 | 151.045 | 151.157 | 149.56 |  | 784.106 | 828.357 |  | 4.6006 | 3.1205 | 4.676 | 4.4792 | 4.4136 | 4.6379 | 4.4487 | 4.3481 | 34.7246 | 0.031252 |  | 62.069 | 100
19980912063000 | 1998-09-12 06:30 | 375.624 |  | 2.378 | 148.955 | 150.746 | 151.335 | 150.004 |  | 788.606 | 831.607 |  | 4.4807 | 4.3938 | 4.541 | 4.2527 | 4.2915 | 4.4685 | 4.2939 | 4.2039 | 34.926 | 0.031433 |  | 62.069 | 100
19980912070000 | 1998-09-12 07:00 | 374.55 |  | 0 | 148.859 | 151.489 | 151.235 | 148.518 |  | 792.439 | 835.024 |  | 4.406 | 4.4326 | 4.4343 | 4.2261 | 4.2222 | 4.4473 | 4.281 | 4.1597 | 34.6092 | 0.031148 |  | 62.069 | 100
19980912073000 | 1998-09-12 07:30 | 409.31 |  | 2.624 | 148.723 | 150.524 | 150.917 | 149.534 |  | 896.276 | 970.278 |  | 5.0347 | 5.0461 | 5.179 | 5.0637 | 4.7798 | 5.0034 | 4.8225 | 4.7607 | 39.6899 | 0.035721 |  | 62.069 | 100
19980912080000 | 1998-09-12 08:00 | 423.361 |  | 0 | 149.291 | 151.999 | 151.774 | 149.524 |  | 878.525 | 937.61 |  | 4.8774 | 4.9148 | 5.002 | 4.8523 | 4.6716 | 4.8547 | 4.6624 | 4.6228 | 38.458 | 0.034612 |  | 62.069 | 100
19980912083000 | 1998-09-12 08:30 | 429.705 |  | 2.254 | 148.702 | 150.473 | 151.246 | 148.245 |  | 938.777 | 1012.279 |  | 5.2271 | 5.2871 | 5.4482 | 5.3521 | 5.011 | 5.2285 | 5.0164 | 4.9783 | 41.5487 | 0.037394 |  | 62.069 | 100
19980912090000 | 1998-09-12 09:00 | 561.484 |  | 0.168 | 149.825 | 153.598 | 152.062 | 151.865 |  | 1152.783 | 1249.203 |  | 6.2942 | 6.3469 | 6.7285 | 6.717 | 5.9944 | 6.1394 | 5.8618 | 5.9854 | 50.0676 | 0.045061 |  | 62.069 | 100
19980912093000 | 1998-09-12 09:30 | 575.168 |  | 2.868 | 150.235 | 151.489 | 152.86 | 149.261 |  | 1185.201 | 1287.787 |  | 6.4392 | 6.4668 | 6.9116 | 6.9138 | 6.1121 | 6.2493 | 5.967 | 6.1165 | 51.1763 | 0.046059 |  | 62.069 | 100
19980912100000 | 1998-09-12 10:00 | 607.437 |  | 0.29 | 149.365 | 153.31 | 151.764 | 150.092 |  | 1263.453 | 1385.456 |  | 6.8496 | 6.8872 | 7.364 | 7.4294 | 6.488 | 6.6255 | 6.3318 | 6.5042 | 54.4797 | 0.049032 |  | 62.069 | 100
19980912103000 | 1998-09-12 10:30 | 627.806 |  | 2.866 | 149.792 | 152.423 | 152.313 | 148.958 |  | 1316.538 | 1452.375 |  | 7.0847 | 7.1084 | 7.6721 | 7.7112 | 6.7307 | 6.8528 | 6.5498 | 6.73 | 56.4397 | 0.050796 |  | 62.069 | 100
19980912110000 | 1998-09-12 11:00 | 640.546 |  | 0.168 | 149.385 | 151.592 | 151.837 | 147.384 |  | 1346.955 | 1480.959 |  | 7.1938 | 7.2244 | 7.801 | 7.8721 | 6.8391 | 6.968 | 6.6536 | 6.8596 | 57.4116 | 0.05167 |  | 62.069 | 100
19980912113000 | 1998-09-12 11:30 | 639.996 |  | 2.502 | 148.743 | 150.432 | 151.285 | 147.462 |  | 1329.371 | 1466.542 |  | 7.1816 | 7.2136 | 7.7859 | 7.8394 | 6.8162 | 6.9573 | 6.6399 | 6.8467 | 57.2806 | 0.051553 |  | 62.069 | 100
19980912120000 | 1998-09-12 12:00 | 643.666 |  | 0.082 | 148.439 | 150.994 | 151.113 | 147.528 |  | 1333.705 | 1466.625 |  | 7.2305 | 7.2571 | 7.8271 | 7.8933 | 6.8628 | 6.9932 | 6.6736 | 6.8726 | 57.6102 | 0.051849 |  | 62.069 | 100
19980912123000 | 1998-09-12 12:30 | 644.924 |  | 2.129 | 148.746 | 151.175 | 151.037 | 147.462 |  | 1326.871 | 1460.209 |  | 7.1985 | 7.2068 | 7.7981 | 7.8293 | 6.833 | 6.949 | 6.6406 | 6.8313 | 57.2866 | 0.051558 |  | 62.069 | 100
19980912130000 | 1998-09-12 13:00 | 648.017 |  | 0.165 | 148.375 | 151.865 | 150.52 | 147.905 |  | 1326.871 | 1461.209 |  | 7.2129 | 7.2129 | 7.8118 | 7.8584 | 6.842 | 6.949 | 6.6399 | 6.8428 | 57.3697 | 0.051633 |  | 62.069 | 100
19980912133000 | 1998-09-12 13:30 | 650.245 |  | 2.372 | 148.607 | 151.799 | 151.093 | 147.096 |  | 1324.288 | 1460.125 |  | 7.168 | 7.1853 | 7.76 | 7.8049 | 6.8093 | 6.9253 | 6.6155 | 6.814 | 57.0823 | 0.051374 |  | 62.069 | 100
19980912140000 | 1998-09-12 14:00 | 648.699 |  | 0.204 | 148.443 | 151.865 | 151.321 | 147.163 |  | 1325.705 | 1461.042 |  | 7.1633 | 7.2 | 7.7637 | 7.8301 | 6.8101 | 6.9382 | 6.6238 | 6.8191 | 57.1483 | 0.051433 |  | 62.069 | 100
19980912143000 | 1998-09-12 14:30 | 646.025 |  | 2.005 | 148.767 | 152.087 | 151.245 | 148.127 |  | 1326.121 | 1458.292 |  | 7.168 | 7.1975 | 7.7637 | 7.8362 | 6.7971 | 6.9443 | 6.6323 | 6.833 | 57.1721 | 0.051455 |  | 62.069 | 100
19980912150000 | 1998-09-12 15:00 | 644.557 |  | 0.082 | 148.857 | 151.747 | 151.241 | 148.282 |  | 1332.122 | 1460.292 |  | 7.1724 | 7.2083 | 7.7759 | 7.8584 | 6.8093 | 6.9595 | 6.6492 | 6.8452 | 57.2782 | 0.05155 |  | 62.069 | 100
19980912153000 | 1998-09-12 15:30 | 645.632 |  | 2.008 | 148.966 | 151.345 | 151.311 | 148.127 |  | 1324.205 | 1458.458 |  | 7.1641 | 7.2053 | 7.7615 | 7.8477 | 6.7979 | 6.9595 | 6.6392 | 6.8452 | 57.2204 | 0.051498 |  | 62.069 | 100
19980912160000 | 1998-09-12 16:00 | 645.317 |  | 0.082 | 148.477 | 152.165 | 151.11 | 147.957 |  | 1329.205 | 1458.125 |  | 7.1785 | 7.2068 | 7.7866 | 7.8577 | 6.813 | 6.9573 | 6.6377 | 6.8428 | 57.2804 | 0.051552 |  | 62.069 | 100
19980912163000 | 1998-09-12 16:30 | 647.519 |  | 1.882 | 148.644 | 151.84 | 151.111 | 147.879 |  | 1330.205 | 1458.625 |  | 7.1724 | 7.2144 | 7.7712 | 7.8376 | 6.8162 | 6.9512 | 6.6377 | 6.842 | 57.2427 | 0.051518 |  | 62.069 | 100
19980912170000 | 1998-09-12 17:00 | 647.991 |  | 0.082 | 148.529 | 151.644 | 150.67 | 147.188 |  | 1324.205 | 1456.542 |  | 7.1831 | 7.2053 | 7.7905 | 7.8262 | 6.8201 | 6.9429 | 6.6323 | 6.8352 | 57.2356 | 0.051512 |  | 62.069 | 100
19980912173000 | 1998-09-12 17:30 | 651.268 |  | 2.248 | 149.271 | 151.566 | 151.187 | 148.596 |  | 1328.621 | 1462.292 |  | 7.1809 | 7.2197 | 7.7798 | 7.8369 | 6.8123 | 6.9465 | 6.6345 | 6.8313 | 57.2419 | 0.051518 |  | 62.069 | 100
19980912180000 | 1998-09-12 18:00 | 646.051 |  | 0.41 | 149.123 | 150.979 | 151.799 | 148.503 |  | 1353.539 | 1486.459 |  | 7.1899 | 7.2305 | 7.7896 | 7.8469 | 6.8269 | 6.9587 | 6.6506 | 6.8542 | 57.3473 | 0.051613 |  | 62.069 | 100
19980912183000 | 1998-09-12 18:30 | 644.033 |  | 2.129 | 148.783 | 150.55 | 151.172 | 147.333 |  | 1350.789 | 1488.293 |  | 7.1809 | 7.2021 | 7.7813 | 7.8416 | 6.8169 | 6.9534 | 6.6445 | 6.8352 | 57.2559 | 0.05153 |  | 62.069 | 100
19980912190000 | 1998-09-12 19:00 | 645.736 |  | 0.164 | 148.625 | 149.338 | 151.044 | 147.606 |  | 1350.372 | 1485.543 |  | 7.1809 | 7.209 | 7.7896 | 7.8347 | 6.8237 | 6.9634 | 6.6514 | 6.8398 | 57.2925 | 0.051563 |  | 62.069 | 100
19980912193000 | 1998-09-12 19:30 | 646.497 |  | 20.977 | 148.781 | 150.014 | 151.076 | 147.787 |  | 1346.039 | 1484.709 |  | 7.1899 | 7.2251 | 7.8027 | 7.8477 | 6.8276 | 6.9634 | 6.6528 | 6.8413 | 57.3505 | 0.051615 |  | 62.069 | 100
19980912200000 | 1998-09-12 20:00 | 647.965 |  | 0.164 | 148.204 | 149.989 | 150.455 | 146.523 |  | 1327.371 | 1458.875 |  | 7.1831 | 7.2029 | 7.7859 | 7.8408 | 6.8101 | 6.9587 | 6.6421 | 6.8337 | 57.2573 | 0.051532 |  | 62.069 | 100
19980912203000 | 1998-09-12 20:30 | 648.541 |  | 2.374 | 147.975 | 151.67 | 150.418 | 147.709 |  | 1328.038 | 1459.875 |  | 7.1748 | 7.1885 | 7.7668 | 7.8096 | 6.8054 | 6.926 | 6.6177 | 6.8201 | 57.1089 | 0.051398 |  | 62.069 | 100
19980912210000 | 1998-09-12 21:00 | 607.831 |  | 0.167 | 148.145 | 150.613 | 150.701 | 146.157 |  | 1253.286 | 1371.539 |  | 6.7734 | 6.823 | 7.3005 | 7.3281 | 6.4424 | 6.5759 | 6.2881 | 6.4751 | 54.0065 | 0.048606 |  | 62.069 | 100
19980912213000 | 1998-09-12 21:30 | 605.891 |  | 2.124 | 148.131 | 151.566 | 150.446 | 147.606 |  | 1255.786 | 1378.79 |  | 6.7483 | 6.7856 | 7.2639 | 7.2815 | 6.4202 | 6.5483 | 6.2622 | 6.4294 | 53.7394 | 0.048365 |  | 62.069 | 100
19980912220000 | 1998-09-12 22:00 | 580.489 |  | 0.082 | 148.312 | 151.16 | 150.746 | 147.447 |  | 1190.951 | 1291.287 |  | 6.4636 | 6.4973 | 6.9275 | 6.9084 | 6.1631 | 6.2744 | 6.0022 | 6.1372 | 51.3737 | 0.046236 |  | 62.069 | 100
19980912223000 | 1998-09-12 22:30 | 575.272 |  | 2.492 | 148.483 | 150.875 | 150.736 | 148.153 |  | 1186.617 | 1298.537 |  | 6.4355 | 6.4819 | 6.8955 | 6.8772 | 6.1333 | 6.2668 | 5.9968 | 6.125 | 51.212 | 0.046091 |  | 62.069 | 100
19980912230000 | 1998-09-12 23:00 | 524.469 |  | 0 | 148.359 | 149.87 | 150.888 | 146.9 |  | 1099.615 | 1183.367 |  | 5.9585 | 6.0105 | 6.3064 | 6.2493 | 5.7083 | 5.8472 | 5.5908 | 5.6909 | 47.3619 | 0.042626 |  | 62.069 | 100
19980912233000 | 1998-09-12 23:30 | 530.997 |  | 2.251 | 148.065 | 150.979 | 150.192 | 148.256 |  | 1083.364 | 1174.7 |  | 5.9297 | 5.9487 | 6.2837 | 6.2302 | 5.6587 | 5.803 | 5.5581 | 5.6313 | 47.0434 | 0.042339 |  | 62.069 | 100
19980913000000 | 1998-09-13 | 525.596 |  | 0.164 | 148.396 | 152.15 | 150.766 | 149.179 |  | 1081.114 | 1164.283 |  | 5.8547 | 5.8755 | 6.1768 | 6.1111 | 5.5811 | 5.7114 | 5.458 | 5.5344 | 46.303 | 0.041673 |  | 62.069 | 100
19980913003000 | 1998-09-13 00:30 | 376.07 |  | 2.126 | 148.472 | 148.23 | 150.524 | 146.002 |  | 780.189 | 823.107 |  | 4.3755 | 4.3228 | 4.3633 | 4.0283 | 4.1848 | 4.3435 | 4.1641 | 4.0498 | 33.8321 | 0.030449 |  | 62.069 | 100
19980913010000 | 1998-09-13 01:00 | 356.96 |  | 0 | 146.993 | 149.612 | 149.263 | 147.879 |  | 730.604 | 761.272 |  | 4.0786 | 4.0383 | 4.0093 | 3.6667 | 3.8949 | 4.1116 | 3.9216 | 3.8003 | 31.5213 | 0.028369 |  | 62.069 | 100
19980913013000 | 1998-09-13 01:30 | 339.737 |  | 2.129 | 148.037 | 149.767 | 150.418 | 148.777 |  | 731.188 | 762.855 |  | 4.0063 | 4.0139 | 3.9209 | 3.6249 | 3.8416 | 4.1284 | 3.9468 | 3.7698 | 31.2526 | 0.028127 |  | 62.069 | 100
19980913020000 | 1998-09-13 02:00 | 336.487 |  | 0 | 148.359 | 150.927 | 150.772 | 149.442 |  | 739.855 | 771.939 |  | 4.104 | 4.0803 | 4.0369 | 3.7531 | 3.9407 | 4.1833 | 4.0071 | 3.8247 | 31.9301 | 0.028737 |  | 62.069 | 100
19980913023000 | 1998-09-13 02:30 | 328.046 |  | 2.618 | 148.799 | 150.746 | 151 | 149.756 |  | 742.188 | 782.022 |  | 4.1062 | 4.0757 | 4.0337 | 3.7637 | 3.9376 | 4.1726 | 4.0161 | 3.8331 | 31.9387 | 0.028745 |  | 62.069 | 100
19980913030000 | 1998-09-13 03:00 | 327.259 |  | 0 | 148.478 | 150.447 | 151.064 | 149.704 |  | 728.688 | 759.938 |  | 4.0718 | 4.0466 | 3.988 | 3.7118 | 3.9003 | 4.1047 | 3.9819 | 3.7996 | 31.6047 | 0.028444 |  | 62.069 | 100
19980913033000 | 1998-09-13 03:30 | 333.813 |  | 2.376 | 148.369 | 152.231 | 151.02 | 150.746 |  | 731.688 | 769.105 |  | 4.0491 | 4.0085 | 3.9758 | 3.6531 | 3.882 | 4.0376 | 3.9301 | 3.7698 | 31.306 | 0.028175 |  | 62.069 | 100
19980913040000 | 1998-09-13 04:00 | 339.475 |  | 0 | 149.207 | 150.447 | 151.838 | 149.209 |  | 731.604 | 764.272 |  | 4.0337 | 4.0107 | 3.9545 | 3.6423 | 3.8606 | 4.0107 | 3.9216 | 3.7583 | 31.1924 | 0.028073 |  | 62.069 | 100
19980913043000 | 1998-09-13 04:30 | 337.247 |  | 2.129 | 148.535 | 150.029 | 151.092 | 148.049 |  | 736.271 | 776.189 |  | 4.0796 | 4.0574 | 3.9994 | 3.6615 | 3.9094 | 4.0269 | 3.9445 | 3.7935 | 31.4722 | 0.028325 |  | 62.069 | 100
19980913050000 | 1998-09-13 05:00 | 329.487 |  | 0 | 148.786 | 150.746 | 150.94 | 149.756 |  | 755.188 | 792.773 |  | 4.1184 | 4.0901 | 4.0664 | 3.7561 | 3.9484 | 4.0703 | 3.9956 | 3.8362 | 31.8815 | 0.028693 |  | 62.069 | 100
19980913053000 | 1998-09-13 05:30 | 327.862 |  | 2.539 | 148.755 | 151.241 | 151.425 | 149.013 |  | 742.021 | 780.772 |  | 4.0603 | 4.0481 | 3.9918 | 3.6851 | 3.8956 | 4.0269 | 3.9536 | 3.7935 | 31.4549 | 0.028309 |  | 62.069 | 100
19980913060000 | 1998-09-13 06:00 | 338.112 |  | 0 | 148.477 | 149.782 | 150.737 | 149.039 |  | 728.354 | 758.772 |  | 4.0337 | 3.9949 | 3.943 | 3.631 | 3.8651 | 3.9841 | 3.9139 | 3.7599 | 31.1256 | 0.028013 |  | 62.069 | 100
19980913063000 | 1998-09-13 06:30 | 340.733 |  | 2.374 | 148.573 | 150.617 | 150.8 | 149.132 |  | 732.188 | 765.772 |  | 4.0344 | 4.0125 | 3.9423 | 3.6301 | 3.8575 | 3.9803 | 3.9178 | 3.7629 | 31.1378 | 0.028024 |  | 62.069 | 100
19980913070000 | 1998-09-13 07:00 | 335.097 |  | 0 | 148.588 | 150.643 | 150.995 | 149.158 |  | 750.438 | 788.273 |  | 4.104 | 4.0742 | 4.0369 | 3.7347 | 3.9155 | 4.0481 | 3.978 | 3.8186 | 31.71 | 0.028539 |  | 62.069 | 100
19980913073000 | 1998-09-13 07:30 | 328.675 |  | 1.393 | 149.276 | 150.24 | 151.437 | 148.755 |  | 753.605 | 800.023 |  | 4.1238 | 4.1199 | 4.0688 | 3.8125 | 3.9552 | 4.0901 | 4.0254 | 3.8599 | 32.0556 | 0.02885 |  | 62.069 | 100
19980913080000 | 1998-09-13 08:00 | 329.671 |  | 0 | 148.475 | 148.038 | 150.681 | 147.791 |  | 737.354 | 770.272 |  | 4.1345 | 4.103 | 4.0505 | 3.8003 | 3.9667 | 4.0962 | 4.0344 | 3.8599 | 32.0455 | 0.028841 |  | 62.069 | 100
19980913083000 | 1998-09-13 08:30 | 331.637 |  | 2.38 | 147.842 | 150.953 | 150.149 | 149.963 |  | 720.271 | 754.272 |  | 4.0466 | 4.0269 | 3.9552 | 3.6606 | 3.8667 | 3.9949 | 3.9407 | 3.7736 | 31.2652 | 0.028139 |  | 62.069 | 100
19980913090000 | 1998-09-13 09:00 | 342.49 |  | 0 | 148.819 | 150.798 | 151.228 | 150.55 |  | 767.272 | 807.273 |  | 4.2786 | 4.2534 | 4.2534 | 3.962 | 4.1101 | 4.2405 | 4.1816 | 4.0032 | 33.2828 | 0.029955 |  | 62.069 | 100
19980913093000 | 1998-09-13 09:30 | 413.111 |  | 2.373 | 149.383 | 150.89 | 151.899 | 150.395 |  | 876.192 | 944.527 |  | 4.8547 | 4.8569 | 4.9568 | 4.7866 | 4.657 | 4.7722 | 4.6372 | 4.5679 | 38.0893 | 0.03428 |  | 62.069 | 100
19980913100000 | 1998-09-13 10:00 | 522.241 |  | 20.618 | 149.843 | 153.624 | 152.386 | 151.891 |  | 1080.698 | 1169.034 |  | 5.9167 | 5.9456 | 6.2646 | 6.1965 | 5.6343 | 5.7458 | 5.5054 | 5.5947 | 46.8036 | 0.042123 |  | 62.069 | 100
19980913103000 | 1998-09-13 10:30 | 527.746 |  | 1.883 | 149.902 | 151.278 | 152.631 | 149.545 |  | 1081.781 | 1174.617 |  | 5.9265 | 5.9517 | 6.2769 | 6.2209 | 5.6565 | 5.7786 | 5.5337 | 5.6228 | 46.9676 | 0.042271 |  | 62.069 | 100
19980913110000 | 1998-09-13 11:00 | 527.222 |  | 0 | 148.792 | 150.849 | 151.327 | 147.879 |  | 1096.281 | 1183.201 |  | 5.9395 | 5.9678 | 6.3042 | 6.2295 | 5.6702 | 5.7922 | 5.5466 | 5.6282 | 47.0782 | 0.04237 |  | 62.069 | 100
19980913113000 | 1998-09-13 11:30 | 527.562 |  | 2.129 | 148.549 | 151.37 | 151.169 | 148.4 |  | 1077.781 | 1169.117 |  | 5.9021 | 5.9517 | 6.2485 | 6.2188 | 5.6343 | 5.7725 | 5.5237 | 5.6152 | 46.8668 | 0.04218 |  | 62.069 | 100
19980913120000 | 1998-09-13 12:00 | 526.828 |  | 0 | 148.666 | 151.226 | 151.028 | 148.008 |  | 1088.531 | 1173.617 |  | 5.9509 | 5.9685 | 6.2927 | 6.2349 | 5.6619 | 5.8008 | 5.5488 | 5.636 | 47.0945 | 0.042385 |  | 62.069 | 100
19980913123000 | 1998-09-13 12:30 | 526.986 |  | 2.128 | 148.87 | 151.304 | 151.082 | 149.076 |  | 1076.614 | 1167.45 |  | 5.9243 | 5.9434 | 6.2554 | 6.1775 | 5.6343 | 5.7725 | 5.5176 | 5.6016 | 46.8266 | 0.042144 |  | 62.069 | 100
19980913130000 | 1998-09-13 13:00 | 517.182 |  | 0 | 148.713 | 151.448 | 151.111 | 148.725 |  | 1037.613 | 1119.449 |  | 5.729 | 5.71 | 6.0083 | 5.9319 | 5.4436 | 5.5581 | 5.3186 | 5.3955 | 45.095 | 0.040585 |  | 62.069 | 100
19980913133000 | 1998-09-13 13:30 | 472.486 |  | 1.27 | 148.022 | 149.261 | 150.205 | 147.281 |  | 983.862 | 1059.78 |  | 5.458 | 5.4512 | 5.6938 | 5.5481 | 5.22 | 5.3467 | 5.1201 | 5.1423 | 42.9802 | 0.038682 |  | 62.069 | 100
19980913140000 | 1998-09-13 14:00 | 474.164 |  | 0 | 147.995 | 151.37 | 150.357 | 149.143 |  | 984.528 | 1061.447 |  | 5.4055 | 5.4016 | 5.6321 | 5.4978 | 5.1797 | 5.304 | 5.0842 | 5.1033 | 42.6082 | 0.038347 |  | 62.069 | 100
19980913143000 | 1998-09-13 14:30 | 472.591 |  | 2.253 | 149.371 | 151.215 | 151.609 | 148.988 |  | 984.862 | 1064.697 |  | 5.3979 | 5.3979 | 5.6252 | 5.4749 | 5.1599 | 5.301 | 5.0735 | 5.0896 | 42.5199 | 0.038268 |  | 62.069 | 100
19980913150000 | 1998-09-13 15:00 | 470.809 |  | 0 | 148.829 | 150.081 | 151.194 | 148.101 |  | 981.528 | 1057.864 |  | 5.4055 | 5.4077 | 5.6252 | 5.4946 | 5.1711 | 5.3079 | 5.0881 | 5.1003 | 42.6004 | 0.03834 |  | 62.069 | 100
19980913153000 | 1998-09-13 15:30 | 471.044 |  | 1.886 | 148.333 | 151.282 | 150.872 | 148.312 |  | 981.362 | 1064.197 |  | 5.3987 | 5.4214 | 5.6382 | 5.5154 | 5.1636 | 5.3186 | 5.0964 | 5.1101 | 42.6624 | 0.038396 |  | 62.069 | 100
19980913160000 | 1998-09-13 16:00 | 475.134 |  | 0 | 148.788 | 150.576 | 150.867 | 148.101 |  | 971.861 | 1047.363 |  | 5.4023 | 5.4109 | 5.6213 | 5.5093 | 5.1628 | 5.3186 | 5.0964 | 5.1072 | 42.6288 | 0.038366 |  | 62.069 | 100
19980913163000 | 1998-09-13 16:30 | 525.308 |  | 2.374 | 148.483 | 151.36 | 150.757 | 149.379 |  | 1118.782 | 1218.368 |  | 6.0593 | 6.0823 | 6.4294 | 6.4133 | 5.7725 | 5.9495 | 5.6899 | 5.7549 | 48.1511 | 0.043336 |  | 62.069 | 100
19980913170000 | 1998-09-13 17:00 | 530.761 |  | 0.081 | 149.749 | 151.618 | 152.262 | 149.143 |  | 1085.281 | 1175.284 |  | 5.9158 | 5.8931 | 6.2454 | 6.1523 | 5.6167 | 5.7458 | 5.4978 | 5.5811 | 46.648 | 0.041983 |  | 62.069 | 100
19980913173000 | 1998-09-13 17:30 | 577.317 |  | 2.372 | 148.847 | 152.933 | 151.417 | 149.468 |  | 1190.117 | 1300.371 |  | 6.5408 | 6.5552 | 7.0215 | 7.0007 | 6.2012 | 6.3333 | 6.0493 | 6.1904 | 51.8924 | 0.046703 |  | 62.069 | 100
19980913180000 | 1998-09-13 18:00 | 629.693 |  | 0.529 | 150.251 | 152.139 | 153.021 | 148.921 |  | 1313.288 | 1445.208 |  | 7.0266 | 7.0381 | 7.5845 | 7.6074 | 6.6597 | 6.7842 | 6.4766 | 6.6704 | 55.8475 | 0.050263 |  | 62.069 | 100
19980913183000 | 1998-09-13 18:30 | 629.615 |  | 2.126 | 149.396 | 151.164 | 151.978 | 147.203 |  | 1321.871 | 1451.875 |  | 7.0503 | 7.0808 | 7.637 | 7.666 | 6.6963 | 6.8215 | 6.5171 | 6.7092 | 56.1782 | 0.05056 |  | 62.069 | 100
19980913190000 | 1998-09-13 19:00 | 627.229 |  | 0.161 | 148.376 | 151.525 | 150.959 | 148.308 |  | 1312.871 | 1439.791 |  | 7.0305 | 7.0649 | 7.6074 | 7.6638 | 6.6812 | 6.8147 | 6.5117 | 6.707 | 56.0812 | 0.050473 |  | 62.069 | 100
19980913193000 | 1998-09-13 19:30 | 630.165 |  | 2.125 | 148.791 | 151.995 | 151.007 | 148.282 |  | 1325.038 | 1460.542 |  | 7.042 | 7.0747 | 7.6333 | 7.6753 | 6.6858 | 6.8245 | 6.5225 | 6.7192 | 56.1773 | 0.05056 |  | 62.069 | 100
19980913200000 | 1998-09-13 20:00 | 630.27 |  | 0.16 | 148.259 | 149.793 | 150.698 | 147.07 |  | 1298.037 | 1428.041 |  | 7.0374 | 7.0649 | 7.6265 | 7.6707 | 6.6926 | 6.814 | 6.5027 | 6.7041 | 56.1129 | 0.050502 |  | 62.069 | 100
19980913203000 | 1998-09-13 20:30 | 630.375 |  | 2.003 | 148.012 | 151.355 | 150.453 | 148.88 |  | 1292.12 | 1420.457 |  | 6.9924 | 7.042 | 7.5593 | 7.6135 | 6.6506 | 6.7925 | 6.4805 | 6.6704 | 55.8012 | 0.050221 |  | 62.069 | 100
19980913210000 | 1998-09-13 21:00 | 631.817 |  | 0.081 | 148.623 | 152.66 | 150.9 | 149.194 |  | 1297.621 | 1426.541 |  | 7.0015 | 7.0527 | 7.5708 | 7.6309 | 6.6467 | 6.7993 | 6.4956 | 6.6848 | 55.8823 | 0.050294 |  | 62.069 | 100
19980913213000 | 1998-09-13 21:30 | 632.131 |  | 2.006 | 149.263 | 151.134 | 151.65 | 148.411 |  | 1296.871 | 1424.458 |  | 7.0205 | 7.0474 | 7.5798 | 7.6118 | 6.6682 | 6.7932 | 6.4866 | 6.6765 | 55.884 | 0.050296 |  | 62.069 | 100
19980913220000 | 1998-09-13 22:00 | 627.046 |  | 20.788 | 148.459 | 151.289 | 151.164 | 147.823 |  | 1299.871 | 1428.458 |  | 7.0474 | 7.0618 | 7.637 | 7.647 | 6.6926 | 6.8123 | 6.5034 | 6.6948 | 56.0963 | 0.050487 |  | 62.069 | 100
19980913223000 | 1998-09-13 22:30 | 632.865 |  | 2.126 | 148.648 | 152.227 | 151.109 | 147.772 |  | 1293.787 | 1425.124 |  | 7.0459 | 7.0474 | 7.6157 | 7.6265 | 6.6858 | 6.7986 | 6.4956 | 6.6772 | 55.9927 | 0.050393 |  | 62.069 | 100
19980913230000 | 1998-09-13 23:00 | 519.331 |  | 0 | 148.302 | 148.308 | 150.345 | 145.337 |  | 1072.364 | 1157.783 |  | 5.9502 | 5.9434 | 6.302 | 6.2065 | 5.6816 | 5.7778 | 5.5383 | 5.6282 | 47.028 | 0.042325 |  | 62.069 | 100
19980913233000 | 1998-09-13 23:30 | 478.909 |  | 1.518 | 147.198 | 149.597 | 149.124 | 147.122 |  | 976.861 | 1057.364 |  | 5.4092 | 5.4146 | 5.6191 | 5.4939 | 5.1926 | 5.3186 | 5.0972 | 5.1125 | 42.6577 | 0.038392 |  | 62.069 | 100
19980914000000 | 1998-09-14 | 425.196 |  | 0 | 147.415 | 150.731 | 149.791 | 148.751 |  | 890.026 | 950.527 |  | 5.0103 | 4.9873 | 5.114 | 4.5396 | 4.7876 | 4.9553 | 4.7463 | 4.7097 | 38.8501 | 0.034965 |  | 62.069 | 100
19980914003000 | 1998-09-14 00:30 | 351.35 |  | 0.084 | 147.391 | 149.39 | 150.187 | 148.648 |  | 716.521 | 751.938 |  | 4.1016 | 4.0857 | 4.0322 | 3.3014 | 3.9552 | 4.1924 | 4.0017 | 3.8552 | 31.5254 | 0.028373 |  | 62.069 | 100
19980914010000 | 1998-09-14 01:00 | 343.46 |  | 0 | 147.347 | 150.783 | 149.885 | 148.803 |  | 739.521 | 777.689 |  | 4.1321 | 4.1008 | 4.0681 | 3.7545 | 3.9636 | 4.2053 | 4.0161 | 3.8438 | 32.0843 | 0.028876 |  | 62.069 | 100
19980914013000 | 1998-09-14 01:30 | 337.902 |  | 1.641 | 148.421 | 151.267 | 150.835 | 149.534 |  | 744.271 | 789.356 |  | 4.364 | 4.3237 | 4.3464 | 4.0542 | 2.7345 | 4.3862 | 4.1938 | 4.0376 | 32.4404 | 0.029196 |  | 62.069 | 100
19980914020000 | 1998-09-14 02:00 | 330.85 |  | 0 | 148.663 | 150.72 | 150.977 | 149.235 |  | 740.355 | 774.106 |  | 4.2078 | 4.1702 | 4.1794 | 3.8621 | 2.7375 | 4.2488 | 4.0825 | 3.9155 | 31.4038 | 0.028263 |  | 62.069 | 100
19980914023000 | 1998-09-14 02:30 | 338.557 |  | 1.759 | 148.544 | 151.36 | 150.956 | 149.627 |  | 740.771 | 782.439 |  | 4.2764 | 4.2634 | 4.2444 | 3.9735 | 2.7817 | 4.322 | 4.1572 | 3.985 | 32.0036 | 0.028803 |  | 62.069 | 100
19980914030000 | 1998-09-14 03:00 | 341.389 |  | 0 | 148.707 | 150.72 | 151.062 | 149.483 |  | 733.604 | 770.355 |  | 4.0764 | 4.0872 | 4.0032 | 3.7491 | 4.0002 | 4.155 | 4.0085 | 3.8315 | 31.9111 | 0.02872 |  | 62.069 | 100
19980914033000 | 1998-09-14 03:30 | 337.85 |  | 1.762 | 148.502 | 150.591 | 151.007 | 148.611 |  | 737.854 | 783.356 |  | 4.1389 | 4.1694 | 4.0908 | 3.8514 | 4.0664 | 4.187 | 4.0596 | 3.8995 | 32.463 | 0.029217 |  | 62.069 | 100
19980914040000 | 1998-09-14 04:00 | 339.816 |  | 0.084 | 148.279 | 150.931 | 150.599 | 149.446 |  | 725.187 | 759.105 |  | 4.0962 | 4.0908 | 4.0222 | 3.7491 | 4.0176 | 4.0886 | 3.9963 | 3.8339 | 31.8947 | 0.028705 |  | 62.069 | 100
19980914043000 | 1998-09-14 04:30 | 342.227 |  | 1.393 | 148.724 | 150.658 | 151.331 | 149.42 |  | 723.937 | 761.522 |  | 4.0979 | 4.0955 | 4.0322 | 3.7683 | 4.0161 | 4.0818 | 3.9956 | 3.8477 | 31.9351 | 0.028742 |  | 62.069 | 100
19980914050000 | 1998-09-14 05:00 | 340.943 |  | 0 | 148.519 | 151.241 | 151.015 | 149.756 |  | 735.438 | 771.439 |  | 4.1292 | 4.1252 | 4.0718 | 3.808 | 4.0574 | 4.0894 | 4.0085 | 3.8599 | 32.1494 | 0.028934 |  | 62.069 | 100
19980914053000 | 1998-09-14 05:30 | 334.232 |  | 1.884 | 149.018 | 151.448 | 151.268 | 150.458 |  | 730.271 | 769.189 |  | 4.1313 | 4.1213 | 4.0642 | 3.8224 | 4.0405 | 4.0933 | 4.0154 | 3.8674 | 32.1558 | 0.02894 |  | 62.069 | 100
19980914060000 | 1998-09-14 06:00 | 335.779 |  | 0 | 148.587 | 151.086 | 151.042 | 149.106 |  | 725.021 | 759.105 |  | 4.1016 | 4.1016 | 4.0176 | 3.7782 | 4.0298 | 4.0786 | 3.9911 | 3.8522 | 31.9507 | 0.028756 |  | 62.069 | 100
19980914063000 | 1998-09-14 06:30 | 346.133 |  | 2.008 | 148.79 | 150.55 | 150.944 | 149.313 |  | 726.021 | 764.605 |  | 4.0725 | 4.0559 | 3.9979 | 3.6958 | 3.9857 | 4.0413 | 3.9514 | 3.8118 | 31.6123 | 0.028451 |  | 62.069 | 100
19980914070000 | 1998-09-14 07:00 | 357.641 |  | 0 | 148.553 | 151.149 | 151.451 | 149.416 |  | 779.939 | 826.607 |  | 4.3945 | 4.3848 | 4.4189 | 4.187 | 4.3152 | 4.3572 | 4.2732 | 4.1353 | 34.4661 | 0.031019 |  | 62.069 | 100
19980914073000 | 1998-09-14 07:30 | 503.55 |  | 2.251 | 150.188 | 154.444 | 152.199 | 151.721 |  | 1089.531 | 1190.868 |  | 6.0601 | 6.1304 | 5.4023 | 6.4583 | 5.9128 | 5.9351 | 5.7021 | 5.7886 | 47.3897 | 0.042651 |  | 62.069 | 100
19980914080000 | 1998-09-14 08:00 | 578.392 |  | 0.286 | 151.492 | 152.881 | 154.143 | 149.911 |  | 1219.952 | 1338.872 |  | 6.6331 | 6.6499 | 5.957 | 7.1587 | 6.4485 | 6.427 | 6.147 | 6.3027 | 51.7239 | 0.046552 |  | 62.069 | 100
19980914083000 | 1998-09-14 08:30 | 637.977 |  | 2.739 | 150.24 | 152.438 | 152.83 | 148.973 |  | 1333.122 | 1465.792 |  | 7.2183 | 7.2578 | 6.5308 | 7.8943 | 7.0359 | 6.9856 | 6.6765 | 6.8909 | 56.4901 | 0.050841 |  | 62.069 | 100
19980914090000 | 1998-09-14 09:00 | 644.531 |  | 0.204 | 149.249 | 151.695 | 151.885 | 147.983 |  | 1313.621 | 1451.875 |  | 7.2351 | 7.2778 | 6.5505 | 7.9133 | 7.042 | 7.0007 | 6.6819 | 6.8984 | 56.5997 | 0.05094 |  | 62.069 | 100
19980914093000 | 1998-09-14 09:30 | 646.995 |  | 1.759 | 148.878 | 152.242 | 151.339 | 147.787 |  | 1332.372 | 1470.709 |  | 7.2969 | 7.3533 | 6.6094 | 7.9788 | 7.1084 | 7.0549 | 6.7383 | 6.9641 | 57.1041 | 0.051394 |  | 62.069 | 100
19980914100000 | 1998-09-14 10:00 | 651.058 |  | 0.081 | 148.748 | 151.876 | 151.177 | 147.668 |  | 1328.288 | 1464.459 |  | 7.2754 | 7.3257 | 6.5872 | 7.9751 | 7.093 | 7.0398 | 6.7246 | 6.9429 | 56.9637 | 0.051267 |  | 62.069 | 100
19980914103000 | 1998-09-14 10:30 | 640.939 |  | 1.761 | 148.235 | 151.304 | 150.774 | 146.848 |  | 1306.954 | 1438.958 |  | 7.4966 | 7.5601 | 6.8047 | 8.2349 | 7.303 | 7.2603 | 6.9238 | 4.8394 | 56.4228 | 0.050781 |  | 62.069 | 100
19980914110000 | 1998-09-14 11:00 | 647.309 |  | 0.163 | 148.408 | 152.501 | 150.992 | 148.045 |  | 1326.205 | 1461.959 |  | 7.2473 | 7.303 | 6.5637 | 7.9263 | 7.0664 | 7.0144 | 6.6934 | 6.8933 | 56.7078 | 0.051037 |  | 62.069 | 100
19980914113000 | 1998-09-14 11:30 | 646.706 |  | 2.128 | 148.854 | 152.175 | 151.3 | 148.463 |  | 1314.371 | 1449.375 |  | 7.2168 | 7.2646 | 6.5239 | 7.8918 | 7.0244 | 6.9856 | 6.6697 | 6.8704 | 56.4472 | 0.050802 |  | 62.069 | 100
19980914120000 | 1998-09-14 12:00 | 645.396 |  | 0.161 | 148.762 | 151.366 | 151.359 | 148.891 |  | 1311.204 | 1442.041 |  | 7.2388 | 7.2839 | 6.5376 | 7.9055 | 7.051 | 7.0107 | 6.6934 | 6.8977 | 56.6186 | 0.050957 |  | 62.069 | 100
19980914123000 | 1998-09-14 12:30 | 642.958 |  | 22.269 | 148.471 | 151.706 | 151.106 | 147.746 |  | 1312.288 | 1445.125 |  | 7.0413 | 7.0955 | 7.6394 | 7.666 | 6.8635 | 6.8237 | 6.5254 | 6.7131 | 56.3679 | 0.050731 |  | 62.069 | 100
19980914130000 | 1998-09-14 13:00 | 646.654 |  | 0.164 | 148.715 | 152.175 | 150.994 | 147.72 |  | 1309.038 | 1442.958 |  | 7.0474 | 7.0984 | 7.6699 | 7.6882 | 6.875 | 6.8435 | 6.5217 | 6.7231 | 56.4672 | 0.05082 |  | 62.069 | 100
19980914133000 | 1998-09-14 13:30 | 643.325 |  | 1.518 | 148.856 | 151.747 | 151.098 | 146.549 |  | 1310.454 | 1444.208 |  | 7.0747 | 7.0999 | 7.689 | 7.6631 | 6.8811 | 6.8359 | 6.5186 | 6.717 | 56.4793 | 0.050831 |  | 62.069 | 100
19980914140000 | 1998-09-14 14:00 | 645.474 |  | 0.288 | 148.73 | 152.057 | 150.751 | 147.354 |  | 1310.538 | 1443.875 |  | 7.0535 | 7.093 | 7.6614 | 7.6736 | 6.8711 | 6.8201 | 6.5071 | 6.7102 | 56.39 | 0.050751 |  | 62.069 | 100
19980914143000 | 1998-09-14 14:30 | 644.898 |  | 2.009 | 149.006 | 151.5 | 151.149 | 148.282 |  | 1310.121 | 1441.958 |  | 7.2388 | 7.2847 | 7.8882 | 6.5515 | 7.0542 | 7.0022 | 6.6726 | 6.8811 | 56.5733 | 0.050916 |  | 62.069 | 100
19980914150000 | 1998-09-14 15:00 | 644.819 |  | 0.082 | 148.658 | 152.124 | 151.305 | 147.173 |  | 1323.705 | 1457.542 |  | 7.103 | 7.1321 | 7.7356 | 7.7102 | 6.9238 | 6.8826 | 6.5645 | 6.7529 | 56.8047 | 0.051124 |  | 62.069 | 100
19980914153000 | 1998-09-14 15:30 | 646.235 |  | 2.007 | 148.857 | 152.046 | 151.137 | 148.333 |  | 1316.038 | 1451.292 |  | 7.0947 | 7.1191 | 7.7141 | 7.6943 | 6.9177 | 6.8618 | 6.5544 | 6.7368 | 56.6929 | 0.051024 |  | 62.069 | 100
19980914160000 | 1998-09-14 16:00 | 650.874 |  | 0.288 | 148.883 | 151.876 | 151.251 | 148.411 |  | 1326.121 | 1462.042 |  | 7.1497 | 7.1694 | 7.7661 | 7.7407 | 6.9512 | 6.9124 | 6.5933 | 6.7856 | 57.0684 | 0.051362 |  | 62.069 | 100
19980914163000 | 1998-09-14 16:30 | 646.706 |  | 1.762 | 148.61 | 151.655 | 151.169 | 147.447 |  | 1330.205 | 1462.875 |  | 7.1221 | 7.1602 | 7.76 | 7.7468 | 6.9451 | 6.9063 | 6.5828 | 6.7773 | 57.0006 | 0.051301 |  | 62.069 | 100
19980914170000 | 1998-09-14 17:00 | 652.316 |  | 0.289 | 148.876 | 151.773 | 151.163 | 147.813 |  | 1328.371 | 1468.209 |  | 7.1321 | 7.1633 | 7.7522 | 7.7224 | 6.9443 | 6.9023 | 6.582 | 6.7781 | 56.9767 | 0.051279 |  | 62.069 | 100
19980914173000 | 1998-09-14 17:30 | 649.747 |  | 2.006 | 148.489 | 151.799 | 151.34 | 147.838 |  | 1320.538 | 1455.958 |  | 7.1221 | 7.1443 | 7.7607 | 7.7156 | 6.9343 | 6.884 | 6.5667 | 6.7642 | 56.8919 | 0.051203 |  | 62.069 | 100
19980914180000 | 1998-09-14 18:00 | 649.275 |  | 0.411 | 148.622 | 151.814 | 150.993 | 146.863 |  | 1322.038 | 1455.958 |  | 7.1228 | 7.1411 | 7.7468 | 7.7202 | 6.9397 | 6.8933 | 6.5713 | 6.7659 | 56.9011 | 0.051211 |  | 62.069 | 100
19980914183000 | 1998-09-14 18:30 | 651.871 |  | 2.007 | 148.641 | 151.876 | 151.081 | 147.173 |  | 1328.705 | 1456.792 |  | 7.1313 | 7.1526 | 7.7637 | 7.7249 | 6.9565 | 6.8977 | 6.5759 | 6.7659 | 56.9685 | 0.051272 |  | 62.069 | 100
19980914190000 | 1998-09-14 19:00 | 650.245 |  | 0.083 | 148.641 | 151.278 | 151.132 | 147.565 |  | 1329.871 | 1457.458 |  | 7.1228 | 7.1357 | 7.7546 | 7.7148 | 6.939 | 6.8894 | 6.5667 | 6.7666 | 56.8896 | 0.051201 |  | 62.069 | 100
19980914193000 | 1998-09-14 19:30 | 649.8 |  | 1.516 | 148.797 | 152.072 | 151.162 | 146.627 |  | 1323.621 | 1456.042 |  | 7.1243 | 7.1418 | 7.75 | 7.7263 | 6.9368 | 6.8894 | 6.5713 | 6.7666 | 56.9065 | 0.051216 |  | 62.069 | 100
19980914200000 | 1998-09-14 20:00 | 651.766 |  | 0.083 | 148.858 | 152.619 | 151.127 | 148.658 |  | 1322.121 | 1453.375 |  | 7.1099 | 7.1304 | 7.7478 | 7.708 | 6.9307 | 6.8765 | 6.5659 | 6.7551 | 56.8243 | 0.051142 |  | 62.069 | 100
19980914203000 | 1998-09-14 20:30 | 650.036 |  | 2.129 | 148.828 | 152.046 | 151.067 | 147.838 |  | 1324.288 | 1457.375 |  | 7.1121 | 7.1436 | 7.7363 | 7.7034 | 6.9275 | 6.884 | 6.5674 | 6.772 | 56.8463 | 0.051162 |  | 62.069 | 100
19980914210000 | 1998-09-14 21:00 | 652.474 |  | 0.168 | 148.698 | 152.686 | 151.121 | 147.983 |  | 1323.038 | 1452.875 |  | 7.1091 | 7.1426 | 7.74 | 7.7119 | 6.9336 | 6.8855 | 6.5667 | 6.7627 | 56.8521 | 0.051167 |  | 62.069 | 100
19980914213000 | 1998-09-14 21:30 | 650.219 |  | 2.129 | 148.897 | 151.943 | 151.158 | 147.983 |  | 1329.371 | 1458.958 |  | 7.1282 | 7.1602 | 7.7651 | 7.7234 | 6.9558 | 6.9116 | 6.5781 | 6.7896 | 57.012 | 0.051311 |  | 62.069 | 100
19980914220000 | 1998-09-14 22:00 | 646.916 |  | 0.169 | 148.732 | 151.995 | 151.161 | 148.282 |  | 1323.705 | 1455.458 |  | 7.1274 | 7.158 | 7.7729 | 7.731 | 6.9534 | 6.8955 | 6.5659 | 6.7803 | 56.9844 | 0.051286 |  | 62.069 | 100
19980914223000 | 1998-09-14 22:30 | 575.535 |  | 1.395 | 148.578 | 149.778 | 150.938 | 145.817 |  | 1155.283 | 1266.87 |  | 6.2927 | 6.3394 | 6.8025 | 6.6621 | 6.1311 | 6.1204 | 5.8457 | 5.9854 | 50.1793 | 0.045161 |  | 62.069 | 100
19980914230000 | 1998-09-14 23:00 | 519.017 |  | 0.083 | 147.281 | 150.169 | 149.31 | 147.199 |  | 1030.78 | 1114.699 |  | 5.6794 | 5.697 | 5.9922 | 5.8167 | 5.5291 | 5.4939 | 5.2551 | 5.3604 | 44.8238 | 0.040341 |  | 62.069 | 100
19980914233000 | 1998-09-14 23:30 | 426.69 |  | 1.643 | 146.886 | 148.596 | 148.984 | 146.121 |  | 871.275 | 949.111 |  | 4.9072 | 4.937 | 5.0308 | 4.8494 | 4.7966 | 4.9036 | 4.6907 | 4.6541 | 38.7694 | 0.034892 |  | 62.069 | 100
19980915000000 | 1998-09-15 | 336.696 |  | 0 | 147.374 | 149.664 | 149.611 | 148.178 |  | 699.52 | 754.688 |  | 4.0908 | 4.0786 | 4.0369 | 3.1061 | 4.0222 | 4.2046 | 4.0107 | 3.8285 | 31.3784 | 0.028241 |  | 62.069 | 100
19980915003000 | 1998-09-15 00:30 | 343.197 |  | 2.012 | 147.278 | 150.159 | 149.985 | 149.168 |  | 713.521 | 775.022 |  | 4.2122 | 4.21 | 4.2078 | 3.2808 | 4.1482 | 4.3167 | 4.1055 | 3.9392 | 32.4204 | 0.029178 |  | 62.069 | 100
19980915010000 | 1998-09-15 01:00 | 344.377 |  | 0 | 147.898 | 151.37 | 150.516 | 149.885 |  | 720.354 | 780.939 |  | 4.1956 | 4.22 | 4.1755 | 3.2266 | 4.1152 | 4.2739 | 4.0879 | 3.9331 | 32.2278 | 0.029005 |  | 62.069 | 100
19980915013000 | 1998-09-15 01:30 | 349.384 |  | 1.273 | 148.627 | 150.968 | 150.918 | 148.988 |  | 730.438 | 791.273 |  | 4.3748 | 4.3572 | 4.3848 | 3.3967 | 4.2756 | 4.406 | 2.9115 | 4.084 | 32.1906 | 0.028972 |  | 62.069 | 100
19980915020000 | 1998-09-15 02:00 | 342.07 |  | 0 | 148.981 | 151.035 | 151.253 | 149.549 |  | 740.021 | 801.356 |  | 4.4534 | 4.4832 | 4.4753 | 3.4836 | 4.3503 | 4.48 | 2.9474 | 4.1633 | 32.8365 | 0.029553 |  | 62.069 | 100
19980915023000 | 1998-09-15 02:30 | 339.921 |  | 2.008 | 148.821 | 150.266 | 151.442 | 149.276 |  | 736.188 | 798.19 |  | 4.6265 | 4.6472 | 4.6533 | 3.7034 | 4.4846 | 4.6106 | 1.5565 | 4.3374 | 32.6195 | 0.029358 |  | 62.069 | 100
19980915030000 | 1998-09-15 03:00 | 339.606 |  | 20.712 | 148.66 | 151.179 | 150.996 | 150.189 |  | 735.188 | 795.69 |  | 4.3892 | 4.3923 | 4.4053 | 3.4265 | 4.2915 | 4.4021 | 2.9382 | 4.126 | 32.3711 | 0.029134 |  | 62.069 | 100
19980915033000 | 1998-09-15 03:30 | 343.302 |  | 2.255 | 148.573 | 150.709 | 151.221 | 147.739 |  | 732.521 | 799.356 |  | 4.3953 | 4.3884 | 4.416 | 3.4303 | 4.2976 | 4.374 | 2.9878 | 4.1047 | 32.3941 | 0.029155 |  | 62.069 | 100
19980915040000 | 1998-09-15 04:00 | 342.096 |  | 0 | 148.801 | 151.973 | 150.923 | 149.993 |  | 734.854 | 810.19 |  | 4.4343 | 4.4419 | 4.4702 | 3.4852 | 4.332 | 4.4175 | 3.0214 | 4.1497 | 32.7522 | 0.029477 |  | 62.069 | 100
19980915043000 | 1998-09-15 04:30 | 338.951 |  | 1.434 | 149.085 | 150.333 | 151.444 | 149.095 |  | 733.688 | 813.107 |  | 4.4128 | 4.3899 | 4.4373 | 3.4517 | 4.3098 | 4.3809 | 2.9993 | 4.1274 | 32.5091 | 0.029258 |  | 62.069 | 100
19980915050000 | 1998-09-15 05:00 | 344.928 |  | 0 | 148.261 | 150.214 | 150.756 | 148.482 |  | 726.437 | 788.773 |  | 4.3909 | 4.3823 | 4.397 | 3.4073 | 4.2778 | 4.3374 | 2.9801 | 4.0872 | 32.26 | 0.029034 |  | 62.069 | 100
19980915053000 | 1998-09-15 05:30 | 346.631 |  | 0.207 | 148.354 | 150.709 | 150.645 | 149.967 |  | 728.271 | 790.023 |  | 4.3823 | 4.3809 | 4.3923 | 3.4089 | 4.2786 | 4.3313 | 2.9756 | 4.094 | 32.2439 | 0.02902 |  | 62.069 | 100
19980915060000 | 1998-09-15 06:00 | 344.272 |  | 0 | 149.46 | 150.111 | 151.972 | 149.368 |  | 748.938 | 813.523 |  | 4.4397 | 4.4373 | 4.4854 | 3.4761 | 4.3381 | 4.3953 | 3.0167 | 4.1475 | 32.7361 | 0.029462 |  | 62.069 | 100
19980915063000 | 1998-09-15 06:30 | 337.456 |  | 2.254 | 148.744 | 150.359 | 151.414 | 148.626 |  | 739.188 | 804.94 |  | 4.3672 | 4.3748 | 4.374 | 3.4204 | 4.2566 | 4.3359 | 2.9672 | 4.094 | 32.1901 | 0.028971 |  | 62.069 | 100
19980915070000 | 1998-09-15 07:00 | 411.538 |  | 0.084 | 148.38 | 151.075 | 150.591 | 149.095 |  | 914.193 | 997.779 |  | 5.2712 | 5.3132 | 5.4773 | 4.4778 | 5.1606 | 5.2009 | 3.576 | 5.0088 | 39.4858 | 0.035537 |  | 62.069 | 100
19980915073000 | 1998-09-15 07:30 | 519.672 |  | 20.134 | 150.045 | 153.041 | 152.848 | 151.06 |  | 1095.948 | 1195.534 |  | 6.0867 | 6.0967 | 6.4927 | 6.4263 | 5.9128 | 5.9128 | 4.0979 | 5.7549 | 46.7808 | 0.042103 |  | 62.069 | 100
19980915080000 | 1998-09-15 08:00 | 623.664 |  | 0.784 | 149.657 | 152.701 | 152.38 | 148.988 |  | 1286.454 | 1414.374 |  | 7.0901 | 7.1365 | 7.7141 | 7.7224 | 6.9009 | 6.8811 | 4.7815 | 6.7551 | 54.9817 | 0.049484 |  | 62.069 | 100
19980915083000 | 1998-09-15 08:30 | 642.276 |  | 2.254 | 149.728 | 152.242 | 152.421 | 148.777 |  | 1317.121 | 1447.875 |  | 6.9802 | 7.0168 | 7.605 | 7.5554 | 6.7932 | 6.7544 | 6.6841 | 6.6543 | 56.0434 | 0.050439 |  | 62.069 | 100
19980915090000 | 1998-09-15 09:00 | 651.137 |  | 0.412 | 149.198 | 152.139 | 151.812 | 147.683 |  | 1316.038 | 1444.208 |  | 7.0632 | 7.1008 | 7.689 | 7.6814 | 6.875 | 6.8359 | 6.7803 | 6.7415 | 56.7671 | 0.05109 |  | 62.069 | 100
19980915093000 | 1998-09-15 09:30 | 649.747 |  | 2.004 | 148.791 | 151.773 | 151.363 | 148.06 |  | 1318.038 | 1445.792 |  | 7.0503 | 7.093 | 7.6707 | 7.6523 | 6.8589 | 6.8374 | 6.7673 | 6.73 | 56.6599 | 0.050994 |  | 62.069 | 100
19980915100000 | 1998-09-15 10:00 | 652.002 |  | 0.327 | 148.727 | 151.644 | 151.333 | 147.931 |  | 1312.954 | 1444.958 |  | 7.061 | 7.1008 | 7.7019 | 7.6768 | 6.8811 | 6.8306 | 6.7703 | 6.7354 | 56.7579 | 0.051082 |  | 62.069 | 100
19980915103000 | 1998-09-15 10:30 | 654.466 |  | 1.398 | 148.662 | 151.263 | 150.95 | 147.302 |  | 1316.704 | 1446.042 |  | 7.0862 | 7.0984 | 7.7126 | 7.6729 | 6.9023 | 6.8374 | 6.7681 | 6.7329 | 56.8108 | 0.05113 |  | 62.069 | 100
19980915110000 | 1998-09-15 11:00 | 654.02 |  | 0.41 | 148.348 | 152.32 | 150.783 | 148.112 |  | 1321.621 | 1448.458 |  | 7.0535 | 7.0779 | 7.6821 | 7.6477 | 6.8833 | 6.8086 | 6.7559 | 6.7153 | 56.6243 | 0.050962 |  | 62.069 | 100
19980915113000 | 1998-09-15 11:30 | 650.507 |  | 2.005 | 149.038 | 151.67 | 151.382 | 147.957 |  | 1320.955 | 1453.375 |  | 7.0496 | 7.0916 | 7.6821 | 7.6423 | 6.8772 | 6.823 | 6.7666 | 6.7268 | 56.6592 | 0.050993 |  | 62.069 | 100
19980915120000 | 1998-09-15 12:00 | 650.691 |  | 0.166 | 148.778 | 151.381 | 151.369 | 147.916 |  | 1323.455 | 1449.958 |  | 7.0442 | 7.0916 | 7.6814 | 7.647 | 6.8704 | 6.8284 | 6.7605 | 6.7192 | 56.6427 | 0.050978 |  | 62.069 | 100
19980915123000 | 1998-09-15 12:30 | 652.054 |  | 2.009 | 148.834 | 151.655 | 151.177 | 147.942 |  | 1324.955 | 1454.458 |  | 7.0825 | 7.1069 | 7.7065 | 7.6675 | 6.8977 | 6.842 | 6.7712 | 6.7336 | 56.8079 | 0.051127 |  | 62.069 | 100
19980915130000 | 1998-09-15 13:00 | 647.231 |  | 0.533 | 149.051 | 151.525 | 151.477 | 147.565 |  | 1317.038 | 1450.708 |  | 7.0747 | 7.0991 | 7.6958 | 7.6516 | 6.8872 | 6.8298 | 6.7727 | 6.7346 | 56.7455 | 0.051071 |  | 62.069 | 100
19980915133000 | 1998-09-15 13:30 | 640.205 |  | 1.642 | 148.713 | 151.355 | 150.948 | 146.652 |  | 1291.787 | 1418.874 |  | 6.949 | 7.0032 | 7.5669 | 7.5508 | 6.7788 | 6.7085 | 6.6506 | 6.6316 | 55.8394 | 0.050255 |  | 62.069 | 100
19980915140000 | 1998-09-15 14:00 | 603.007 |  | 0.168 | 147.784 | 151.16 | 149.974 | 147.199 |  | 1222.535 | 1334.372 |  | 6.5591 | 6.5925 | 7.0854 | 6.9824 | 6.3889 | 6.3516 | 6.2852 | 6.2324 | 52.4775 | 0.04723 |  | 62.069 | 100
19980915143000 | 1998-09-15 14:30 | 597.581 |  | 1.888 | 148.218 | 151.799 | 150.666 | 147.591 |  | 1218.368 | 1330.788 |  | 6.5713 | 6.6018 | 7.0908 | 7.0022 | 6.4019 | 6.3752 | 6.3157 | 6.2532 | 52.6121 | 0.047351 |  | 62.069 | 100
19980915150000 | 1998-09-15 15:00 | 595.903 |  | 0 | 148.827 | 152.175 | 151.293 | 148.215 |  | 1217.702 | 1331.788 |  | 6.5781 | 6.5857 | 7.106 | 7.0007 | 6.4172 | 6.3789 | 6.3081 | 6.2402 | 52.6149 | 0.047353 |  | 62.069 | 100
19980915153000 | 1998-09-15 15:30 | 641.464 |  | 2.505 | 149.101 | 153.062 | 151.569 | 149.349 |  | 1316.954 | 1450.792 |  | 7.0374 | 7.0869 | 7.6775 | 7.6379 | 6.8772 | 6.8313 | 6.7742 | 6.7192 | 56.6416 | 0.050977 |  | 62.069 | 100
19980915160000 | 1998-09-15 16:00 | 649.433 |  | 0.091 | 149.457 | 151.695 | 152.166 | 148.23 |  | 1328.788 | 1460.459 |  | 7.0786 | 7.1213 | 7.7119 | 7.6699 | 6.9009 | 6.8521 | 6.7896 | 6.7422 | 56.8665 | 0.05118 |  | 62.069 | 100
19980915163000 | 1998-09-15 16:30 | 648.174 |  | 1.524 | 148.47 | 151.263 | 151.351 | 147.302 |  | 1320.371 | 1449.208 |  | 7.071 | 7.116 | 7.7051 | 7.6736 | 6.9001 | 6.8474 | 6.7817 | 6.7415 | 56.8364 | 0.051153 |  | 62.069 | 100
19980915170000 | 1998-09-15 17:00 | 652.369 |  | 0.169 | 148.562 | 152.501 | 151.082 | 147.798 |  | 1330.121 | 1458.875 |  | 7.0962 | 7.1282 | 7.7263 | 7.7034 | 6.9177 | 6.875 | 6.8069 | 6.759 | 57.0127 | 0.051311 |  | 62.069 | 100
19980915173000 | 1998-09-15 17:30 | 646.575 |  | 22.518 | 148.883 | 150.953 | 151.145 | 147.24 |  | 1330.288 | 1462.292 |  | 7.0779 | 7.0999 | 7.6958 | 7.6584 | 6.8923 | 6.8474 | 6.7849 | 6.73 | 56.7866 | 0.051108 |  | 62.069 | 100
19980915180000 | 1998-09-15 18:00 | 645.527 |  | 0.293 | 148.492 | 151.566 | 151.169 | 147.111 |  | 1332.122 | 1462.042 |  | 7.0833 | 7.1121 | 7.7202 | 7.6882 | 6.9031 | 6.8618 | 6.7957 | 6.7444 | 56.9088 | 0.051218 |  | 62.069 | 100
19980915183000 | 1998-09-15 18:30 | 650.901 |  | 2.136 | 148.81 | 151.917 | 151.113 | 147.462 |  | 1328.955 | 1461.792 |  | 7.0754 | 7.1069 | 7.7102 | 7.6667 | 6.8955 | 6.8542 | 6.791 | 6.739 | 56.8389 | 0.051155 |  | 62.069 | 100
19980915190000 | 1998-09-15 19:00 | 647.388 |  | 0.168 | 149.032 | 151.149 | 151.239 | 147.931 |  | 1334.788 | 1465.625 |  | 7.093 | 7.1221 | 7.7439 | 7.7058 | 6.9138 | 6.8679 | 6.8101 | 6.7437 | 57.0003 | 0.0513 |  | 62.069 | 100
19980915193000 | 1998-09-15 19:30 | 645.474 |  | 1.645 | 148.413 | 151.68 | 151.072 | 147.225 |  | 1329.788 | 1463.792 |  | 7.0808 | 7.116 | 7.7256 | 7.6958 | 6.9031 | 6.8665 | 6.8069 | 6.7476 | 56.9423 | 0.051248 |  | 62.069 | 100
19980915200000 | 1998-09-15 20:00 | 650.743 |  | 0.168 | 148.698 | 151.747 | 150.903 | 147.787 |  | 1331.705 | 1462.125 |  | 7.0991 | 7.1167 | 7.731 | 7.6882 | 6.9138 | 6.865 | 6.7993 | 6.7483 | 56.9614 | 0.051265 |  | 62.069 | 100
19980915203000 | 1998-09-15 20:30 | 604.842 |  | 2.012 | 149.059 | 150.783 | 151.267 | 147.318 |  | 1224.118 | 1342.955 |  | 6.5566 | 6.5796 | 7.1106 | 7.0259 | 6.3965 | 6.3523 | 6.2859 | 6.2385 | 52.5459 | 0.047291 |  | 62.069 | 100
19980915210000 | 1998-09-15 21:00 | 577.422 |  | 0.082 | 147.51 | 150.509 | 149.671 | 146.797 |  | 1184.701 | 1286.704 |  | 6.3835 | 6.408 | 6.8604 | 6.7712 | 6.2195 | 6.1997 | 6.1394 | 6.0601 | 51.0418 | 0.045938 |  | 62.069 | 100
19980915213000 | 1998-09-15 21:30 | 480.639 |  | 1.525 | 147.466 | 148.648 | 149.737 | 145.677 |  | 972.195 | 1052.78 |  | 5.3384 | 5.333 | 5.584 | 5.3406 | 5.2095 | 5.2515 | 5.1865 | 5.043 | 42.2865 | 0.038058 |  | 62.069 | 100
19980915220000 | 1998-09-15 22:00 | 469.236 |  | 19.219 | 147.128 | 151.278 | 149.222 | 148.308 |  | 993.945 | 1074.531 |  | 5.3521 | 5.3682 | 5.5955 | 5.4192 | 5.2339 | 5.2964 | 5.23 | 5.0752 | 42.5705 | 0.038313 |  | 62.069 | 100
19980915223000 | 1998-09-15 22:30 | 420.398 |  | 1.688 | 148.985 | 149.623 | 151.319 | 147.395 |  | 891.442 | 967.528 |  | 4.8914 | 4.9026 | 5.0178 | 4.7998 | 4.7744 | 4.8806 | 4.8225 | 4.615 | 38.7041 | 0.034834 |  | 62.069 | 100
19980915230000 | 1998-09-15 23:00 | 338.19 |  | 0 | 147.902 | 149.117 | 150.387 | 148.374 |  | 750.688 | 810.107 |  | 4.1489 | 4.1008 | 4.1145 | 4.0474 | 4.0703 | 4.2114 | 4.1519 | 3.8538 | 32.699 | 0.029429 |  | 62.069 | 100
19980915233000 | 1998-09-15 23:30 | 334.232 |  | 2.056 | 147.492 | 149.209 | 149.829 | 148.467 |  | 748.271 | 814.69 |  | 4.1313 | 4.104 | 4.1077 | 4.0657 | 4.0674 | 4.2161 | 4.1565 | 3.8484 | 32.6971 | 0.029427 |  | 62.069 | 100
19980916000000 | 1998-09-16 | 344.272 |  | 0 | 148.185 | 150.72 | 150.732 | 149.235 |  | 743.688 | 808.19 |  | 4.0872 | 4.0908 | 4.0444 | 4.0125 | 4.0039 | 4.1687 | 4.1152 | 3.8354 | 32.3581 | 0.029122 |  | 62.069 | 100
19980916003000 | 1998-09-16 00:30 | 347.732 |  | 1.686 | 147.953 | 149.483 | 150.578 | 147.75 |  | 736.271 | 799.106 |  | 4.0674 | 4.0764 | 4.0315 | 4.0291 | 4.0002 | 4.1458 | 4.1055 | 3.8278 | 32.2837 | 0.029055 |  | 62.069 | 100
19980916010000 | 1998-09-16 01:00 | 343.066 |  | 0 | 148.241 | 151.02 | 150.621 | 149.782 |  | 744.855 | 805.44 |  | 4.1077 | 4.1284 | 4.0796 | 4.0803 | 4.033 | 4.168 | 4.1489 | 3.8629 | 32.6088 | 0.029348 |  | 62.069 | 100
19980916013000 | 1998-09-16 01:30 | 334.049 |  | 1.687 | 148.976 | 151.045 | 151.446 | 149.313 |  | 746.771 | 809.273 |  | 4.3489 | 4.3572 | 3.016 | 4.3931 | 4.2642 | 4.3374 | 4.3489 | 4.0757 | 33.1414 | 0.029827 |  | 62.069 | 100
19980916020000 | 1998-09-16 02:00 | 335.359 |  | 0 | 148.691 | 151.02 | 151.393 | 149.782 |  | 735.938 | 793.439 |  | 4.2466 | 4.2566 | 3.0045 | 4.3167 | 4.1848 | 4.2703 | 4.2976 | 4.0017 | 32.5788 | 0.029321 |  | 62.069 | 100
19980916023000 | 1998-09-16 02:30 | 343.119 |  | 2.303 | 148.631 | 151.644 | 150.911 | 149.168 |  | 737.771 | 799.19 |  | 4.0803 | 4.0757 | 4.0994 | 4.0261 | 4.0032 | 4.0796 | 4.1145 | 3.8232 | 32.302 | 0.029072 |  | 62.069 | 100
19980916030000 | 1998-09-16 03:00 | 346.579 |  | 0 | 148.706 | 149.313 | 150.884 | 148.075 |  | 738.438 | 800.356 |  | 4.0771 | 4.0491 | 4.0474 | 3.9918 | 3.9902 | 4.0337 | 4.0742 | 3.7897 | 32.0532 | 0.028848 |  | 62.069 | 100
19980916033000 | 1998-09-16 03:30 | 348.231 |  | 2.181 | 148.313 | 150.602 | 151.072 | 149.117 |  | 735.354 | 800.94 |  | 4.0955 | 4.0857 | 4.0825 | 3.9933 | 4.0002 | 4.033 | 4.0947 | 3.8033 | 32.1882 | 0.028969 |  | 62.069 | 100
19980916040000 | 1998-09-16 04:00 | 342.988 |  | 0 | 148.407 | 150.576 | 150.856 | 148.843 |  | 735.604 | 794.856 |  | 4.1047 | 4.0969 | 4.1145 | 4.0498 | 4.0413 | 4.0657 | 4.1443 | 3.8438 | 32.461 | 0.029215 |  | 62.069 | 100
19980916043000 | 1998-09-16 04:30 | 343.145 |  | 1.812 | 148.629 | 151.685 | 150.83 | 149.952 |  | 725.687 | 783.106 |  | 4.1711 | 4.1963 | 4.219 | 3.4738 | 4.1047 | 4.1382 | 4.2046 | 3.9155 | 32.4232 | 0.029181 |  | 62.069 | 100
19980916050000 | 1998-09-16 05:00 | 347.156 |  | 0 | 148.631 | 150.421 | 151.456 | 149.679 |  | 730.438 | 787.689 |  | 4.1848 | 4.1877 | 4.2275 | 3.4639 | 4.1055 | 4.1396 | 4.1855 | 3.9071 | 32.4016 | 0.029161 |  | 62.069 | 100
19980916053000 | 1998-09-16 05:30 | 345.19 |  | 2.67 | 148.866 | 150.524 | 151.342 | 149.782 |  | 736.938 | 795.773 |  | 4.2153 | 4.2068 | 4.271 | 3.4714 | 4.1382 | 4.1572 | 4.2053 | 3.927 | 32.5922 | 0.029333 |  | 62.069 | 100
19980916060000 | 1998-09-16 06:00 | 338.322 |  | 0 | 149.465 | 152.128 | 151.655 | 149.9 |  | 758.105 | 820.774 |  | 4.2458 | 4.248 | 4.3237 | 3.5287 | 4.1748 | 4.2031 | 4.2566 | 3.9674 | 32.9481 | 0.029653 |  | 62.069 | 100
19980916063000 | 1998-09-16 06:30 | 343.774 |  | 2.55 | 149.46 | 150.019 | 151.832 | 148.286 |  | 746.438 | 807.69 |  | 4.1802 | 4.1755 | 4.2312 | 3.4379 | 4.1091 | 4.1375 | 4.1924 | 3.8995 | 32.3633 | 0.029127 |  | 62.069 | 100
19980916070000 | 1998-09-16 07:00 | 384.564 |  | 0 | 148.359 | 150.292 | 150.799 | 148.807 |  | 849.358 | 921.443 |  | 4.7051 | 4.7349 | 4.8669 | 4.0635 | 4.5938 | 4.6411 | 4.6968 | 4.4214 | 36.7235 | 0.033051 |  | 62.069 | 100
19980916073000 | 1998-09-16 07:30 | 505.044 |  | 1.895 | 149.614 | 153.391 | 152.017 | 151.659 |  | 1092.698 | 1197.534 |  | 5.8008 | 5.8335 | 6.2776 | 5.2285 | 5.6572 | 5.655 | 5.636 | 5.5054 | 45.594 | 0.041035 |  | 62.069 | 100
19980916080000 | 1998-09-16 08:00 | 633.363 |  | 0.458 | 150.661 | 152.752 | 153.424 | 150.524 |  | 1323.205 | 1453.125 |  | 7.0886 | 7.1572 | 7.8796 | 6.6086 | 6.9001 | 6.9016 | 6.8406 | 6.7773 | 56.1536 | 0.050538 |  | 62.069 | 100
19980916083000 | 1998-09-16 08:30 | 650.298 |  | 2.631 | 149.752 | 152.737 | 152.502 | 148.529 |  | 1339.372 | 1468.542 |  | 7.2312 | 7.2786 | 8.0718 | 6.7253 | 7.0703 | 6.9863 | 6.9238 | 6.9619 | 57.2492 | 0.051524 |  | 62.069 | 100
19980916090000 | 1998-09-16 09:00 | 651.661 |  | 0.419 | 149.108 | 151.2 | 151.69 | 148.23 |  | 1329.371 | 1459.709 |  | 7.0876 | 7.1252 | 8.084 | 6.7458 | 7.1121 | 6.8696 | 6.8069 | 7.0503 | 56.8815 | 0.051193 |  | 62.069 | 100
19980916093000 | 1998-09-16 09:30 | 652.211 |  | 1.651 | 148.41 | 151.773 | 151.341 | 147.318 |  | 1319.621 | 1451.458 |  | 6.8933 | 6.9412 | 7.9651 | 7.824 | 6.929 | 6.6719 | 6.6125 | 6.8826 | 56.7196 | 0.051048 |  | 62.069 | 100
19980916100000 | 1998-09-16 10:00 | 652.395 |  | 0.173 | 148.521 | 151.381 | 150.938 | 147.421 |  | 1321.871 | 1453.042 |  | 6.926 | 6.9543 | 8.0308 | 7.8416 | 6.9429 | 6.6858 | 6.6316 | 6.8948 | 56.9078 | 0.051217 |  | 62.069 | 100
19980916103000 | 1998-09-16 10:30 | 652.133 |  | 0.298 | 148.718 | 151.876 | 150.899 | 147.421 |  | 1322.705 | 1449.042 |  | 6.9092 | 6.9612 | 8.0635 | 7.8689 | 6.9512 | 6.6948 | 6.6399 | 6.9031 | 56.9918 | 0.051293 |  | 62.069 | 100
19980916110000 | 1998-09-16 11:00 | 657.061 |  | 0.174 | 149.022 | 152.072 | 151.293 | 148.607 |  | 1324.288 | 1451.375 |  | 6.929 | 6.9612 | 8.0664 | 7.8613 | 6.9512 | 6.6956 | 6.6377 | 6.916 | 57.0184 | 0.051317 |  | 62.069 | 100
19980916113000 | 1998-09-16 11:30 | 654.282 |  | 2.262 | 148.734 | 151.433 | 151.445 | 148.215 |  | 1321.705 | 1451.208 |  | 6.939 | 6.9734 | 8.0718 | 7.8523 | 6.9604 | 6.7056 | 6.6506 | 6.9185 | 57.0716 | 0.051364 |  | 62.069 | 100
19980916120000 | 1998-09-16 12:00 | 577.973 |  | 0 | 148.205 | 149.974 | 150.639 | 144.528 |  | 1179.284 | 1276.203 |  | 6.1836 | 6.2119 | 7.2358 | 6.9382 | 6.2698 | 5.98 | 5.9319 | 6.199 | 50.9502 | 0.045855 |  | 62.069 | 100
19980916123000 | 1998-09-16 12:30 | 545.755 |  | 19.417 | 147.494 | 150.535 | 149.389 | 147.318 |  | 1064.781 | 1152.533 |  | 5.6382 | 5.5854 | 6.5415 | 6.2012 | 5.7556 | 5.4536 | 5.4048 | 5.6838 | 46.2641 | 0.041638 |  | 62.069 | 100
19980916130000 | 1998-09-16 13:00 | 518.833 |  | 0 | 147.763 | 151.2 | 149.874 | 148.23 |  | 1053.697 | 1142.283 |  | 5.5923 | 5.5977 | 6.5247 | 6.199 | 5.7793 | 5.4878 | 5.4314 | 5.6992 | 46.3114 | 0.04168 |  | 62.069 | 100
19980916133000 | 1998-09-16 13:30 | 519.882 |  | 1.4 | 148.915 | 151.211 | 151.021 | 148.983 |  | 1062.031 | 1151.616 |  | 5.5215 | 5.52 | 6.3979 | 6.0938 | 5.7107 | 5.4246 | 5.3643 | 5.6123 | 45.6451 | 0.041081 |  | 62.069 | 100
19980916140000 | 1998-09-16 14:00 | 519.672 |  | 0.082 | 148.615 | 150.447 | 151.404 | 147.477 |  | 1055.28 | 1146.866 |  | 5.5283 | 5.5649 | 6.4346 | 6.157 | 5.7419 | 5.4536 | 5.3918 | 5.635 | 45.9071 | 0.041316 |  | 62.069 | 100
19980916143000 | 1998-09-16 14:30 | 515.661 |  | 2.176 | 148.509 | 150.875 | 151.07 | 148.153 |  | 1051.864 | 1142.949 |  | 5.5352 | 5.5444 | 6.4072 | 6.1172 | 5.7258 | 5.4375 | 5.3779 | 5.6206 | 45.7658 | 0.041189 |  | 62.069 | 100
19980916150000 | 1998-09-16 15:00 | 521.953 |  | 0 | 148.66 | 151.37 | 150.893 | 148.153 |  | 1053.364 | 1144.449 |  | 5.5251 | 5.5481 | 6.4417 | 6.1387 | 5.7419 | 5.4497 | 5.3933 | 5.6282 | 45.8667 | 0.04128 |  | 62.069 | 100
19980916153000 | 1998-09-16 15:30 | 498.307 |  | 2.301 | 148.839 | 150.783 | 150.936 | 148.308 |  | 979.361 | 1066.697 |  | 5.1926 | 5.188 | 5.9646 | 5.6604 | 5.3772 | 5.0645 | 5.0117 | 5.2605 | 42.7195 | 0.038448 |  | 62.069 | 100
19980916160000 | 1998-09-16 16:00 | 473.168 |  | 0 | 148.443 | 149.106 | 150.487 | 147.126 |  | 960.278 | 1044.613 |  | 5.1025 | 5.1079 | 5.8816 | 5.5688 | 5.3628 | 5.0591 | 5.0081 | 5.2346 | 42.3254 | 0.038093 |  | 62.069 | 100
19980916163000 | 1998-09-16 16:30 | 475.186 |  | 1.319 | 147.988 | 151.071 | 150.693 | 148.843 |  | 962.861 | 1044.863 |  | 5.0813 | 5.0942 | 5.8442 | 5.5391 | 5.3474 | 5.0408 | 4.9873 | 5.2087 | 42.143 | 0.037929 |  | 62.069 | 100
19980916170000 | 1998-09-16 17:00 | 471.176 |  | 0 | 148.411 | 151.747 | 151.33 | 148.034 |  | 963.778 | 1046.447 |  | 5.0684 | 5.1025 | 5.8564 | 5.5786 | 5.3542 | 5.0537 | 4.9973 | 5.2185 | 42.2296 | 0.038007 |  | 62.069 | 100
19980916173000 | 1998-09-16 17:30 | 473.43 |  | 1.688 | 149.012 | 151.463 | 151.289 | 149.235 |  | 966.694 | 1051.947 |  | 5.1094 | 5.1118 | 5.8816 | 5.5947 | 5.3765 | 5.0896 | 5.0378 | 5.2651 | 42.4665 | 0.03822 |  | 62.069 | 100
19980916180000 | 1998-09-16 18:00 | 540.198 |  | 0 | 149.527 | 153.351 | 152.095 | 150.38 |  | 1126.366 | 1220.868 |  | 5.8762 | 5.9075 | 6.7986 | 6.5688 | 6.0486 | 5.7556 | 5.6985 | 5.9333 | 48.5871 | 0.043728 |  | 62.069 | 100
19980916183000 | 1998-09-16 18:30 | 543.501 |  | 2.266 | 149.536 | 151.304 | 151.993 | 148.333 |  | 1129.949 | 1228.869 |  | 5.8547 | 5.8801 | 6.7764 | 6.5444 | 6.0173 | 5.7319 | 5.6716 | 5.9045 | 48.3809 | 0.043543 |  | 62.069 | 100
19980916190000 | 1998-09-16 19:00 | 544.759 |  | 0.082 | 148.598 | 150.979 | 150.997 | 148.008 |  | 1137.533 | 1229.952 |  | 5.9028 | 5.9341 | 6.8345 | 6.6147 | 6.0073 | 5.7954 | 5.7351 | 5.7229 | 48.5468 | 0.043692 |  | 62.069 | 100
19980916193000 | 1998-09-16 19:30 | 544.864 |  | 1.525 | 148.363 | 151.995 | 150.785 | 147.787 |  | 1128.699 | 1229.702 |  | 5.9846 | 6.0266 | 6.7573 | 6.7192 | 5.8618 | 5.8418 | 5.7886 | 5.6909 | 48.6708 | 0.043804 |  | 62.069 | 100
19980916200000 | 1998-09-16 20:00 | 551.653 |  | 0.082 | 148.508 | 151.278 | 150.67 | 148.555 |  | 1115.449 | 1215.785 |  | 6.0579 | 6.0938 | 6.6726 | 6.3613 | 5.9158 | 5.9204 | 5.8608 | 5.7693 | 48.6519 | 0.043787 |  | 62.069 | 100
19980916203000 | 1998-09-16 20:30 | 547.38 |  | 1.897 | 148.644 | 151.175 | 151.244 | 148.204 |  | 1115.365 | 1211.951 |  | 6.0439 | 6.1143 | 6.5918 | 6.3469 | 5.9236 | 5.9219 | 5.8633 | 5.7703 | 48.576 | 0.043718 |  | 62.069 | 100
19980916210000 | 1998-09-16 21:00 | 458.986 |  | 0.091 | 148.568 | 150.406 | 151.013 | 146.941 |  | 905.443 | 984.028 |  | 5.0378 | 5.021 | 5.2422 | 4.9568 | 4.9004 | 4.9561 | 4.9043 | 4.7532 | 39.7718 | 0.035795 |  | 62.069 | 100
19980916213000 | 1998-09-16 21:30 | 338.793 |  | 1.32 | 146.779 | 148.178 | 148.815 | 147.188 |  | 713.687 | 771.772 |  | 4.0146 | 3.9895 | 3.9705 | 3.5599 | 3.9484 | 4.1306 | 4.0674 | 3.7531 | 31.434 | 0.028291 |  | 62.069 | 100
19980916220000 | 1998-09-16 22:00 | 339.737 |  | 0 | 147.098 | 150.159 | 149.354 | 148.426 |  | 691.02 | 749.021 |  | 3.8804 | 3.8629 | 3.785 | 3.3716 | 3.8141 | 4.0229 | 3.9628 | 3.6362 | 30.3359 | 0.027302 |  | 62.069 | 100
19980916223000 | 1998-09-16 22:30 | 344.403 |  | 1.695 | 148.218 | 150.602 | 150.62 | 149.364 |  | 702.354 | 761.272 |  | 3.9583 | 3.9139 | 3.9178 | 3.4639 | 3.8956 | 4.0222 | 3.9827 | 3.6714 | 30.8258 | 0.027743 |  | 62.069 | 100
19980916230000 | 1998-09-16 23:00 | 340.471 |  | 0 | 148.645 | 150.055 | 151.233 | 148.323 |  | 706.437 | 766.605 |  | 3.9521 | 3.9545 | 3.9087 | 3.5386 | 3.8865 | 4.0405 | 4.0308 | 3.6989 | 31.0106 | 0.02791 |  | 62.069 | 100
19980916233000 | 1998-09-16 23:30 | 331.742 |  | 2.059 | 148.379 | 150.576 | 151.216 | 149.338 |  | 706.104 | 766.022 |  | 3.9811 | 3.9789 | 3.9392 | 3.5531 | 3.9094 | 4.0054 | 4.0444 | 3.7347 | 31.1462 | 0.028032 |  | 62.069 | 100
19980917000000 | 1998-09-17 | 328.334 |  | 0 | 148.49 | 150.55 | 150.981 | 148.57 |  | 705.687 | 761.855 |  | 4.0115 | 3.9758 | 3.9613 | 3.5477 | 3.9353 | 3.9735 | 4.0437 | 3.7332 | 31.182 | 0.028064 |  | 62.069 | 100
19980917003000 | 1998-09-17 00:30 | 331.82 |  | 2.426 | 148.638 | 151.566 | 150.931 | 149.834 |  | 707.354 | 765.605 |  | 4.0071 | 3.9803 | 3.9658 | 3.5721 | 3.9216 | 3.9506 | 4.0405 | 3.7362 | 31.1742 | 0.028057 |  | 62.069 | 100
19980917010000 | 1998-09-17 01:00 | 330.877 |  | 0 | 148.858 | 150.38 | 151.461 | 149.885 |  | 712.854 | 771.439 |  | 4.0283 | 4.0024 | 3.9865 | 3.5905 | 3.946 | 3.9773 | 4.0603 | 3.7522 | 31.3435 | 0.028209 |  | 62.069 | 100
19980917013000 | 1998-09-17 01:30 | 329.828 |  | 1.691 | 148.452 | 151.396 | 151.217 | 149.664 |  | 707.604 | 765.439 |  | 3.9963 | 3.9865 | 3.9536 | 3.4303 | 3.9384 | 3.9735 | 4.0459 | 3.7347 | 31.0592 | 0.027953 |  | 62.069 | 100
19980917020000 | 1998-09-17 02:00 | 329.828 |  | 0 | 148.888 | 152.035 | 151.113 | 149.808 |  | 699.437 | 757.272 |  | 4.042 | 4.0894 | 4.033 | 2.6422 | 3.985 | 4.0674 | 4.1467 | 3.8613 | 30.867 | 0.02778 |  | 62.069 | 100
19980917023000 | 1998-09-17 02:30 | 334.94 |  | 2.182 | 148.561 | 150.602 | 151.239 | 148.622 |  | 699.77 | 756.022 |  | 3.9628 | 3.9963 | 3.8873 | 3.4852 | 3.882 | 3.9613 | 4.0369 | 3.7568 | 30.9686 | 0.027872 |  | 62.069 | 100
19980917030000 | 1998-09-17 03:00 | 335.91 |  | 19.099 | 148.273 | 151.644 | 150.449 | 149.664 |  | 703.104 | 758.438 |  | 3.9102 | 3.9628 | 3.8773 | 3.7134 | 3.8324 | 3.9453 | 4.0107 | 3.7332 | 30.9853 | 0.027887 |  | 62.069 | 100
19980917033000 | 1998-09-17 03:30 | 332.056 |  | 2.431 | 148.968 | 151.045 | 151.285 | 149.065 |  | 708.77 | 769.272 |  | 3.962 | 4.0161 | 3.9224 | 3.7675 | 3.8881 | 4.0039 | 4.052 | 3.7728 | 31.3848 | 0.028246 |  | 62.069 | 100
19980917040000 | 1998-09-17 04:00 | 331.506 |  | 0 | 148.705 | 151.045 | 151.015 | 149.313 |  | 700.02 | 755.355 |  | 3.9674 | 3.9949 | 3.9261 | 3.7545 | 3.8926 | 3.9712 | 4.0261 | 3.7461 | 31.2789 | 0.028151 |  | 62.069 | 100
19980917043000 | 1998-09-17 04:30 | 334.416 |  | 1.939 | 149.127 | 152.113 | 151.034 | 150.628 |  | 719.104 | 776.356 |  | 4.0078 | 4.0168 | 3.9667 | 3.7805 | 3.9384 | 3.9857 | 4.0359 | 3.7637 | 31.4955 | 0.028346 |  | 62.069 | 100
19980917050000 | 1998-09-17 05:00 | 346.736 |  | 0 | 149.347 | 150.576 | 151.678 | 149.091 |  | 734.271 | 791.606 |  | 4.0864 | 4.0994 | 4.0969 | 3.8773 | 3.9994 | 4.0444 | 4.0947 | 3.8416 | 32.1401 | 0.028926 |  | 62.069 | 100
19980917053000 | 1998-09-17 05:30 | 341.467 |  | 2.427 | 148.783 | 150.705 | 151.476 | 149.468 |  | 740.938 | 798.94 |  | 4.104 | 4.1292 | 4.0955 | 3.9392 | 4.0298 | 4.0925 | 4.1382 | 3.8698 | 32.3982 | 0.029158 |  | 62.069 | 100
19980917060000 | 1998-09-17 06:00 | 340.786 |  | 0 | 148.595 | 151.67 | 151.048 | 148.947 |  | 732.688 | 794.189 |  | 4.0886 | 4.0657 | 4.0779 | 3.6432 | 4.0208 | 4.0681 | 4.1138 | 3.8362 | 31.9143 | 0.028723 |  | 62.069 | 100
19980917063000 | 1998-09-17 06:30 | 490.679 |  | 2.513 | 149.544 | 154.784 | 151.865 | 151.814 |  | 1077.614 | 1172.617 |  | 5.8145 | 5.8748 | 6.2622 | 5.2231 | 5.6931 | 5.7114 | 5.7021 | 5.5635 | 45.8447 | 0.04126 |  | 62.069 | 100
19980917070000 | 1998-09-17 07:00 | 636.273 |  | 0.915 | 151.594 | 154.825 | 154.435 | 152.845 |  | 1378.706 | 1513.46 |  | 7.168 | 7.2646 | 7.9971 | 6.7124 | 6.9709 | 6.9832 | 6.9246 | 6.884 | 56.9048 | 0.051214 |  | 62.069 | 100
19980917073000 | 1998-09-17 07:30 | 651.582 |  | 1.778 | 150.4 | 151.463 | 153.291 | 148.245 |  | 1333.038 | 1470.959 |  | 7.2725 | 7.3379 | 8.1191 | 6.7559 | 7.0894 | 7.0542 | 6.9954 | 6.9558 | 57.5802 | 0.051822 |  | 62.069 | 100
19980917080000 | 1998-09-17 08:00 | 652.867 |  | 0.302 | 148.442 | 151.917 | 150.963 | 147.709 |  | 1327.121 | 1460.542 |  | 7.2366 | 7.2998 | 8.0796 | 6.717 | 7.0374 | 6.9985 | 6.9397 | 6.9131 | 57.2217 | 0.0515 |  | 62.069 | 100
19980917083000 | 1998-09-17 08:30 | 651.897 |  | 1.896 | 148.639 | 151.695 | 151.152 | 147.488 |  | 1326.288 | 1458.042 |  | 7.2168 | 7.293 | 8.0483 | 6.6956 | 7.0222 | 7.0054 | 6.9368 | 6.916 | 57.1341 | 0.051421 |  | 62.069 | 100
19980917090000 | 1998-09-17 09:00 | 652.421 |  | 0.175 | 148.64 | 151.84 | 151.285 | 147.632 |  | 1324.705 | 1453.375 |  | 7.2097 | 7.3013 | 8.0625 | 6.7261 | 7.0327 | 7.0161 | 6.9465 | 6.9307 | 57.2256 | 0.051503 |  | 62.069 | 100
19980917093000 | 1998-09-17 09:30 | 647.938 |  | 1.77 | 148.795 | 151.603 | 151.136 | 148.385 |  | 1321.621 | 1452.208 |  | 7.1931 | 7.2861 | 8.0283 | 6.6819 | 7.0115 | 7.0039 | 6.9282 | 6.9106 | 57.0436 | 0.051339 |  | 62.069 | 100
19980917100000 | 1998-09-17 10:00 | 652.185 |  | 0.175 | 148.711 | 151.85 | 151.102 | 147.147 |  | 1317.454 | 1446.792 |  | 7.2205 | 7.2891 | 8.061 | 6.5889 | 7.0466 | 6.9893 | 6.9282 | 6.8977 | 57.0213 | 0.051319 |  | 62.069 | 100
19980917103000 | 1998-09-17 10:30 | 647.729 |  | 1.44 | 148.431 | 152.02 | 150.876 | 147.07 |  | 1314.871 | 1442.875 |  | 7.2334 | 7.3013 | 8.0869 | 6.6101 | 7.0657 | 7.0061 | 6.9504 | 6.9106 | 57.1645 | 0.051448 |  | 62.069 | 100
19980917110000 | 1998-09-17 11:00 | 652.788 |  | 0.086 | 148.71 | 150.576 | 151.171 | 146.863 |  | 1316.454 | 1441.958 |  | 7.248 | 7.322 | 8.0825 | 6.6438 | 7.0581 | 7.0266 | 6.9604 | 6.9321 | 57.2735 | 0.051546 |  | 62.069 | 100
19980917113000 | 1998-09-17 11:30 | 656.563 |  | 1.684 | 148.495 | 151.799 | 150.692 | 147.096 |  | 1309.704 | 1442.958 |  | 7.2495 | 7.3289 | 8.0977 | 6.6414 | 7.0657 | 7.0359 | 6.9688 | 6.9397 | 57.3276 | 0.051595 |  | 62.069 | 100
19980917120000 | 1998-09-17 12:00 | 580.306 |  | 0 | 148.107 | 149.741 | 150.324 | 146.028 |  | 1163.617 | 1265.453 |  | 6.6858 | 6.7673 | 7.3708 | 4.8645 | 6.5049 | 6.4966 | 6.4399 | 6.3843 | 51.5141 | 0.046363 |  | 62.069 | 100
19980917123000 | 1998-09-17 12:30 | 581.8 |  | 1.559 | 147.828 | 151.747 | 149.947 | 147.539 |  | 1162.117 | 1263.536 |  | 6.4514 | 6.5193 | 7.0969 | 5.8618 | 6.2852 | 6.2898 | 6.2317 | 6.1577 | 50.8938 | 0.045804 |  | 62.069 | 100
19980917130000 | 1998-09-17 13:00 | 577.474 |  | 0 | 148.606 | 151.226 | 150.814 | 147.761 |  | 1162.533 | 1261.036 |  | 6.3013 | 6.3875 | 6.9185 | 6.8481 | 6.1555 | 6.1753 | 6.1287 | 6.031 | 50.9459 | 0.045851 |  | 62.069 | 100
19980917133000 | 1998-09-17 13:30 | 578.733 |  | 1.402 | 148.808 | 151.474 | 151.132 | 148.503 |  | 1164.45 | 1260.203 |  | 6.2927 | 6.3875 | 6.9063 | 6.8535 | 6.1501 | 6.1807 | 6.1416 | 6.0486 | 50.961 | 0.045865 |  | 62.069 | 100
19980917140000 | 1998-09-17 14:00 | 578.628 |  | 0 | 148.88 | 151.097 | 151.348 | 148.622 |  | 1162.033 | 1264.37 |  | 6.3293 | 6.3936 | 6.949 | 6.8496 | 6.1821 | 6.1958 | 6.1387 | 6.0493 | 51.0874 | 0.045979 |  | 62.069 | 100
19980917143000 | 1998-09-17 14:30 | 578.051 |  | 1.559 | 148.379 | 152.397 | 151.461 | 148.684 |  | 1167.867 | 1267.87 |  | 6.3408 | 6.3972 | 6.9619 | 6.8657 | 6.1821 | 6.1875 | 6.147 | 6.0571 | 51.1393 | 0.046025 |  | 62.069 | 100
19980917150000 | 1998-09-17 15:00 | 578.156 |  | 20.726 | 148.992 | 151.825 | 151.339 | 148.359 |  | 1163.867 | 1265.453 |  | 6.3333 | 6.4094 | 6.9604 | 6.8862 | 6.1836 | 6.2036 | 6.1631 | 6.0669 | 51.2065 | 0.046086 |  | 62.069 | 100
19980917153000 | 1998-09-17 15:30 | 578.444 |  | 0.084 | 148.672 | 151.19 | 151.32 | 147.724 |  | 1166.533 | 1267.536 |  | 6.3257 | 6.4216 | 6.9443 | 6.8818 | 6.167 | 6.2004 | 6.1509 | 6.0745 | 51.1662 | 0.04605 |  | 62.069 | 100
19980917160000 | 1998-09-17 16:00 | 523.342 |  | 0 | 148.724 | 150.406 | 151.054 | 146.941 |  | 1061.864 | 1154.95 |  | 5.6978 | 6.0342 | 6.1462 | 6.3875 | 5.5811 | 5.8594 | 5.5427 | 5.7122 | 46.9611 | 0.042265 |  | 62.069 | 100
19980917163000 | 1998-09-17 16:30 | 526.252 |  | 1.398 | 148.03 | 151.474 | 149.996 | 148.256 |  | 1063.447 | 1157.117 |  | 5.6938 | 6.0457 | 6.1416 | 6.3813 | 5.5688 | 5.8716 | 5.5581 | 5.7014 | 46.9623 | 0.042266 |  | 62.069 | 100
19980917170000 | 1998-09-17 17:00 | 526.75 |  | 0 | 148.662 | 151.876 | 150.944 | 148.411 |  | 1058.364 | 1151.7 |  | 5.7053 | 6.064 | 6.1509 | 6.4194 | 5.5847 | 5.8923 | 5.5732 | 5.7251 | 47.1149 | 0.042403 |  | 62.069 | 100
19980917173000 | 1998-09-17 17:30 | 531.495 |  | 19.803 | 148.858 | 151.411 | 151.171 | 147.698 |  | 1058.197 | 1153.283 |  | 5.7441 | 5.9333 | 6.1997 | 6.2898 | 5.613 | 5.7717 | 5.5872 | 5.6313 | 46.7701 | 0.042093 |  | 62.069 | 100
19980917180000 | 1998-09-17 18:00 | 575.98 |  | 0.168 | 149.301 | 152.66 | 151.946 | 149.194 |  | 1168.534 | 1274.037 |  | 6.2637 | 6.3057 | 6.8506 | 6.7185 | 6.134 | 6.1165 | 6.0693 | 5.9761 | 50.4344 | 0.045391 |  | 62.069 | 100
19980917183000 | 1998-09-17 18:30 | 574.46 |  | 1.68 | 149.112 | 152.19 | 151.613 | 147.983 |  | 1156.95 | 1261.036 |  | 6.3064 | 6.3699 | 6.936 | 6.7773 | 6.1731 | 6.1768 | 6.125 | 6.0371 | 50.9016 | 0.045811 |  | 62.069 | 100
19980917190000 | 1998-09-17 19:00 | 533.12 |  | 0 | 148.796 | 150.55 | 151.04 | 147.58 |  | 1042.363 | 1137.116 |  | 5.7588 | 5.7771 | 6.1836 | 6.0037 | 5.5969 | 5.5833 | 5.5427 | 5.4543 | 45.9004 | 0.04131 |  | 62.069 | 100
19980917193000 | 1998-09-17 19:30 | 532.229 |  | 1.434 | 147.737 | 150.369 | 150.011 | 147.152 |  | 1056.364 | 1157.033 |  | 5.8098 | 5.8662 | 6.3049 | 6.1638 | 5.6924 | 5.7144 | 5.6648 | 5.5549 | 46.7712 | 0.042094 |  | 62.069 | 100
19980917200000 | 1998-09-17 20:00 | 530.472 |  | 0 | 148.203 | 151.618 | 150.858 | 148.4 |  | 1098.115 | 1200.284 |  | 5.9412 | 5.9854 | 6.4155 | 6.3096 | 5.8044 | 5.835 | 5.7876 | 5.6733 | 47.752 | 0.042977 |  | 62.069 | 100
19980917203000 | 1998-09-17 20:30 | 571.734 |  | 2.012 | 149.846 | 152.401 | 152.399 | 148.688 |  | 1183.867 | 1290.12 |  | 6.3423 | 6.3691 | 6.9612 | 6.7834 | 6.189 | 6.1792 | 6.1196 | 6.0439 | 50.9877 | 0.045889 |  | 62.069 | 100
19980917210000 | 1998-09-17 21:00 | 571.865 |  | 0.085 | 149.061 | 150.654 | 151.636 | 147.683 |  | 1184.701 | 1286.037 |  | 6.3401 | 6.3552 | 6.9412 | 6.7734 | 6.1829 | 6.1653 | 6.1082 | 6.0349 | 50.9012 | 0.045811 |  | 62.069 | 100
19980917213000 | 1998-09-17 21:30 | 571.734 |  | 1.89 | 148.173 | 151.123 | 150.546 | 147.163 |  | 1179.617 | 1281.203 |  | 6.3301 | 6.3416 | 6.9329 | 6.7605 | 6.1731 | 6.1477 | 6.0974 | 6.022 | 50.8053 | 0.045725 |  | 62.069 | 100
19980917220000 | 1998-09-17 22:00 | 523.132 |  | 0 | 148.336 | 150.055 | 150.671 | 147.58 |  | 1088.031 | 1185.534 |  | 5.8945 | 5.9211 | 6.3979 | 6.2393 | 5.7664 | 5.7656 | 5.7236 | 5.6206 | 47.329 | 0.042596 |  | 62.069 | 100
19980917223000 | 1998-09-17 22:30 | 475.448 |  | 1.398 | 147.637 | 149.065 | 149.893 | 145.352 |  | 959.611 | 1047.447 |  | 5.3926 | 5.3779 | 5.7502 | 5.5627 | 5.2727 | 5.2979 | 5.2498 | 5.1248 | 43.0286 | 0.038726 |  | 62.069 | 100
19980917230000 | 1998-09-17 23:00 | 479.354 |  | 0 | 146.956 | 150.055 | 149.117 | 147.333 |  | 949.777 | 1034.53 |  | 5.3208 | 5.3567 | 5.6565 | 5.5024 | 5.1987 | 5.2712 | 5.2102 | 5.0667 | 42.5832 | 0.038325 |  | 62.069 | 100
19980917233000 | 1998-09-17 23:30 | 476.156 |  | 1.68 | 148.177 | 151.37 | 150.639 | 148.895 |  | 947.027 | 1037.696 |  | 5.3162 | 5.3413 | 5.6702 | 5.4985 | 5.1912 | 5.2437 | 5.1843 | 5.0544 | 42.4998 | 0.03825 |  | 62.069 | 100
19980918000000 | 1998-09-18 | 398.3 |  | 0 | 148.713 | 149.704 | 151.233 | 147.724 |  | 805.773 | 879.109 |  | 4.6143 | 4.6235 | 4.7815 | 4.5884 | 4.5227 | 4.6218 | 4.5686 | 4.3748 | 36.6956 | 0.033026 |  | 62.069 | 100
19980918003000 | 1998-09-18 00:30 | 348.938 |  | 1.802 | 147.576 | 150.772 | 149.927 | 149.039 |  | 729.021 | 794.773 |  | 4.1687 | 4.1436 | 4.2017 | 3.9109 | 4.0925 | 4.2107 | 4.1626 | 3.9017 | 32.7924 | 0.029513 |  | 62.069 | 100
19980918010000 | 1998-09-18 01:00 | 345.163 |  | 0 | 148.233 | 150.705 | 150.268 | 148.973 |  | 728.938 | 791.273 |  | 4.1497 | 4.136 | 4.165 | 3.9117 | 4.0786 | 4.2305 | 4.1687 | 3.8881 | 32.7283 | 0.029455 |  | 62.069 | 100
19980918013000 | 1998-09-18 01:30 | 340.445 |  | 1.191 | 148.781 | 150.066 | 150.971 | 149.323 |  | 723.937 | 791.939 |  | 4.1313 | 4.1252 | 4.1794 | 3.9125 | 4.0513 | 4.2114 | 4.1572 | 3.8812 | 32.6495 | 0.029385 |  | 62.069 | 100
19980918020000 | 1998-09-18 02:00 | 334.756 |  | 0 | 148.727 | 151.34 | 151.282 | 149.855 |  | 727.021 | 794.106 |  | 4.1353 | 4.1604 | 4.1672 | 3.9468 | 4.0603 | 4.2244 | 4.1794 | 3.9071 | 32.7809 | 0.029503 |  | 62.069 | 100
19980918023000 | 1998-09-18 02:30 | 335.805 |  | 1.802 | 148.898 | 151.495 | 151.444 | 149.02 |  | 727.604 | 795.356 |  | 4.075 | 4.0969 | 4.1145 | 3.8712 | 4.0107 | 4.1558 | 4.1313 | 3.8514 | 32.3068 | 0.029076 |  | 62.069 | 100
19980918030000 | 1998-09-18 03:00 | 342.175 |  | 0 | 148.783 | 151.078 | 150.957 | 149.84 |  | 720.354 | 790.023 |  | 4.0596 | 4.062 | 4.0596 | 3.8293 | 3.9705 | 4.1123 | 4.1055 | 3.8354 | 32.0342 | 0.028831 |  | 62.069 | 100
19980918033000 | 1998-09-18 03:30 | 348.257 |  | 1.926 | 148.742 | 150.088 | 151.258 | 149.345 |  | 725.271 | 796.44 |  | 4.2695 | 4.3044 | 4.3525 | 2.6002 | 4.1809 | 4.2642 | 4.2664 | 4.0229 | 32.261 | 0.029035 |  | 62.069 | 100
19980918040000 | 1998-09-18 04:00 | 336.565 |  | 0 | 148.124 | 151.351 | 151.068 | 149.371 |  | 722.187 | 789.689 |  | 4.2588 | 4.2329 | 4.2976 | 3.2129 | 4.1658 | 4.2268 | 4.2412 | 3.9597 | 32.5957 | 0.029336 |  | 62.069 | 100
19980918043000 | 1998-09-18 04:30 | 337.876 |  | 2.049 | 148.377 | 152.419 | 150.875 | 150.686 |  | 730.354 | 797.106 |  | 4.2383 | 4.2214 | 4.2947 | 3.209 | 4.1475 | 4.2031 | 4.2297 | 3.9552 | 32.4989 | 0.029249 |  | 62.069 | 100
19980918050000 | 1998-09-18 05:00 | 371.273 |  | 0 | 149.585 | 151.754 | 152.037 | 149.526 |  | 814.94 | 895.526 |  | 4.6379 | 4.6846 | 4.7844 | 3.7385 | 4.5586 | 4.6143 | 4.6616 | 4.3909 | 36.0708 | 0.032464 |  | 62.069 | 100
19980918053000 | 1998-09-18 05:30 | 479.564 |  | 22.512 | 149.68 | 152.666 | 152.036 | 150.686 |  | 984.612 | 1070.614 |  | 5.4612 | 5.5154 | 5.845 | 4.606 | 5.342 | 5.3521 | 5.3276 | 5.2131 | 42.6624 | 0.038396 |  | 62.069 | 100
19980918060000 | 1998-09-18 06:00 | 471.149 |  | 0 | 149.563 | 150.923 | 152.077 | 148.943 |  | 970.945 | 1061.114 |  | 5.5039 | 5.5129 | 5.8792 | 4.6067 | 5.3643 | 5.3818 | 5.3345 | 5.2156 | 42.7989 | 0.038519 |  | 62.069 | 100
19980918063000 | 1998-09-18 06:30 | 483.339 |  | 1.763 | 148.857 | 151.237 | 151.432 | 148.267 |  | 1022.613 | 1119.949 |  | 5.668 | 5.6863 | 6.134 | 4.7891 | 5.5664 | 5.5833 | 5.5176 | 5.407 | 44.3517 | 0.039917 |  | 62.069 | 100
19980918070000 | 1998-09-18 07:00 | 636.85 |  | 0.784 | 149.134 | 154.222 | 151.472 | 149.767 |  | 1314.454 | 1447.875 |  | 7.0977 | 7.1541 | 7.9041 | 6.3667 | 6.8994 | 6.8779 | 6.8115 | 6.7864 | 55.8978 | 0.050308 |  | 62.069 | 100
19980918073000 | 1998-09-18 07:30 | 633.494 |  | 2.134 | 150.233 | 152.01 | 152.89 | 148.297 |  | 1296.37 | 1427.708 |  | 7.0442 | 7.1016 | 7.8262 | 6.2966 | 6.8428 | 6.8176 | 6.7566 | 6.7422 | 55.4278 | 0.049885 |  | 62.069 | 100
19980918080000 | 1998-09-18 08:00 | 653.863 |  | 20.007 | 149.27 | 152.02 | 151.578 | 148.308 |  | 1305.537 | 1439.875 |  | 7.1985 | 7.2524 | 8.0283 | 6.4729 | 7.0015 | 6.9734 | 6.9063 | 6.8923 | 56.7256 | 0.051053 |  | 62.069 | 100
19980918083000 | 1998-09-18 08:30 | 651.582 |  | 2.133 | 148.982 | 151.799 | 151.585 | 148.086 |  | 1339.872 | 1477.626 |  | 7.2358 | 7.2656 | 8.0757 | 6.4812 | 7.0466 | 6.9939 | 6.9573 | 6.9077 | 56.9638 | 0.051267 |  | 62.069 | 100
19980918090000 | 1998-09-18 09:00 | 651.975 |  | 0.293 | 148.852 | 152.046 | 151.312 | 147.343 |  | 1304.537 | 1436.958 |  | 7.2266 | 7.2595 | 8.0679 | 6.4712 | 7.0222 | 6.9856 | 6.9375 | 6.9009 | 56.8714 | 0.051184 |  | 62.069 | 100
19980918093000 | 1998-09-18 09:30 | 650.403 |  | 1.433 | 148.858 | 152.309 | 150.905 | 146.863 |  | 1304.621 | 1435.041 |  | 7.1541 | 7.1838 | 7.9644 | 7.679 | 6.968 | 6.907 | 6.8733 | 6.8245 | 57.5541 | 0.051799 |  | 62.069 | 100
19980918100000 | 1998-09-18 10:00 | 652.5 |  | 0.17 | 148.762 | 151.241 | 150.809 | 147.776 |  | 1317.621 | 1456.208 |  | 7.1045 | 7.1418 | 7.9216 | 7.644 | 6.9177 | 6.884 | 6.8201 | 6.7964 | 57.2301 | 0.051507 |  | 62.069 | 100
19980918103000 | 1998-09-18 10:30 | 651.241 |  | 2.01 | 148.641 | 151.736 | 151.248 | 147.776 |  | 1304.037 | 1438.375 |  | 7.0535 | 7.0901 | 7.8423 | 7.5752 | 6.875 | 6.8406 | 6.7756 | 6.739 | 56.7913 | 0.051112 |  | 62.069 | 100
19980918110000 | 1998-09-18 11:00 | 651.425 |  | 0.167 | 148.464 | 151.88 | 151.299 | 147.673 |  | 1302.037 | 1430.624 |  | 7.0808 | 7.1252 | 7.8721 | 7.624 | 6.9001 | 6.8733 | 6.8108 | 6.7781 | 57.0644 | 0.051358 |  | 62.069 | 100
19980918113000 | 1998-09-18 11:30 | 652.631 |  | 2.008 | 148.796 | 152.205 | 151.38 | 147.75 |  | 1303.954 | 1437.125 |  | 7.0991 | 7.1206 | 7.8904 | 7.6143 | 6.9063 | 6.8635 | 6.7964 | 6.7673 | 57.0579 | 0.051352 |  | 62.069 | 100
19980918120000 | 1998-09-18 12:00 | 652.578 |  | 0.292 | 148.859 | 152.113 | 151.165 | 147.658 |  | 1302.371 | 1427.874 |  | 7.0962 | 7.1213 | 7.9019 | 7.6143 | 6.9207 | 6.8628 | 6.7993 | 6.7673 | 57.0838 | 0.051375 |  | 62.069 | 100
19980918123000 | 1998-09-18 12:30 | 649.511 |  | 1.52 | 148.909 | 151.334 | 151.28 | 147.868 |  | 1300.454 | 1429.624 |  | 7.0801 | 7.1174 | 7.8882 | 7.6096 | 6.8977 | 6.8643 | 6.8032 | 6.7712 | 57.0317 | 0.051329 |  | 62.069 | 100
19980918130000 | 1998-09-18 13:00 | 651.399 |  | 0.168 | 148.641 | 152.061 | 150.889 | 147.853 |  | 1303.037 | 1428.708 |  | 7.071 | 7.1113 | 7.866 | 7.5996 | 6.8879 | 6.8604 | 6.7993 | 6.759 | 56.9545 | 0.051259 |  | 62.069 | 100
19980918133000 | 1998-09-18 13:30 | 655.855 |  | 1.642 | 148.719 | 151.88 | 150.902 | 146.93 |  | 1304.954 | 1432.875 |  | 7.0679 | 7.0962 | 7.8682 | 7.592 | 6.884 | 6.8542 | 6.791 | 6.7551 | 56.9086 | 0.051218 |  | 62.069 | 100
19980918140000 | 1998-09-18 14:00 | 652.919 |  | 0.292 | 148.856 | 151.36 | 151.086 | 146.904 |  | 1297.287 | 1426.041 |  | 7.074 | 7.0825 | 7.8667 | 7.5906 | 6.884 | 6.8445 | 6.7742 | 6.7415 | 56.858 | 0.051172 |  | 62.069 | 100
19980918143000 | 1998-09-18 14:30 | 583.451 |  | 1.553 | 148.132 | 148.936 | 150.47 | 145.718 |  | 1170.867 | 1273.536 |  | 6.4675 | 6.4966 | 7.1365 | 6.8384 | 6.3218 | 6.3081 | 6.2539 | 6.1929 | 52.0157 | 0.046814 |  | 62.069 | 100
19980918150000 | 1998-09-18 15:00 | 513.931 |  | 0 | 147.783 | 149.013 | 149.915 | 146.538 |  | 988.862 | 1080.698 |  | 5.6184 | 5.5818 | 5.9883 | 5.6313 | 5.4734 | 5.459 | 5.4055 | 5.2896 | 44.4473 | 0.040003 |  | 62.069 | 100
19980918153000 | 1998-09-18 15:30 | 482.631 |  | 1.31 | 147.169 | 149.926 | 149.371 | 146.956 |  | 946.027 | 1041.03 |  | 5.3628 | 5.3604 | 5.719 | 5.3438 | 5.2566 | 5.2942 | 5.2278 | 5.0857 | 42.6503 | 0.038385 |  | 62.069 | 100
19980918160000 | 1998-09-18 16:00 | 479.669 |  | 0 | 148.006 | 151.149 | 150.362 | 148.426 |  | 949.944 | 1040.197 |  | 5.397 | 5.3909 | 5.7571 | 5.4009 | 5.2856 | 5.3254 | 5.2659 | 5.1101 | 42.9329 | 0.03864 |  | 62.069 | 100
19980918163000 | 1998-09-18 16:30 | 479.931 |  | 1.925 | 148.618 | 151.293 | 151.232 | 148.818 |  | 959.111 | 1051.03 |  | 5.3384 | 5.3535 | 5.6938 | 5.3628 | 5.2444 | 5.2864 | 5.2246 | 5.0735 | 42.5774 | 0.03832 |  | 62.069 | 100
19980918170000 | 1998-09-18 17:00 | 478.987 |  | 0 | 148.648 | 150.942 | 151.329 | 148.962 |  | 947.944 | 1036.946 |  | 5.3101 | 5.333 | 5.6611 | 5.3376 | 5.2117 | 5.2651 | 5.2087 | 5.0537 | 42.381 | 0.038143 |  | 62.069 | 100
19980918173000 | 1998-09-18 17:30 | 479.564 |  | 1.802 | 148.641 | 151.112 | 151.17 | 149.379 |  | 946.861 | 1038.363 |  | 5.3384 | 5.3657 | 5.6978 | 5.3887 | 5.2285 | 5.2856 | 5.2178 | 5.0767 | 42.5992 | 0.038339 |  | 62.069 | 100
19980918180000 | 1998-09-18 18:00 | 542.741 |  | 0.168 | 148.743 | 152.664 | 151.323 | 149.446 |  | 1076.698 | 1179.451 |  | 5.9868 | 6.0112 | 6.5261 | 6.2332 | 5.8572 | 5.8723 | 5.8076 | 5.697 | 47.9914 | 0.043192 |  | 62.069 | 100
19980918183000 | 1998-09-18 18:30 | 544.366 |  | 1.399 | 149.697 | 151.685 | 152.238 | 148.219 |  | 1091.115 | 1192.368 |  | 6.0098 | 6.0327 | 6.5591 | 6.2813 | 5.8923 | 5.8877 | 5.8274 | 5.7161 | 48.2064 | 0.043386 |  | 62.069 | 100
19980918190000 | 1998-09-18 19:00 | 593.518 |  | 0.168 | 150.169 | 152.298 | 152.71 | 149.575 |  | 1223.535 | 1332.455 |  | 6.5293 | 6.5522 | 7.2168 | 6.9124 | 6.3806 | 6.3545 | 6.2874 | 6.2241 | 52.4573 | 0.047212 |  | 62.069 | 100
19980918193000 | 1998-09-18 19:30 | 590.791 |  | 2.256 | 149.074 | 151.592 | 151.747 | 148.374 |  | 1225.785 | 1342.039 |  | 6.8672 | 6.8643 | 7.605 | 7.3418 | 6.678 | 4.5837 | 6.5796 | 6.5469 | 53.0665 | 0.04776 |  | 62.069 | 100
19980918200000 | 1998-09-18 20:00 | 596.087 |  | 20.84 | 148.369 | 151.009 | 150.967 | 146.553 |  | 1209.618 | 1319.121 |  | 6.5881 | 6.5842 | 7.2402 | 6.9321 | 6.4058 | 6.3325 | 6.302 | 6.2524 | 52.6373 | 0.047374 |  | 62.069 | 100
19980918203000 | 1998-09-18 20:30 | 452.301 |  | 0.204 | 147.966 | 149.431 | 150.02 | 146.956 |  | 903.776 | 989.445 |  | 5.1506 | 5.166 | 5.5215 | 5.1284 | 5.0576 | 5.0317 | 5.0186 | 4.8997 | 40.9741 | 0.036877 |  | 62.069 | 100
19980918210000 | 1998-09-18 21:00 | 329.671 |  | 0 | 146.053 | 147.688 | 148.132 | 145.46 |  | 635.018 | 693.103 |  | 0.0024 | 0.0078 | 4.9629 | 4.6089 | 4.7439 | 4.821 | 4.8049 | 4.5364 | 28.4882 | 0.025639 |  | 62.069 | 100
19980918213000 | 1998-09-18 21:30 | 294.937 |  | 1.557 | 145.922 | 148.899 | 147.999 | 147.414 |  | 586.85 | 641.268 |  | 0.0024 | 0.0093 | 4.5723 | 4.1985 | 4.3992 | 4.4763 | 4.467 | 4.2419 | 26.3669 | 0.02373 |  | 62.069 | 100
19980918220000 | 1998-09-18 22:00 | 258.001 |  | 0 | 146.998 | 149.771 | 149.331 | 149.028 |  | 535.099 | 585.6 |  | 0.004 | 0.0093 | 4.1938 | 3.785 | 4.126 | 4.2419 | 1.5161 | 3.9346 | 21.8107 | 0.01963 |  | 62.069 | 100
19980918223000 | 1998-09-18 22:30 | 237.79 |  | 20.045 | 147.37 | 148.09 | 149.44 | 147.595 |  | 549.182 | 591.35 |  | 0.0032 | 0.0085 | 4.6677 | 2.8833 | 4.4404 | 4.5945 | 1.5955 | 4.2893 | 22.4824 | 0.020234 |  | 62.069 | 100
19980918230000 | 1998-09-18 23:00 | 241.329 |  | 0 | 147.203 | 151.071 | 149.33 | 149.586 |  | 531.849 | 574.85 |  | 0.0032 | 0.0093 | 4.8372 | 3.0267 | 4.6387 | 4.6853 | 1.5756 | 4.4792 | 23.2552 | 0.02093 |  | 62.069 | 100
19980918233000 | 1998-09-18 23:30 | 236.663 |  | 2.047 | 148.589 | 151.123 | 150.979 | 150.133 |  | 527.015 | 567.683 |  | 0.0055 | 0.0093 | 4.9111 | 3.0542 | 4.6494 | 4.7166 | 1.5802 | 4.5029 | 23.4292 | 0.021086 |  | 62.069 | 100
19980919000000 | 1998-09-19 | 235.876 |  | 0 | 148.592 | 150.38 | 150.944 | 150.38 |  | 535.515 | 575.35 |  | 0.0032 | 0.0078 | 4.9316 | 3.0526 | 4.6387 | 4.7058 | 1.5794 | 4.4731 | 23.3922 | 0.021053 |  | 62.069 | 100
19980919003000 | 1998-09-19 00:30 | 237.344 |  | 1.433 | 148.427 | 150.159 | 150.851 | 150.406 |  | 538.349 | 582.517 |  | 0.0032 | 0.0085 | 4.9424 | 3.0656 | 4.6646 | 4.7288 | 1.587 | 4.5266 | 23.5267 | 0.021174 |  | 62.069 | 100
19980919010000 | 1998-09-19 01:00 | 232.966 |  | 0 | 148.645 | 150.055 | 151.088 | 150.55 |  | 527.515 | 582.433 |  | 0.0032 | 0.0078 | 4.9294 | 3.0573 | 4.6807 | 4.728 | 1.5794 | 4.5098 | 23.4956 | 0.021146 |  | 62.069 | 100
19980919013000 | 1998-09-19 01:30 | 238.052 |  | 1.923 | 148.645 | 150.251 | 151.117 | 150.499 |  | 531.765 | 589.017 |  | 0.0047 | 0.0078 | 4.9226 | 3.0862 | 4.6807 | 4.7317 | 1.5863 | 4.5327 | 23.5527 | 0.021197 |  | 62.069 | 100
19980919020000 | 1998-09-19 02:00 | 236.872 |  | 0 | 148.798 | 149.9 | 151.303 | 151.138 |  | 533.849 | 587.434 |  | 0.0017 | 0.0085 | 4.9417 | 3.0808 | 4.696 | 4.7317 | 1.5977 | 4.5525 | 23.6106 | 0.02125 |  | 62.069 | 100
19980919023000 | 1998-09-19 02:30 | 237.921 |  | 1.802 | 148.861 | 150.813 | 151.376 | 151.308 |  | 531.099 | 581.183 |  | 0.0032 | 0.007 | 4.8853 | 3.0472 | 4.6609 | 4.686 | 1.5794 | 4.499 | 23.368 | 0.021031 |  | 62.069 | 100
19980919030000 | 1998-09-19 03:00 | 234.644 |  | 0 | 148.772 | 150.436 | 151.039 | 149.198 |  | 526.432 | 578.517 |  | 0.0047 | 0.0078 | 4.9683 | 3.1038 | 4.7083 | 4.7607 | 1.5992 | 4.5586 | 23.7114 | 0.02134 |  | 62.069 | 100
19980919033000 | 1998-09-19 03:30 | 238.629 |  | 1.434 | 148.583 | 150.137 | 151.074 | 150.137 |  | 525.765 | 580.517 |  | 0.0024 | 0.0085 | 4.9158 | 3.0549 | 4.667 | 4.7241 | 1.584 | 4.5281 | 23.4848 | 0.021136 |  | 62.069 | 100
19980919040000 | 1998-09-19 04:00 | 239.52 |  | 0 | 148.956 | 150.632 | 151.344 | 151.127 |  | 527.348 | 581.433 |  | 0.0047 | 0.0085 | 4.9331 | 3.0831 | 4.6838 | 4.7241 | 1.5955 | 4.5181 | 23.5509 | 0.021196 |  | 62.069 | 100
19980919043000 | 1998-09-19 04:30 | 234.277 |  | 2.172 | 148.577 | 150.318 | 151.396 | 150.565 |  | 526.515 | 582.35 |  | 0.0047 | 0.007 | 5.0063 | 3.1418 | 4.7341 | 4.7798 | 1.6122 | 4.583 | 23.8689 | 0.021482 |  | 62.069 | 100
19980919050000 | 1998-09-19 05:00 | 234.723 |  | 0 | 148.497 | 150.901 | 150.882 | 151.149 |  | 523.348 | 578.433 |  | 0.0047 | 0.0085 | 4.9758 | 3.1045 | 4.7126 | 4.7722 | 1.6023 | 4.5776 | 23.7582 | 0.021382 |  | 62.069 | 100
19980919053000 | 1998-09-19 05:30 | 239.258 |  | 2.051 | 148.932 | 150.329 | 151.35 | 150.824 |  | 532.849 | 586.767 |  | 0.0032 | 0.0078 | 5.0256 | 3.1266 | 4.7327 | 4.8135 | 1.6107 | 4.6067 | 23.9268 | 0.021534 |  | 62.069 | 100
19980919060000 | 1998-09-19 06:00 | 237.37 |  | 0 | 148.519 | 149.859 | 150.9 | 150.354 |  | 536.182 | 589.35 |  | 0.0032 | 0.0093 | 4.9973 | 3.1167 | 4.7219 | 4.7974 | 1.6053 | 4.5891 | 23.8402 | 0.021456 |  | 62.069 | 100
19980919063000 | 1998-09-19 06:30 | 238.865 |  | 1.559 | 148.912 | 150.628 | 151.058 | 151.123 |  | 526.515 | 580.35 |  | 0.0032 | 0.0085 | 4.988 | 3.1266 | 4.7456 | 4.7891 | 1.6122 | 4.5784 | 23.8516 | 0.021466 |  | 62.069 | 100
19980919070000 | 1998-09-19 07:00 | 239.232 |  | 0 | 148.628 | 150.38 | 151.349 | 149.885 |  | 531.682 | 584.267 |  | 0.0024 | 0.0085 | 4.8982 | 3.0747 | 4.657 | 4.7212 | 1.5802 | 4.519 | 23.4612 | 0.021115 |  | 62.069 | 100
19980919073000 | 1998-09-19 07:30 | 239.048 |  | 1.683 | 148.735 | 150.55 | 150.746 | 149.313 |  | 511.348 | 615.268 |  | 0.004 | 0.007 | 4.8904 | 3.0603 | 4.6494 | 4.7356 | 1.5802 | 4.519 | 23.4459 | 0.021101 |  | 62.069 | 100
19980919080000 | 1998-09-19 08:00 | 237.344 |  | 0 | 148.744 | 150.927 | 150.888 | 150.679 |  | 514.765 | 608.767 |  | 0.0032 | 0.0078 | 4.9417 | 3.0991 | 4.6838 | 4.741 | 1.6016 | 4.5417 | 23.6199 | 0.021258 |  | 62.069 | 100
19980919083000 | 1998-09-19 08:30 | 236.925 |  | 2.295 | 148.936 | 149.926 | 151.238 | 150.916 |  | 508.181 | 601.267 |  | 0.004 | 0.0078 | 4.9309 | 3.0786 | 4.6951 | 4.7424 | 1.5909 | 4.5403 | 23.59 | 0.021231 |  | 62.069 | 100
19980919090000 | 1998-09-19 09:00 | 233.858 |  | 0 | 148.654 | 149.782 | 151.442 | 150.029 |  | 514.181 | 595.6 |  | 0.004 | 0.007 | 5.0171 | 3.1335 | 4.7607 | 4.8164 | 1.6099 | 4.6157 | 23.9643 | 0.021568 |  | 62.069 | 100
19980919093000 | 1998-09-19 09:30 | 233.622 |  | 2.504 | 148.495 | 150.591 | 151.129 | 150.839 |  | 507.598 | 593.434 |  | 0.0032 | 0.0078 | 5.0278 | 3.1495 | 4.75 | 4.812 | 1.6099 | 4.6096 | 23.9698 | 0.021573 |  | 62.069 | 100
19980919100000 | 1998-09-19 10:00 | 238.917 |  | 0.416 | 148.54 | 150.473 | 151.331 | 150.72 |  | 514.265 | 597.017 |  | 0.0024 | 0.0085 | 5.0042 | 3.1388 | 4.7363 | 4.7876 | 1.5985 | 4.5913 | 23.8676 | 0.021481 |  | 62.069 | 100
19980919103000 | 1998-09-19 10:30 | 239.494 |  | 1.524 | 148.579 | 150.916 | 151.334 | 150.669 |  | 514.515 | 591.35 |  | 0.004 | 0.0101 | 4.927 | 3.0854 | 4.6838 | 4.7439 | 1.587 | 4.5403 | 23.5815 | 0.021223 |  | 62.069 | 100
19980919110000 | 1998-09-19 11:00 | 235.797 |  | 0.085 | 148.858 | 150.344 | 151.13 | 150.344 |  | 516.848 | 588.184 |  | 0.0047 | 0.0078 | 4.9409 | 3.0786 | 4.699 | 4.7654 | 1.5833 | 4.564 | 23.6437 | 0.021279 |  | 62.069 | 100
19980919113000 | 1998-09-19 11:30 | 235.43 |  | 1.275 | 149.014 | 150.395 | 150.891 | 150.395 |  | 515.181 | 590.767 |  | 0.0032 | 0.0078 | 4.9858 | 3.1296 | 4.7249 | 4.7937 | 1.5992 | 4.5837 | 23.8279 | 0.021445 |  | 62.069 | 100
19980919120000 | 1998-09-19 12:00 | 237.921 |  | 0.088 | 148.375 | 150.395 | 150.891 | 150.89 |  | 516.848 | 591.017 |  | 0.004 | 0.0078 | 4.9417 | 3.1075 | 4.689 | 4.7554 | 1.5992 | 4.5586 | 23.6632 | 0.021297 |  | 62.069 | 100
19980919123000 | 1998-09-19 12:30 | 236.191 |  | 1.888 | 148.781 | 150.669 | 151.081 | 151.164 |  | 519.015 | 593.767 |  | 0.0032 | 0.0078 | 4.9392 | 3.119 | 4.7021 | 4.7791 | 1.5779 | 4.5754 | 23.7037 | 0.021333 |  | 62.069 | 100
19980919130000 | 1998-09-19 13:00 | 241.093 |  | 19.809 | 148.38 | 150.081 | 150.924 | 150.081 |  | 521.682 | 590.767 |  | 0.004 | 0.0078 | 4.9561 | 3.1068 | 4.6975 | 4.7578 | 1.5909 | 4.5601 | 23.681 | 0.021313 |  | 62.069 | 100
19980919133000 | 1998-09-19 13:30 | 235.378 |  | 1.804 | 148.47 | 150.499 | 150.908 | 150.499 |  | 520.432 | 591.684 |  | 0.004 | 0.0078 | 4.9377 | 3.1052 | 4.6777 | 4.741 | 1.5909 | 4.5435 | 23.6078 | 0.021247 |  | 62.069 | 100
19980919140000 | 1998-09-19 14:00 | 237.475 |  | 0 | 148.82 | 149.56 | 151.24 | 150.55 |  | 516.848 | 587.85 |  | 0.004 | 0.007 | 4.9072 | 3.0969 | 4.6616 | 4.7363 | 1.5863 | 4.5342 | 23.5335 | 0.02118 |  | 62.069 | 100
19980919143000 | 1998-09-19 14:30 | 237.659 |  | 1.805 | 148.639 | 150.979 | 151.409 | 150.484 |  | 516.431 | 587.684 |  | 0.0047 | 0.0078 | 4.9614 | 3.1061 | 4.6868 | 4.7485 | 1.5916 | 4.5593 | 23.6662 | 0.0213 |  | 62.069 | 100
19980919150000 | 1998-09-19 15:00 | 239.336 |  | 0 | 148.517 | 151.149 | 150.889 | 150.159 |  | 515.515 | 585.933 |  | 0.0032 | 0.0078 | 4.9309 | 3.0786 | 4.6875 | 4.7388 | 1.5939 | 4.5486 | 23.5893 | 0.02123 |  | 62.069 | 100
19980919153000 | 1998-09-19 15:30 | 238.235 |  | 2.625 | 148.849 | 151.004 | 151.082 | 150.757 |  | 522.515 | 594.35 |  | 0.0032 | 0.007 | 4.9126 | 3.0648 | 4.6541 | 4.7083 | 1.5916 | 4.519 | 23.4606 | 0.021115 |  | 62.069 | 100
19980919160000 | 1998-09-19 16:00 | 234.749 |  | 0 | 149.077 | 150.509 | 151.569 | 150.757 |  | 518.932 | 591.267 |  | 0.004 | 0.0078 | 4.8904 | 3.0618 | 4.6479 | 4.7205 | 1.5794 | 4.5098 | 23.4216 | 0.021079 |  | 62.069 | 100
19980919163000 | 1998-09-19 16:30 | 236.217 |  | 2.38 | 148.48 | 150.092 | 151.118 | 149.349 |  | 520.432 | 596.267 |  | 0.0032 | 0.0078 | 4.8713 | 3.0634 | 4.634 | 4.7083 | 1.5695 | 4.509 | 23.3665 | 0.02103 |  | 62.069 | 100
19980919170000 | 1998-09-19 17:00 | 235.299 |  | 0 | 148.581 | 150.809 | 150.723 | 150.809 |  | 522.182 | 598.767 |  | 0.0024 | 0.007 | 4.9141 | 3.0892 | 4.6685 | 4.7424 | 1.587 | 4.5486 | 23.5592 | 0.021203 |  | 62.069 | 100
19980919173000 | 1998-09-19 17:30 | 236.112 |  | 1.643 | 148.706 | 150.834 | 151.178 | 151.33 |  | 517.265 | 589.6 |  | 0.0047 | 0.007 | 4.8508 | 3.0389 | 4.6304 | 4.6943 | 1.5687 | 4.4824 | 23.2772 | 0.020949 |  | 62.069 | 100
19980919180000 | 1998-09-19 18:00 | 235.483 |  | 0 | 148.78 | 150.494 | 151.246 | 150.247 |  | 520.348 | 595.767 |  | 0.0032 | 0.0078 | 4.9043 | 3.0679 | 4.6631 | 4.7195 | 1.5863 | 4.5227 | 23.4748 | 0.021127 |  | 62.069 | 100
19980919183000 | 1998-09-19 18:30 | 231.813 |  | 2.135 | 148.785 | 150.886 | 150.851 | 149.896 |  | 524.182 | 599.434 |  | 0.0024 | 0.0085 | 4.9417 | 3.1052 | 4.6838 | 4.7654 | 1.5992 | 4.5403 | 23.6465 | 0.021282 |  | 62.069 | 100
19980919190000 | 1998-09-19 19:00 | 236.164 |  | 0 | 148.668 | 150.494 | 151.005 | 151.485 |  | 507.515 | 585.35 |  | 0.004 | 0.0078 | 4.9531 | 3.0679 | 4.6882 | 4.7432 | 1.587 | 4.5417 | 23.5929 | 0.021234 |  | 62.069 | 100
19980919193000 | 1998-09-19 19:30 | 235.247 |  | 2.17 | 148.408 | 150.964 | 151.387 | 149.726 |  | 516.682 | 596.934 |  | 0.0047 | 0.0085 | 4.8975 | 3.0725 | 4.6494 | 4.7151 | 1.5825 | 4.5059 | 23.4361 | 0.021092 |  | 62.069 | 100
19980919200000 | 1998-09-19 20:00 | 239.284 |  | 0.087 | 148.687 | 151.134 | 150.967 | 151.629 |  | 515.431 | 595.6 |  | 0.0032 | 0.0078 | 4.9004 | 3.0465 | 4.6494 | 4.7021 | 1.5863 | 4.509 | 23.4047 | 0.021064 |  | 62.069 | 100
19980919203000 | 1998-09-19 20:30 | 234.723 |  | 1.52 | 149.015 | 150.391 | 151.361 | 150.391 |  | 515.015 | 591.1 |  | 0.0047 | 0.0085 | 4.918 | 3.0488 | 4.6455 | 4.7083 | 1.5931 | 4.5105 | 23.4374 | 0.021094 |  | 62.069 | 100
19980919210000 | 1998-09-19 21:00 | 239.73 |  | 0 | 148.379 | 150.964 | 150.777 | 150.221 |  | 520.182 | 594.684 |  | 0.0032 | 0.0085 | 4.9836 | 3.0702 | 4.7134 | 4.7622 | 1.6008 | 4.5662 | 23.7081 | 0.021337 |  | 62.069 | 100
19980919213000 | 1998-09-19 21:30 | 233.569 |  | 1.926 | 148.783 | 150.365 | 151.159 | 150.613 |  | 516.515 | 590.6 |  | 0.0024 | 0.0078 | 4.9097 | 3.0573 | 4.6577 | 4.7126 | 1.5794 | 4.509 | 23.4359 | 0.021092 |  | 62.069 | 100
19980919220000 | 1998-09-19 22:00 | 237.632 |  | 0 | 148.858 | 150.69 | 151.125 | 150.195 |  | 513.015 | 589.85 |  | 0.0032 | 0.0078 | 4.8699 | 3.0198 | 4.635 | 4.699 | 1.5687 | 4.4824 | 23.2858 | 0.020957 |  | 62.069 | 100
19980919223000 | 1998-09-19 22:30 | 235.64 |  | 1.647 | 148.477 | 149.896 | 150.758 | 150.144 |  | 516.765 | 594.184 |  | 0.004 | 0.0078 | 4.95 | 3.0862 | 4.6807 | 4.7532 | 1.5947 | 4.5403 | 23.6169 | 0.021255 |  | 62.069 | 100
19980919230000 | 1998-09-19 23:00 | 235.43 |  | 0 | 148.777 | 151.355 | 151.309 | 149.623 |  | 518.348 | 596.684 |  | 0.0032 | 0.0085 | 4.9355 | 3.0977 | 4.6921 | 4.7639 | 1.6023 | 4.5601 | 23.6633 | 0.021297 |  | 62.069 | 100
19980919233000 | 1998-09-19 23:30 | 238.052 |  | 2.17 | 149.199 | 150.118 | 151.341 | 150.86 |  | 515.098 | 595.267 |  | 0.004 | 0.0078 | 4.9331 | 3.0686 | 4.6838 | 4.7424 | 1.5909 | 4.519 | 23.5496 | 0.021195 |  | 62.069 | 100
19980920000000 | 1998-09-20 | 239.861 |  | 0 | 148.708 | 150.118 | 151.144 | 150.613 |  | 515.431 | 585.85 |  | 0.0047 | 0.0078 | 4.8738 | 3.0237 | 4.634 | 4.6853 | 1.5634 | 4.4763 | 23.269 | 0.020942 |  | 62.069 | 100
19980920003000 | 1998-09-20 00:30 | 235.64 |  | 2.048 | 148.665 | 150.066 | 151.326 | 150.066 |  | 517.348 | 595.017 |  | 0.0032 | 0.0078 | 4.9119 | 3.0625 | 4.657 | 4.7195 | 1.5955 | 4.5266 | 23.484 | 0.021136 |  | 62.069 | 100
19980920010000 | 1998-09-20 01:00 | 234.434 |  | 0 | 148.741 | 150.964 | 151.324 | 150.964 |  | 514.181 | 586.934 |  | 0.004 | 0.0078 | 4.9463 | 3.1113 | 4.7083 | 4.7722 | 1.5947 | 4.5679 | 23.7125 | 0.021341 |  | 62.069 | 100
19980920013000 | 1998-09-20 01:30 | 232.966 |  | 2.01 | 148.44 | 149.648 | 151.002 | 149.401 |  | 520.682 | 597.017 |  | 0.0032 | 0.0085 | 5.0171 | 3.1541 | 4.7524 | 4.8005 | 1.6099 | 4.6121 | 23.9578 | 0.021562 |  | 62.069 | 100
19980920020000 | 1998-09-20 02:00 | 231.158 |  | 0 | 148.756 | 150.834 | 150.998 | 150.834 |  | 517.848 | 597.767 |  | 0.0032 | 0.0078 | 4.9133 | 3.0892 | 4.6838 | 4.7371 | 1.587 | 4.5557 | 23.5771 | 0.021219 |  | 62.069 | 100
19980920023000 | 1998-09-20 02:30 | 236.794 |  | 2.503 | 148.442 | 151.459 | 151.068 | 150.964 |  | 513.931 | 586.767 |  | 0.0032 | 0.0085 | 4.9104 | 3.0511 | 4.6609 | 4.7249 | 1.5909 | 4.5044 | 23.4543 | 0.021109 |  | 62.069 | 100
19980920030000 | 1998-09-20 03:00 | 236.925 |  | 0 | 148.787 | 150.587 | 151.322 | 150.092 |  | 519.848 | 604.934 |  | 0.004 | 0.0093 | 4.8896 | 3.0503 | 4.6724 | 4.7195 | 1.5825 | 4.5037 | 23.4313 | 0.021088 |  | 62.069 | 100
19980920033000 | 1998-09-20 03:30 | 236.82 |  | 20.741 | 148.843 | 151.03 | 151.021 | 150.535 |  | 518.348 | 598.017 |  | 0.0032 | 0.0078 | 4.96 | 3.1 | 4.7134 | 4.7661 | 1.6023 | 4.574 | 23.7268 | 0.021354 |  | 62.069 | 100
19980920040000 | 1998-09-20 04:00 | 231.446 |  | 0 | 148.765 | 150.953 | 150.867 | 150.458 |  | 516.515 | 589.517 |  | 0.0032 | 0.0093 | 4.9873 | 3.1488 | 4.7295 | 4.7891 | 1.6016 | 4.6045 | 23.8733 | 0.021486 |  | 62.069 | 100
19980920043000 | 1998-09-20 04:30 | 240.149 |  | 2.136 | 148.86 | 150.834 | 151.196 | 151.33 |  | 515.515 | 592.35 |  | 0.0024 | 0.0078 | 4.9385 | 3.0679 | 4.6768 | 4.7166 | 1.5955 | 4.5151 | 23.5206 | 0.021169 |  | 62.069 | 100
19980920050000 | 1998-09-20 05:00 | 232.966 |  | 0.088 | 148.767 | 149.545 | 151.449 | 150.04 |  | 512.098 | 591.934 |  | 0.0032 | 0.0085 | 4.9287 | 3.1113 | 4.6814 | 4.7632 | 1.5909 | 4.5669 | 23.6541 | 0.021289 |  | 62.069 | 100
19980920053000 | 1998-09-20 05:30 | 237.265 |  | 2.542 | 148.395 | 150.705 | 150.835 | 150.705 |  | 517.182 | 588.6 |  | 0.0032 | 0.0085 | 4.9087 | 3.0817 | 4.6768 | 4.7302 | 1.5909 | 4.5381 | 23.5381 | 0.021184 |  | 62.069 | 100
19980920060000 | 1998-09-20 06:00 | 232.311 |  | 0 | 148.567 | 151.448 | 150.882 | 150.953 |  | 513.348 | 589.434 |  | 0.0032 | 0.0085 | 4.9355 | 3.1 | 4.6921 | 4.7668 | 1.5947 | 4.5647 | 23.6655 | 0.021299 |  | 62.069 | 100
19980920063000 | 1998-09-20 06:30 | 232.704 |  | 2.048 | 149.106 | 149.545 | 151.29 | 151.03 |  | 516.098 | 595.017 |  | 0.004 | 0.0078 | 4.9561 | 3.1068 | 4.7058 | 4.7754 | 1.5992 | 4.5945 | 23.7496 | 0.021375 |  | 62.069 | 100
19980920070000 | 1998-09-20 07:00 | 232.023 |  | 0 | 148.576 | 150.731 | 151.321 | 149.989 |  | 515.015 | 594.267 |  | 0.004 | 0.0085 | 4.9568 | 3.1235 | 4.7073 | 4.7561 | 1.5992 | 4.5662 | 23.7216 | 0.021349 |  | 62.069 | 100
19980920073000 | 1998-09-20 07:30 | 234.723 |  | 1.889 | 148.768 | 151.149 | 150.79 | 150.654 |  | 515.931 | 586.85 |  | 0.004 | 0.0093 | 4.8623 | 3.0664 | 4.634 | 4.6943 | 1.568 | 4.5059 | 23.3442 | 0.02101 |  | 62.069 | 100
19980920080000 | 1998-09-20 08:00 | 236.243 |  | 0 | 148.748 | 149.468 | 151.239 | 150.953 |  | 527.098 | 598.267 |  | 0.0032 | 0.0085 | 4.9585 | 3.0916 | 4.7112 | 4.7693 | 1.6077 | 4.5662 | 23.7162 | 0.021345 |  | 62.069 | 100
19980920083000 | 1998-09-20 08:30 | 239.363 |  | 2.75 | 148.66 | 150.133 | 151.167 | 150.628 |  | 527.348 | 602.017 |  | 0.0047 | 0.0078 | 4.9133 | 3.0862 | 4.6501 | 4.7288 | 1.5909 | 4.5403 | 23.5221 | 0.02117 |  | 62.069 | 100
19980920090000 | 1998-09-20 09:00 | 239.179 |  | 0 | 148.502 | 150.277 | 151.261 | 151.267 |  | 518.682 | 595.35 |  | 0.0032 | 0.0085 | 4.9004 | 3.0542 | 4.6609 | 4.7104 | 1.587 | 4.5151 | 23.4397 | 0.021096 |  | 62.069 | 100
19980920093000 | 1998-09-20 09:30 | 236.427 |  | 2.381 | 148.697 | 150.994 | 151.298 | 150.994 |  | 513.515 | 590.85 |  | 0.0032 | 0.0078 | 4.9331 | 3.0869 | 4.6768 | 4.7395 | 1.5947 | 4.5442 | 23.5862 | 0.021228 |  | 62.069 | 100
19980920100000 | 1998-09-20 10:00 | 238.917 |  | 0 | 148.859 | 151.37 | 150.895 | 150.875 |  | 517.598 | 596.517 |  | 0.0032 | 0.0078 | 4.928 | 3.0496 | 4.657 | 4.7119 | 1.5909 | 4.5364 | 23.4848 | 0.021136 |  | 62.069 | 100
19980920103000 | 1998-09-20 10:30 | 236.453 |  | 1.769 | 148.778 | 151.097 | 151.035 | 151.097 |  | 515.431 | 593.434 |  | 0.0032 | 0.0078 | 4.9065 | 3.0939 | 4.6724 | 4.7485 | 1.6016 | 4.5586 | 23.5925 | 0.021233 |  | 62.069 | 100
19980920110000 | 1998-09-20 11:00 | 236.4 |  | 0 | 148.858 | 150.694 | 151.336 | 150.694 |  | 513.098 | 593.85 |  | 0.0032 | 0.0078 | 4.9141 | 3.0778 | 4.6731 | 4.7449 | 1.5931 | 4.5518 | 23.5658 | 0.021209 |  | 62.069 | 100
19980920113000 | 1998-09-20 11:30 | 238.393 |  | 2.661 | 148.858 | 150.994 | 151.362 | 150.746 |  | 509.515 | 592.767 |  | 0.0032 | 0.0078 | 4.8645 | 3.0122 | 4.6211 | 4.6655 | 1.5641 | 4.4717 | 23.2101 | 0.020889 |  | 62.069 | 100
19980920120000 | 1998-09-20 12:00 | 237.056 |  | 0 | 148.753 | 150.277 | 150.902 | 150.277 |  | 512.348 | 591.767 |  | 0.0032 | 0.0085 | 4.9385 | 3.0824 | 4.6777 | 4.7349 | 1.5909 | 4.5364 | 23.5725 | 0.021215 |  | 62.069 | 100
19980920123000 | 1998-09-20 12:30 | 238.838 |  | 1.926 | 148.408 | 150.524 | 151.019 | 150.772 |  | 510.598 | 587.684 |  | 0.0032 | 0.0085 | 4.9309 | 3.0824 | 4.6785 | 4.7158 | 1.5909 | 4.5356 | 23.5458 | 0.021191 |  | 62.069 | 100
19980920130000 | 1998-09-20 13:00 | 239.127 |  | 0 | 148.318 | 150.576 | 151.171 | 150.576 |  | 519.015 | 596.85 |  | 0.0032 | 0.007 | 4.927 | 3.0862 | 4.6731 | 4.7241 | 1.5886 | 4.5417 | 23.5509 | 0.021196 |  | 62.069 | 100
19980920133000 | 1998-09-20 13:30 | 235.483 |  | 1.889 | 149.118 | 150.499 | 151.122 | 151.489 |  | 520.682 | 594.434 |  | 0.0024 | 0.0078 | 4.9539 | 3.1106 | 4.7029 | 4.7471 | 1.5878 | 4.5388 | 23.6513 | 0.021286 |  | 62.069 | 100
19980920140000 | 1998-09-20 14:00 | 238.209 |  | 0 | 148.656 | 150.602 | 151.272 | 150.602 |  | 518.182 | 593.767 |  | 0.004 | 0.007 | 4.9158 | 3.0695 | 4.6724 | 4.7378 | 1.5992 | 4.5403 | 23.546 | 0.021191 |  | 62.069 | 100
19980920143000 | 1998-09-20 14:30 | 237.449 |  | 2.625 | 148.883 | 150.824 | 151.108 | 150.329 |  | 517.598 | 593.017 |  | 0.0032 | 0.0078 | 4.9011 | 3.0625 | 4.6631 | 4.7073 | 1.5764 | 4.5151 | 23.4365 | 0.021093 |  | 62.069 | 100
19980920150000 | 1998-09-20 15:00 | 239.467 |  | 0 | 148.469 | 150.38 | 151.108 | 150.38 |  | 517.682 | 596.684 |  | 0.0024 | 0.0085 | 4.9355 | 3.0671 | 4.6829 | 4.7151 | 1.5779 | 4.532 | 23.5214 | 0.021169 |  | 62.069 | 100
19980920153000 | 1998-09-20 15:30 | 234.12 |  | 2.17 | 148.852 | 150.184 | 151.02 | 150.432 |  | 513.598 | 592.684 |  | 0.0032 | 0.0085 | 4.792 | 3.0214 | 4.5837 | 4.6655 | 1.5611 | 4.4778 | 23.1132 | 0.020802 |  | 62.069 | 100
19980920160000 | 1998-09-20 16:00 | 231.105 |  | 0 | 148.46 | 150.901 | 150.876 | 149.664 |  | 520.848 | 595.6 |  | 0.0032 | 0.0078 | 4.8774 | 3.0634 | 4.6455 | 4.7195 | 1.5748 | 4.5181 | 23.4097 | 0.021069 |  | 62.069 | 100
19980920163000 | 1998-09-20 16:30 | 231.603 |  | 1.765 | 148.57 | 150.927 | 150.833 | 151.67 |  | 512.431 | 587.184 |  | 0.0032 | 0.0078 | 4.8706 | 3.0397 | 4.6304 | 4.6792 | 1.568 | 4.4778 | 23.2767 | 0.020949 |  | 62.069 | 100
19980920170000 | 1998-09-20 17:00 | 232.888 |  | 2.171 | 148.696 | 151.03 | 151.464 | 150.04 |  | 512.015 | 578.767 |  | 0.0032 | 0.0078 | 4.9829 | 3.1221 | 4.7119 | 4.7654 | 1.6053 | 4.573 | 23.7716 | 0.021394 |  | 62.069 | 100
19980920173000 | 1998-09-20 17:30 | 235.457 |  | 22.649 | 148.43 | 150.979 | 150.828 | 150.484 |  | 515.681 | 596.434 |  | 0.0032 | 0.0078 | 4.905 | 3.0435 | 4.6724 | 4.7144 | 1.5878 | 4.519 | 23.4531 | 0.021108 |  | 62.069 | 100
19980920180000 | 1998-09-20 18:00 | 236.191 |  | 20.53 | 148.617 | 151.278 | 151.253 | 151.278 |  | 507.765 | 588.434 |  | 0.0032 | 0.007 | 4.8806 | 3.0411 | 4.6365 | 4.6975 | 1.5825 | 4.4839 | 23.3323 | 0.020999 |  | 62.069 | 100
19980920183000 | 1998-09-20 18:30 | 232.835 |  | 2.131 | 149.08 | 150.757 | 151.239 | 150.014 |  | 506.015 | 585.6 |  | 0.004 | 0.0078 | 4.8853 | 3.0411 | 4.635 | 4.696 | 1.5833 | 4.519 | 23.3715 | 0.021034 |  | 62.069 | 100
19980920190000 | 1998-09-20 19:00 | 231.708 |  | 0 | 148.486 | 150.912 | 150.92 | 151.655 |  | 507.015 | 590.267 |  | 0.0047 | 0.007 | 4.9341 | 3.0786 | 4.6982 | 4.741 | 1.5955 | 4.5403 | 23.5994 | 0.021239 |  | 62.069 | 100
19980920193000 | 1998-09-20 19:30 | 234.696 |  | 1.644 | 148.344 | 151.134 | 151.138 | 151.381 |  | 501.098 | 594.6 |  | 0.0032 | 0.0078 | 4.9233 | 3.0679 | 4.686 | 4.7119 | 1.5756 | 4.4961 | 23.4718 | 0.021125 |  | 62.069 | 100
19980920200000 | 1998-09-20 20:00 | 233.124 |  | 0 | 148.859 | 149.283 | 151.19 | 149.778 |  | 501.848 | 582.35 |  | 0.0032 | 0.0078 | 4.9036 | 3.0686 | 4.6838 | 4.696 | 1.5947 | 4.5227 | 23.4804 | 0.021132 |  | 62.069 | 100
19980920203000 | 1998-09-20 20:30 | 234.932 |  | 1.645 | 148.333 | 151.108 | 150.738 | 149.623 |  | 505.598 | 585.683 |  | 0.0024 | 0.0085 | 4.8904 | 3.032 | 4.6462 | 4.699 | 1.5672 | 4.5037 | 23.3494 | 0.021014 |  | 62.069 | 100
19980920210000 | 1998-09-20 21:00 | 230.633 |  | 0 | 148.823 | 151.459 | 150.91 | 151.211 |  | 507.765 | 587.767 |  | 0.004 | 0.0085 | 4.9348 | 3.0878 | 4.6838 | 4.7371 | 1.5909 | 4.5417 | 23.5886 | 0.02123 |  | 62.069 | 100
19980920213000 | 1998-09-20 21:30 | 232.285 |  | 1.924 | 148.688 | 150.86 | 151.405 | 151.355 |  | 505.765 | 596.767 |  | 0.0032 | 0.0078 | 4.9514 | 3.116 | 4.696 | 4.7471 | 1.6023 | 4.5532 | 23.677 | 0.021309 |  | 62.069 | 100
19980920220000 | 1998-09-20 22:00 | 234.723 |  | 0 | 149.124 | 150.339 | 151.422 | 151.082 |  | 507.681 | 592.6 |  | 0.004 | 0.0078 | 4.8516 | 3.0374 | 4.6228 | 4.6753 | 1.5718 | 4.4861 | 23.2568 | 0.020931 |  | 62.069 | 100
19980920223000 | 1998-09-20 22:30 | 234.906 |  | 2.138 | 148.54 | 150.314 | 151.264 | 150.066 |  | 513.515 | 590.767 |  | 0.0032 | 0.0078 | 4.9043 | 3.0671 | 4.6616 | 4.6968 | 1.5764 | 4.5144 | 23.4316 | 0.021088 |  | 62.069 | 100
19980920230000 | 1998-09-20 23:00 | 236.479 |  | 0 | 148.671 | 151.355 | 150.867 | 151.108 |  | 510.598 | 591.017 |  | 0.0032 | 0.0078 | 4.8828 | 3.0374 | 4.6418 | 4.7012 | 1.5718 | 4.4954 | 23.3414 | 0.021007 |  | 62.069 | 100
19980920233000 | 1998-09-20 23:30 | 233.255 |  | 1.891 | 148.858 | 150.912 | 151.317 | 150.664 |  | 510.015 | 594.85 |  | 0.0032 | 0.0078 | 4.9072 | 3.0892 | 4.6616 | 4.7205 | 1.5863 | 4.5327 | 23.5085 | 0.021158 |  | 62.069 | 100
19980921000000 | 1998-09-21 | 235.221 |  | 0 | 148.935 | 150.953 | 150.902 | 150.458 |  | 503.931 | 586.517 |  | 0.0032 | 0.007 | 4.8774 | 3.0496 | 4.6448 | 4.7012 | 1.5695 | 4.4998 | 23.3525 | 0.021017 |  | 62.069 | 100
19980921003000 | 1998-09-21 00:30 | 235.876 |  | 1.644 | 148.707 | 150.21 | 150.891 | 150.705 |  | 508.431 | 592.6 |  | 0.0032 | 0.0085 | 4.8706 | 3.0427 | 4.6401 | 4.6907 | 1.5718 | 4.4961 | 23.3237 | 0.020991 |  | 62.069 | 100
19980921010000 | 1998-09-21 01:00 | 229.349 |  | 0 | 148.749 | 149.338 | 151.091 | 151.071 |  | 506.598 | 588.767 |  | 0.0032 | 0.0078 | 4.8882 | 3.0839 | 4.6426 | 4.709 | 1.587 | 4.5068 | 23.4285 | 0.021086 |  | 62.069 | 100
19980921013000 | 1998-09-21 01:30 | 232.966 |  | 2.504 | 148.385 | 151.097 | 151.395 | 150.354 |  | 510.598 | 594.6 |  | 0.0032 | 0.0078 | 4.9294 | 3.0778 | 4.6807 | 4.7288 | 1.5878 | 4.5288 | 23.5443 | 0.02119 |  | 62.069 | 100
19980921020000 | 1998-09-21 02:00 | 232.521 |  | 0 | 148.828 | 150.994 | 151.289 | 150.746 |  | 502.764 | 587.684 |  | 0.0047 | 0.007 | 4.8882 | 3.0465 | 4.6501 | 4.7058 | 1.5764 | 4.5044 | 23.3831 | 0.021045 |  | 62.069 | 100
19980921023000 | 1998-09-21 02:30 | 237.03 |  | 2.384 | 148.483 | 150.055 | 150.911 | 150.798 |  | 508.348 | 592.6 |  | 0.0032 | 0.007 | 4.886 | 3.0695 | 4.6455 | 4.699 | 1.5756 | 4.5068 | 23.3926 | 0.021053 |  | 62.069 | 100
19980921030000 | 1998-09-21 03:00 | 232.809 |  | 0 | 148.735 | 151.19 | 151.054 | 150.447 |  | 513.015 | 590.934 |  | 0.0047 | 0.007 | 4.9514 | 3.0808 | 4.6943 | 4.7388 | 1.5909 | 4.5449 | 23.6128 | 0.021252 |  | 62.069 | 100
19980921033000 | 1998-09-21 03:30 | 234.461 |  | 1.767 | 148.684 | 150.395 | 151.429 | 151.633 |  | 503.014 | 586.767 |  | 0.004 | 0.007 | 4.8799 | 3.0488 | 4.6462 | 4.6929 | 1.5756 | 4.5029 | 23.3573 | 0.021022 |  | 62.069 | 100
19980921040000 | 1998-09-21 04:00 | 234.88 |  | 0 | 148.404 | 151.215 | 150.947 | 150.72 |  | 508.598 | 588.6 |  | 0.0032 | 0.0078 | 4.9011 | 3.074 | 4.6462 | 4.7083 | 1.5809 | 4.5129 | 23.4344 | 0.021091 |  | 62.069 | 100
19980921043000 | 1998-09-21 04:30 | 234.198 |  | 2.628 | 148.781 | 150.122 | 150.9 | 149.379 |  | 507.515 | 589.017 |  | 0.0032 | 0.0101 | 4.9172 | 3.074 | 4.667 | 4.7317 | 1.5977 | 4.5381 | 23.539 | 0.021185 |  | 62.069 | 100
19980921050000 | 1998-09-21 05:00 | 231.918 |  | 0 | 148.395 | 151.06 | 150.727 | 150.813 |  | 513.515 | 594.017 |  | 0.0024 | 0.0085 | 4.9233 | 3.0686 | 4.667 | 4.7188 | 1.5863 | 4.519 | 23.4939 | 0.021145 |  | 62.069 | 100
19980921053000 | 1998-09-21 05:30 | 247.043 |  | 2.012 | 149.19 | 149.797 | 151.672 | 150.787 |  | 562.683 | 645.185 |  | 0.0032 | 0.0078 | 5.4727 | 3.4723 | 5.0935 | 5.1399 | 1.7435 | 4.9614 | 25.8943 | 0.023305 |  | 62.069 | 100
19980921060000 | 1998-09-21 06:00 | 334.625 |  | 0.909 | 149.454 | 154.758 | 152.051 | 153.521 |  | 729.438 | 824.024 |  | 0.004 | 0.0078 | 6.3721 | 4.0413 | 5.7412 | 5.6741 | 5.5505 | 5.5962 | 32.9872 | 0.029688 |  | 62.069 | 100
19980921063000 | 1998-09-21 06:30 | 335.569 |  | 2.257 | 150.991 | 152.242 | 153.856 | 151.5 |  | 710.104 | 786.023 |  | 0.004 | 0.0085 | 6.1965 | 3.9484 | 5.6306 | 5.6145 | 5.5696 | 5.5208 | 32.4929 | 0.029244 |  | 62.069 | 100
19980921070000 | 1998-09-21 07:00 | 487.061 |  | 2.133 | 150.251 | 153.846 | 152.887 | 151.618 |  | 1083.114 | 1190.534 |  | 6.0967 | 4.033 | 6.6125 | 5.3079 | 5.9182 | 5.9067 | 5.8228 | 5.8174 | 45.5152 | 0.040964 |  | 62.069 | 100
19980921073000 | 1998-09-21 07:30 | 628.356 |  | 5.077 | 151.852 | 155.785 | 154.86 | 152.32 |  | 1432.791 | 1575.045 |  | 7.48 | 4.9873 | 8.2627 | 6.7139 | 7.1602 | 7.1221 | 6.9885 | 7.093 | 55.8077 | 0.050227 |  | 62.069 | 100
19980921080000 | 1998-09-21 08:00 | 633.809 |  | 21.051 | 151.155 | 154.392 | 153.783 | 149.194 |  | 1302.704 | 1434.875 |  | 7.2007 | 7.1404 | 7.9385 | 6.4102 | 6.9092 | 6.8276 | 6.7512 | 6.8108 | 55.9886 | 0.05039 |  | 62.069 | 100
19980921083000 | 1998-09-21 08:30 | 637.479 |  | 20.616 | 150.133 | 153.805 | 151.752 | 148.112 |  | 1289.537 | 1415.541 |  | 7.2427 | 7.1526 | 7.969 | 6.4202 | 6.9397 | 6.8542 | 6.7781 | 6.823 | 56.1795 | 0.050562 |  | 62.069 | 100
19980921090000 | 1998-09-21 09:00 | 583.897 |  | 0.169 | 148.38 | 150.144 | 150.331 | 145.936 |  | 1176.117 | 1285.537 |  | 6.6414 | 6.53 | 7.2273 | 5.7588 | 6.3674 | 6.2769 | 6.208 | 6.2393 | 51.2491 | 0.046124 |  | 62.069 | 100
19980921093000 | 1998-09-21 09:30 | 576.531 |  | 1.763 | 147.618 | 151.5 | 149.933 | 147.292 |  | 1209.701 | 1318.954 |  | 6.8191 | 6.7307 | 7.4243 | 5.9707 | 6.5376 | 6.4895 | 6.4155 | 6.4248 | 52.8122 | 0.047531 |  | 62.069 | 100
19980921100000 | 1998-09-21 10:00 | 645.605 |  | 0.66 | 149.61 | 152.763 | 151.977 | 149.298 |  | 1246.952 | 1534.877 |  | 7.2183 | 7.0938 | 7.9521 | 7.6477 | 6.9238 | 6.833 | 6.7612 | 6.7979 | 57.2278 | 0.051505 |  | 62.069 | 100
19980921103000 | 1998-09-21 10:30 | 653.81 |  | 2.045 | 148.405 | 151.422 | 150.723 | 147.214 |  | 1286.037 | 1407.957 |  | 7.1863 | 7.0901 | 7.9126 | 7.6096 | 6.8948 | 6.8086 | 6.7407 | 6.7756 | 57.0183 | 0.051316 |  | 62.069 | 100
19980921110000 | 1998-09-21 11:00 | 650.272 |  | 0.288 | 148.26 | 151.36 | 150.704 | 147.152 |  | 1291.62 | 1416.457 |  | 7.1741 | 7.0657 | 7.8987 | 7.592 | 6.8811 | 6.8086 | 6.7275 | 6.772 | 56.9197 | 0.051228 |  | 62.069 | 100
19980921113000 | 1998-09-21 11:30 | 651.975 |  | 1.8 | 148.714 | 151.788 | 151.08 | 147.085 |  | 1280.87 | 1409.624 |  | 7.1716 | 7.0642 | 7.8933 | 7.5859 | 6.884 | 6.7971 | 6.7261 | 6.7537 | 56.8759 | 0.051188 |  | 62.069 | 100
19980921120000 | 1998-09-21 12:00 | 653.575 |  | 0.166 | 148.475 | 151.149 | 150.872 | 147.683 |  | 1284.037 | 1408.624 |  | 7.1541 | 7.0564 | 7.876 | 7.5867 | 6.8726 | 6.7939 | 6.7246 | 6.7505 | 56.8148 | 0.051133 |  | 62.069 | 100
19980921123000 | 1998-09-21 12:30 | 651.346 |  | 1.519 | 148.713 | 152.076 | 151.084 | 148.116 |  | 1280.953 | 1403.29 |  | 7.1541 | 7.0657 | 7.8682 | 7.5562 | 6.8711 | 6.7871 | 6.7092 | 6.7429 | 56.7545 | 0.051079 |  | 62.069 | 100
19980921130000 | 1998-09-21 13:00 | 651.844 |  | 0.29 | 148.965 | 151.855 | 151.345 | 147.894 |  | 1293.037 | 1422.791 |  | 7.1519 | 7.0747 | 7.8865 | 7.5874 | 6.8801 | 6.8025 | 6.7346 | 6.7559 | 56.8736 | 0.051186 |  | 62.069 | 100
19980921133000 | 1998-09-21 13:30 | 649.931 |  | 1.887 | 148.854 | 151.618 | 151.671 | 147.658 |  | 1292.037 | 1417.291 |  | 7.1802 | 7.0947 | 7.8972 | 7.6064 | 6.8916 | 6.8108 | 6.7375 | 6.7703 | 56.9887 | 0.05129 |  | 62.069 | 100
19980921140000 | 1998-09-21 14:00 | 654.544 |  | 0.292 | 148.657 | 152.324 | 151.249 | 147.868 |  | 1298.287 | 1424.708 |  | 7.1809 | 7.093 | 7.917 | 7.6021 | 6.9031 | 6.814 | 6.7505 | 6.7749 | 57.0355 | 0.051332 |  | 62.069 | 100
19980921143000 | 1998-09-21 14:30 | 653.575 |  | 1.76 | 148.973 | 151.02 | 151.188 | 148.049 |  | 1298.537 | 1429.124 |  | 7.1938 | 7.0815 | 7.9148 | 7.6104 | 6.9001 | 6.8101 | 6.7444 | 6.7695 | 57.0246 | 0.051322 |  | 62.069 | 100
19980921150000 | 1998-09-21 15:00 | 650.901 |  | 0.166 | 148.578 | 152.072 | 150.898 | 147.369 |  | 1295.204 | 1422.458 |  | 7.1938 | 7.0916 | 7.9109 | 7.6111 | 6.9023 | 6.814 | 6.7476 | 6.7817 | 57.053 | 0.051348 |  | 62.069 | 100
19980921153000 | 1998-09-21 15:30 | 652.893 |  | 1.641 | 148.409 | 151.215 | 150.929 | 147.008 |  | 1293.87 | 1420.957 |  | 7.1863 | 7.1008 | 7.9116 | 7.6287 | 6.9031 | 6.8298 | 6.7573 | 6.7993 | 57.1169 | 0.051405 |  | 62.069 | 100
19980921160000 | 1998-09-21 16:00 | 618.919 |  | 0.088 | 148.26 | 150.735 | 150.939 | 146.033 |  | 1188.367 | 1302.621 |  | 6.7415 | 6.636 | 7.3464 | 7.0266 | 6.4758 | 6.376 | 6.3203 | 6.3516 | 53.2742 | 0.047947 |  | 62.069 | 100
19980921163000 | 1998-09-21 16:30 | 572.73 |  | 1.762 | 147.681 | 150.499 | 149.755 | 147.033 |  | 1131.366 | 1238.869 |  | 6.3667 | 6.3013 | 6.8948 | 6.5889 | 6.1233 | 6.0867 | 6.0334 | 6.0212 | 50.4163 | 0.045375 |  | 62.069 | 100
19980921170000 | 1998-09-21 17:00 | 576.74 |  | 0 | 147.896 | 151.943 | 150.135 | 148.478 |  | 1122.365 | 1233.119 |  | 6.3745 | 6.2905 | 6.8848 | 6.5889 | 6.1104 | 6.1013 | 6.0396 | 6.0112 | 50.4012 | 0.045361 |  | 62.069 | 100
19980921173000 | 1998-09-21 17:30 | 651.32 |  | 2.131 | 148.82 | 154.341 | 151.286 | 150.628 |  | 1301.204 | 1430.208 |  | 7.1863 | 7.1267 | 7.9048 | 7.6531 | 6.9038 | 6.8894 | 6.8115 | 6.8169 | 57.2925 | 0.051563 |  | 62.069 | 100
19980921180000 | 1998-09-21 18:00 | 651.582 |  | 0.167 | 150.064 | 152.376 | 152.746 | 147.92 |  | 1290.62 | 1419.041 |  | 7.1755 | 7.0977 | 7.8821 | 7.6218 | 6.8833 | 6.8313 | 6.7666 | 6.7825 | 57.0408 | 0.051337 |  | 62.069 | 100
19980921183000 | 1998-09-21 18:30 | 652.526 |  | 1.272 | 148.954 | 151.947 | 151.444 | 147.244 |  | 1293.954 | 1421.208 |  | 7.1572 | 7.0947 | 7.8728 | 7.6218 | 6.8657 | 6.8284 | 6.7529 | 6.7773 | 56.9708 | 0.051274 |  | 62.069 | 100
19980921190000 | 1998-09-21 19:00 | 626.521 |  | 0.204 | 148.632 | 151.215 | 151.281 | 147.008 |  | 1216.535 | 1334.788 |  | 6.7939 | 6.7375 | 7.4014 | 7.1465 | 6.5125 | 6.4141 | 6.3674 | 6.3943 | 53.7676 | 0.048391 |  | 62.069 | 100
19980921193000 | 1998-09-21 19:30 | 610.4 |  | 1.764 | 148.22 | 152.386 | 150.193 | 147.683 |  | 1199.618 | 1318.538 |  | 6.7361 | 6.6277 | 7.345 | 7.0237 | 6.4568 | 6.376 | 6.311 | 6.3264 | 53.2027 | 0.047882 |  | 62.069 | 100
19980921200000 | 1998-09-21 20:00 | 579.047 |  | 0.059 | 148.267 | 150.266 | 150.359 | 147.296 |  | 1144.783 | 1259.62 |  | 6.4346 | 6.3423 | 6.958 | 6.6736 | 6.1646 | 6.1394 | 6.0815 | 6.0762 | 50.8702 | 0.045783 |  | 62.069 | 100
19980921203000 | 1998-09-21 20:30 | 577.107 |  | 1.765 | 148.45 | 151.7 | 150.748 | 147.987 |  | 1148.366 | 1260.036 |  | 6.427 | 6.3462 | 6.9336 | 6.6597 | 6.1599 | 6.1365 | 6.0737 | 6.0532 | 50.7898 | 0.045711 |  | 62.069 | 100
19980921210000 | 1998-09-21 21:00 | 506.25 |  | 0 | 148.704 | 150.55 | 151.027 | 147.828 |  | 960.528 | 1046.613 |  | 5.5618 | 5.3918 | 5.7764 | 5.4397 | 5.2932 | 5.2239 | 5.1826 | 5.146 | 43.0154 | 0.038714 |  | 62.069 | 100
19980921213000 | 1998-09-21 21:30 | 380.658 |  | 1.434 | 146.715 | 148.116 | 149.016 | 145.888 |  | 785.106 | 836.774 |  | 4.5815 | 4.4458 | 4.5693 | 4.2495 | 4.3794 | 4.4753 | 4.4167 | 4.2222 | 35.3397 | 0.031806 |  | 62.069 | 100
19980921220000 | 1998-09-21 22:00 | 388.994 |  | 0 | 147.072 | 150.096 | 149.346 | 148.858 |  | 785.273 | 839.441 |  | 4.5701 | 4.4297 | 4.5784 | 4.2527 | 4.377 | 4.48 | 4.4189 | 4.2183 | 35.3251 | 0.031793 |  | 62.069 | 100
19980921223000 | 1998-09-21 22:30 | 379.111 |  | 22.527 | 148.096 | 151.736 | 150.647 | 149.756 |  | 802.44 | 864.858 |  | 4.6455 | 4.5547 | 4.6685 | 4.4404 | 4.4663 | 4.5999 | 4.5417 | 4.3342 | 36.2512 | 0.032626 |  | 62.069 | 100
19980921230000 | 1998-09-21 23:00 | 380.081 |  | 20.657 | 148.422 | 150.643 | 151.055 | 148.663 |  | 749.021 | 796.69 |  | 4.3992 | 4.2268 | 4.3245 | 3.9827 | 4.1809 | 4.2297 | 4.1841 | 4.0039 | 33.5318 | 0.030179 |  | 62.069 | 100
19980921233000 | 1998-09-21 23:30 | 345.111 |  | 1.801 | 148.2 | 149.926 | 150.727 | 148.193 |  | 685.77 | 723.854 |  | 4.0491 | 3.8712 | 3.9445 | 2.9573 | 3.8698 | 3.9545 | 3.9102 | 3.7087 | 30.2653 | 0.027239 |  | 62.069 | 100
19980922000000 | 1998-09-22 | 342.28 |  | 0 | 148.496 | 150.524 | 150.891 | 148.792 |  | 713.604 | 745.188 |  | 4.1885 | 4.0269 | 4.0886 | 3.7362 | 3.9963 | 4.0857 | 4.0657 | 3.8293 | 32.0172 | 0.028815 |  | 62.069 | 100
19980922003000 | 1998-09-22 00:30 | 329.356 |  | 1.432 | 148.445 | 151.149 | 150.987 | 149.664 |  | 727.521 | 763.189 |  | 4.1978 | 4.071 | 4.1184 | 3.7653 | 4.0193 | 4.1047 | 4.0969 | 3.8599 | 32.2333 | 0.02901 |  | 62.069 | 100
19980922010000 | 1998-09-22 01:00 | 328.806 |  | 0 | 149.434 | 151.175 | 151.934 | 150.432 |  | 730.188 | 788.689 |  | 4.2244 | 4.0649 | 4.1206 | 3.7599 | 4.0254 | 4.0886 | 4.1055 | 3.8682 | 32.2575 | 0.029032 |  | 62.069 | 100
19980922013000 | 1998-09-22 01:30 | 337.247 |  | 1.802 | 148.952 | 152.02 | 151.452 | 148.308 |  | 733.438 | 795.606 |  | 4.2366 | 4.0818 | 4.1345 | 3.8071 | 4.0481 | 4.0581 | 4.113 | 3.8728 | 32.352 | 0.029117 |  | 62.069 | 100
19980922020000 | 1998-09-22 02:00 | 343.04 |  | 0 | 148.799 | 150.118 | 150.876 | 147.643 |  | 726.938 | 790.106 |  | 4.2336 | 4.0742 | 4.1335 | 3.7805 | 4.0269 | 4.0491 | 4.0969 | 3.8698 | 32.2645 | 0.029038 |  | 62.069 | 100
19980922023000 | 1998-09-22 02:30 | 339.868 |  | 1.923 | 148.247 | 151.655 | 150.552 | 148.932 |  | 739.021 | 802.356 |  | 4.2581 | 4.1069 | 4.168 | 3.8507 | 4.0718 | 4.0779 | 4.1353 | 3.9094 | 32.5781 | 0.02932 |  | 62.069 | 100
19980922030000 | 1998-09-22 03:00 | 343.355 |  | 0 | 148.523 | 148.71 | 150.858 | 147.72 |  | 708.187 | 769.605 |  | 4.3198 | 4.1755 | 4.2603 | 3.9506 | 4.1389 | 4.1726 | 4.2046 | 2.7322 | 31.9545 | 0.028759 |  | 62.069 | 100
19980922033000 | 1998-09-22 03:30 | 342.385 |  | 1.52 | 147.962 | 151.108 | 150.207 | 150.118 |  | 716.187 | 781.606 |  | 4.3992 | 4.2717 | 4.3823 | 4.0115 | 4.2222 | 4.2153 | 4.2664 | 2.6544 | 32.423 | 0.029181 |  | 62.069 | 100
19980922040000 | 1998-09-22 04:00 | 342.254 |  | 0 | 148.642 | 150.639 | 151.041 | 148.658 |  | 721.687 | 785.189 |  | 4.2312 | 4.1101 | 4.1335 | 3.801 | 4.0398 | 4.0796 | 4.1206 | 3.8796 | 32.3954 | 0.029156 |  | 62.069 | 100
19980922043000 | 1998-09-22 04:30 | 344.115 |  | 1.802 | 148.706 | 151.278 | 151.117 | 149.05 |  | 715.354 | 778.522 |  | 4.2024 | 4.0552 | 4.0771 | 3.7935 | 4.0139 | 4.0535 | 4.103 | 3.8674 | 32.166 | 0.028949 |  | 62.069 | 100
19980922050000 | 1998-09-22 05:00 | 344.534 |  | 0 | 148.861 | 150.901 | 151.335 | 149.664 |  | 715.937 | 780.439 |  | 4.2397 | 4.0979 | 4.1375 | 3.8217 | 4.0369 | 4.0642 | 4.1162 | 3.8804 | 32.3945 | 0.029155 |  | 62.069 | 100
19980922053000 | 1998-09-22 05:30 | 343.328 |  | 1.924 | 148.815 | 149.56 | 151.285 | 148.57 |  | 714.354 | 774.606 |  | 4.2122 | 4.0825 | 4.1177 | 3.8263 | 4.0291 | 4.0818 | 4.1199 | 3.8812 | 32.3507 | 0.029116 |  | 62.069 | 100
19980922060000 | 1998-09-22 06:00 | 342.07 |  | 0 | 148.433 | 150.746 | 150.798 | 149.756 |  | 713.854 | 776.272 |  | 4.2275 | 4.0918 | 4.145 | 3.8193 | 4.0359 | 4.0635 | 4.1206 | 3.8857 | 32.3893 | 0.02915 |  | 62.069 | 100
19980922063000 | 1998-09-22 06:30 | 361.783 |  | 2.048 | 148.714 | 150.968 | 151.124 | 149.73 |  | 754.688 | 822.19 |  | 4.4731 | 4.3472 | 4.4458 | 4.2268 | 4.2832 | 4.342 | 4.3977 | 4.1497 | 34.6655 | 0.031199 |  | 62.069 | 100
19980922070000 | 1998-09-22 07:00 | 510.392 |  | 0.293 | 149.569 | 154.108 | 152.234 | 151.385 |  | 1057.364 | 1162.117 |  | 5.9739 | 5.8762 | 6.3318 | 6.1304 | 5.7366 | 5.7031 | 5.6748 | 5.5854 | 47.0122 | 0.042311 |  | 62.069 | 100
19980922073000 | 1998-09-22 07:30 | 648.41 |  | 2.628 | 151.753 | 154.655 | 154.451 | 152.18 |  | 1332.788 | 1469.375 |  | 7.3005 | 7.1052 | 8.0205 | 7.6187 | 6.9971 | 6.8201 | 6.8679 | 6.7397 | 57.4697 | 0.051723 |  | 62.069 | 100
19980922080000 | 1998-09-22 08:00 | 651.477 |  | 0.416 | 149.964 | 151.659 | 152.886 | 147.451 |  | 1292.954 | 1422.874 |  | 7.2922 | 7.0459 | 8.0283 | 7.5654 | 7.0022 | 6.7573 | 6.8513 | 6.6841 | 57.2267 | 0.051504 |  | 62.069 | 100
19980922083000 | 1998-09-22 08:30 | 655.567 |  | 1.766 | 148.627 | 152.18 | 151.141 | 147.477 |  | 1300.621 | 1430.958 |  | 7.283 | 7.0535 | 8.0459 | 7.5723 | 7.0093 | 6.772 | 6.8665 | 6.6948 | 57.2973 | 0.051568 |  | 62.069 | 100
19980922090000 | 1998-09-22 09:00 | 652.867 |  | 0.533 | 148.859 | 151.736 | 151.11 | 147.528 |  | 1302.371 | 1432.208 |  | 7.2563 | 7.0466 | 7.9941 | 7.5576 | 6.9961 | 6.7756 | 6.8513 | 6.6919 | 57.1695 | 0.051453 |  | 62.069 | 100
19980922093000 | 1998-09-22 09:30 | 654.282 |  | 1.885 | 148.966 | 152.139 | 151.109 | 147.931 |  | 1301.621 | 1428.958 |  | 7.2258 | 7.0847 | 7.9727 | 7.634 | 6.929 | 6.8284 | 6.781 | 6.7415 | 57.1971 | 0.051477 |  | 62.069 | 100
19980922100000 | 1998-09-22 10:00 | 657.585 |  | 0.167 | 148.432 | 151.097 | 150.881 | 147.137 |  | 1290.787 | 1422.124 |  | 7.1548 | 7.0869 | 7.8682 | 7.6028 | 6.8665 | 6.8269 | 6.7092 | 6.7307 | 56.846 | 0.051161 |  | 62.069 | 100
19980922103000 | 1998-09-22 10:30 | 653.391 |  | 1.515 | 148.508 | 151.566 | 150.87 | 147.606 |  | 1290.62 | 1417.791 |  | 7.1663 | 7.0786 | 7.8538 | 7.6028 | 6.8611 | 6.8169 | 6.6995 | 6.7163 | 56.7953 | 0.051116 |  | 62.069 | 100
19980922110000 | 1998-09-22 11:00 | 654.466 |  | 0.166 | 148.684 | 151.721 | 151.259 | 148.256 |  | 1289.537 | 1414.374 |  | 7.1899 | 7.103 | 7.8972 | 7.6179 | 6.8811 | 6.8345 | 6.7163 | 6.73 | 56.9699 | 0.051273 |  | 62.069 | 100
19980922113000 | 1998-09-22 11:30 | 656.406 |  | 1.515 | 148.875 | 151.906 | 151.416 | 147.946 |  | 1289.204 | 1417.624 |  | 7.1946 | 7.106 | 7.9041 | 7.6257 | 6.907 | 6.8452 | 6.7224 | 6.7346 | 57.0396 | 0.051336 |  | 62.069 | 100
19980922120000 | 1998-09-22 12:00 | 654.204 |  | 0.166 | 148.861 | 151.37 | 151.171 | 147.905 |  | 1290.787 | 1419.957 |  | 7.1741 | 7.0894 | 7.8911 | 7.6211 | 6.8855 | 6.833 | 6.7124 | 6.7285 | 56.9351 | 0.051242 |  | 62.069 | 100
19980922123000 | 1998-09-22 12:30 | 657.585 |  | 1.762 | 148.523 | 151.747 | 151.005 | 147.787 |  | 1291.12 | 1414.791 |  | 7.1565 | 7.074 | 7.8552 | 7.5845 | 6.855 | 6.814 | 6.6858 | 6.7092 | 56.7342 | 0.051061 |  | 62.069 | 100
19980922130000 | 1998-09-22 13:00 | 655.043 |  | 20.674 | 148.717 | 151.788 | 150.916 | 147.58 |  | 1295.704 | 1423.958 |  | 7.1602 | 7.0869 | 7.8682 | 7.5913 | 6.865 | 6.8191 | 6.7017 | 6.7185 | 56.8109 | 0.05113 |  | 62.069 | 100
19980922133000 | 1998-09-22 13:30 | 653.391 |  | 0.088 | 148.858 | 152.231 | 151.301 | 147.528 |  | 1291.037 | 1421.208 |  | 7.1663 | 7.0955 | 7.8721 | 7.6096 | 6.8765 | 6.8345 | 6.7192 | 6.7307 | 56.9044 | 0.051214 |  | 62.069 | 100
19980922140000 | 1998-09-22 14:00 | 659.394 |  | 0.291 | 149.055 | 151.695 | 151.469 | 148.23 |  | 1296.287 | 1424.958 |  | 7.1907 | 7.116 | 7.9033 | 7.6348 | 6.9001 | 6.8574 | 6.7354 | 6.7437 | 57.0814 | 0.051373 |  | 62.069 | 100
19980922143000 | 1998-09-22 14:30 | 654.151 |  | 1.516 | 148.501 | 151.995 | 151.297 | 147.787 |  | 1294.704 | 1423.208 |  | 7.1763 | 7.1008 | 7.8638 | 7.6042 | 6.8696 | 6.8345 | 6.7146 | 6.7307 | 56.8945 | 0.051205 |  | 62.069 | 100
19980922150000 | 1998-09-22 15:00 | 656.117 |  | 0.41 | 148.872 | 152.634 | 151.158 | 147.436 |  | 1298.371 | 1426.291 |  | 7.2075 | 7.1016 | 7.9126 | 7.634 | 6.897 | 6.8467 | 6.7275 | 6.7458 | 57.0727 | 0.051365 |  | 62.069 | 100
19980922153000 | 1998-09-22 15:30 | 578.392 |  | 1.555 | 148.35 | 149.405 | 150.396 | 145.197 |  | 1154.366 | 1269.703 |  | 6.5483 | 6.4675 | 7.0901 | 6.8101 | 6.2759 | 6.26 | 6.157 | 6.1409 | 51.7498 | 0.046575 |  | 62.069 | 100
19980922160000 | 1998-09-22 16:00 | 529.03 |  | 0 | 147.03 | 150.159 | 149.071 | 146.941 |  | 1051.114 | 1152.95 |  | 6.0166 | 5.9053 | 6.4172 | 6.1013 | 5.7642 | 5.7495 | 5.6611 | 5.6023 | 47.2175 | 0.042496 |  | 62.069 | 100
19980922163000 | 1998-09-22 16:30 | 532.596 |  | 1.434 | 147.986 | 151.478 | 150.33 | 148.508 |  | 1053.197 | 1157.283 |  | 5.9746 | 5.8547 | 6.3691 | 6.0449 | 5.7236 | 5.7068 | 5.6167 | 5.5459 | 46.8363 | 0.042153 |  | 62.069 | 100
19980922170000 | 1998-09-22 17:00 | 543.265 |  | 0.088 | 148.799 | 151.515 | 151.085 | 148.544 |  | 1116.032 | 1225.869 |  | 6.2698 | 6.157 | 6.7314 | 6.4492 | 6.0303 | 6.0449 | 5.9495 | 5.8701 | 49.5022 | 0.044552 |  | 62.069 | 100
19980922173000 | 1998-09-22 17:30 | 630.454 |  | 1.639 | 150.142 | 153.232 | 152.727 | 149.767 |  | 1260.703 | 1385.123 |  | 6.9993 | 6.9229 | 7.6563 | 7.4036 | 6.6995 | 6.6848 | 6.5667 | 6.5667 | 55.4998 | 0.04995 |  | 62.069 | 100
19980922180000 | 1998-09-22 18:00 | 634.307 |  | 0.167 | 149.518 | 151.53 | 152.131 | 148.064 |  | 1268.62 | 1388.123 |  | 7.0061 | 6.9512 | 7.6821 | 7.4355 | 6.7192 | 6.698 | 6.5881 | 6.5933 | 55.6735 | 0.050106 |  | 62.069 | 100
19980922183000 | 1998-09-22 18:30 | 633.547 |  | 1.888 | 148.687 | 152.283 | 151.312 | 148.075 |  | 1261.036 | 1386.206 |  | 7.0032 | 6.9382 | 7.6592 | 7.4165 | 6.7009 | 6.6797 | 6.5713 | 6.5842 | 55.5532 | 0.049998 |  | 62.069 | 100
19980922190000 | 1998-09-22 19:00 | 567.12 |  | 0 | 147.718 | 149.989 | 150.146 | 146.028 |  | 1147.866 | 1255.703 |  | 6.5332 | 6.4309 | 7.0725 | 6.7666 | 6.2607 | 6.2234 | 6.1218 | 6.1042 | 51.5133 | 0.046362 |  | 62.069 | 100
19980922193000 | 1998-09-22 19:30 | 574.827 |  | 1.639 | 148.196 | 153.536 | 150.477 | 149.328 |  | 1173.7 | 1288.954 |  | 6.5957 | 6.4912 | 7.1487 | 6.8467 | 6.3157 | 6.2683 | 6.1646 | 6.1616 | 51.9925 | 0.046793 |  | 62.069 | 100
19980922200000 | 1998-09-22 20:00 | 629.929 |  | 0.168 | 149.601 | 152.309 | 152.116 | 148.843 |  | 1278.537 | 1404.374 |  | 7.0413 | 6.9673 | 7.7041 | 7.4578 | 6.7354 | 6.6987 | 6.5903 | 6.5986 | 55.7935 | 0.050214 |  | 62.069 | 100
19980922203000 | 1998-09-22 20:30 | 550.448 |  | 1.518 | 149.027 | 149.741 | 151.41 | 145.533 |  | 1092.198 | 1192.701 |  | 6.1577 | 6.0457 | 6.5645 | 6.2356 | 5.8777 | 5.8181 | 5.7319 | 5.7312 | 48.1624 | 0.043346 |  | 62.069 | 100
19980922210000 | 1998-09-22 21:00 | 416.807 |  | 0 | 146.684 | 149.328 | 148.892 | 146.605 |  | 848.608 | 924.86 |  | 5.0117 | 4.8049 | 5.0735 | 4.7112 | 4.7539 | 4.7632 | 4.6899 | 4.5708 | 38.3791 | 0.034541 |  | 62.069 | 100
19980922213000 | 1998-09-22 21:30 | 345.635 |  | 1.432 | 146.547 | 148.673 | 148.62 | 146.446 |  | 707.02 | 762.522 |  | 0.0032 | 0.0085 | 5.6938 | 5.3948 | 5.2361 | 5.2896 | 5.2048 | 5.0842 | 31.915 | 0.028723 |  | 62.069 | 100
19980922220000 | 1998-09-22 22:00 | 345.216 |  | 0 | 146.445 | 148.426 | 148.753 | 147.188 |  | 683.77 | 737.104 |  | 0.0032 | 0.0085 | 5.5574 | 5.2834 | 5.1277 | 5.1858 | 5.0867 | 4.9927 | 31.2454 | 0.028121 |  | 62.069 | 100
19980922223000 | 1998-09-22 22:30 | 331.139 |  | 0.574 | 148.065 | 150.901 | 150.056 | 149.664 |  | 707.354 | 765.522 |  | 0.0032 | 0.0078 | 5.4824 | 5.217 | 5.0759 | 5.1575 | 5.0684 | 4.947 | 30.9592 | 0.027863 |  | 62.069 | 100
19980922230000 | 1998-09-22 23:00 | 326.761 |  | 0 | 148.855 | 151.2 | 151.261 | 149.468 |  | 692.687 | 745.271 |  | 0.0032 | 0.0085 | 5.4138 | 5.1355 | 5.0142 | 5.095 | 5.0063 | 4.8752 | 30.5517 | 0.027497 |  | 62.069 | 100
19980922233000 | 1998-09-22 23:30 | 339.58 |  | 0.574 | 148.43 | 150.705 | 151.006 | 149.468 |  | 690.52 | 743.771 |  | 0.004 | 0.0085 | 5.5215 | 5.2041 | 5.1133 | 5.1453 | 5.0562 | 4.9409 | 30.9938 | 0.027894 |  | 62.069 | 100
19980923000000 | 1998-09-23 | 338.793 |  | 0 | 148.847 | 150.834 | 151.44 | 149.597 |  | 694.52 | 745.355 |  | 0.0032 | 0.0078 | 5.5588 | 5.2429 | 5.1262 | 5.1575 | 5.072 | 4.9668 | 31.1352 | 0.028022 |  | 62.069 | 100
19980923003000 | 1998-09-23 00:30 | 335.884 |  | 1.065 | 148.625 | 149.545 | 151.17 | 148.803 |  | 691.603 | 743.438 |  | 0.0032 | 0.0078 | 5.5513 | 5.2551 | 5.1309 | 5.1621 | 5.0752 | 4.9653 | 31.1509 | 0.028036 |  | 62.069 | 100
19980923010000 | 1998-09-23 01:00 | 331.48 |  | 0 | 148.995 | 151.629 | 151.336 | 150.886 |  | 713.687 | 766.772 |  | 0.0024 | 0.0085 | 5.584 | 5.2705 | 5.1514 | 5.1743 | 5.0796 | 4.9783 | 31.249 | 0.028124 |  | 62.069 | 100
19980923013000 | 1998-09-23 01:30 | 334.599 |  | 1.52 | 149.131 | 150.535 | 151.716 | 149.298 |  | 719.354 | 776.689 |  | 0.004 | 0.0085 | 5.6306 | 5.3865 | 5.1965 | 5.2529 | 5.1636 | 5.0667 | 31.7093 | 0.028538 |  | 62.069 | 100
19980923020000 | 1998-09-23 02:00 | 336.618 |  | 0 | 148.537 | 151.304 | 151.346 | 149.323 |  | 715.937 | 767.689 |  | 0.004 | 0.0078 | 5.626 | 5.3596 | 5.1743 | 5.2253 | 5.1355 | 5.0447 | 31.5772 | 0.028419 |  | 62.069 | 100
19980923023000 | 1998-09-23 02:30 | 337.771 |  | 1.677 | 148.725 | 151.551 | 151.018 | 149.323 |  | 725.604 | 777.939 |  | 0.004 | 0.0078 | 5.6389 | 5.3735 | 5.1926 | 5.2429 | 5.1567 | 5.0652 | 31.6816 | 0.028513 |  | 62.069 | 100
19980923030000 | 1998-09-23 03:00 | 340.891 |  | 0 | 148.887 | 149.819 | 151.048 | 149.076 |  | 701.603 | 751.355 |  | 0.0024 | 0.0078 | 5.6648 | 5.3865 | 5.2041 | 5.2544 | 5.1711 | 5.0728 | 31.7639 | 0.028588 |  | 62.069 | 100
19980923033000 | 1998-09-23 03:30 | 340.655 |  | 1.556 | 147.659 | 150.705 | 150.15 | 148.725 |  | 700.77 | 757.272 |  | 0.0047 | 0.0078 | 5.6282 | 5.3406 | 5.1743 | 5.2192 | 5.1294 | 5.04 | 31.5442 | 0.02839 |  | 62.069 | 100
19980923040000 | 1998-09-23 04:00 | 341.415 |  | 0 | 148.317 | 151.278 | 150.875 | 149.545 |  | 699.353 | 753.688 |  | 0.0032 | 0.0093 | 5.626 | 5.3589 | 5.1858 | 5.2346 | 5.1453 | 5.053 | 31.6161 | 0.028454 |  | 62.069 | 100
19980923043000 | 1998-09-23 04:30 | 343.066 |  | 1.8 | 148.746 | 151.03 | 151.356 | 149.05 |  | 703.52 | 758.022 |  | 0.0032 | 0.0085 | 5.6116 | 5.3535 | 5.1711 | 5.2178 | 5.1294 | 5.0483 | 31.5434 | 0.028389 |  | 62.069 | 100
19980923050000 | 1998-09-23 05:00 | 344.508 |  | 0 | 148.866 | 150.21 | 150.871 | 147.735 |  | 703.937 | 760.355 |  | 0.0024 | 0.0078 | 5.6389 | 5.375 | 5.1873 | 5.2253 | 5.1423 | 5.0562 | 31.6352 | 0.028472 |  | 62.069 | 100
19980923053000 | 1998-09-23 05:30 | 423.649 |  | 1.887 | 148.684 | 153.402 | 151.06 | 151.175 |  | 842.774 | 922.693 |  | 0.0032 | 0.0085 | 6.8909 | 6.6147 | 6.1272 | 6.1204 | 6.0166 | 6.0127 | 37.7942 | 0.034015 |  | 62.069 | 100
19980923060000 | 1998-09-23 06:00 | 419.245 |  | 0 | 150.021 | 151.84 | 152.47 | 149.859 |  | 839.274 | 918.443 |  | 4.7783 | 4.8792 | 5.1362 | 4.8164 | 4.7754 | 4.7866 | 4.7134 | 4.6357 | 38.5212 | 0.034669 |  | 62.069 | 100
19980923063000 | 1998-09-23 06:30 | 421.683 |  | 1.922 | 148.961 | 150.524 | 151.364 | 149.039 |  | 846.024 | 928.61 |  | 4.9417 | 4.8293 | 5.05 | 4.7822 | 4.7288 | 4.7761 | 4.6997 | 4.5845 | 38.3923 | 0.034553 |  | 62.069 | 100
19980923070000 | 1998-09-23 07:00 | 462.97 |  | 0.082 | 148.637 | 151.633 | 150.91 | 148.168 |  | 961.028 | 1058.114 |  | 5.5068 | 5.4063 | 5.7656 | 5.5313 | 5.281 | 5.3108 | 5.2231 | 5.1499 | 43.1748 | 0.038857 |  | 62.069 | 100
19980923073000 | 1998-09-23 07:30 | 543.999 |  | 2.007 | 150.028 | 152.686 | 152.591 | 150.21 |  | 1141.616 | 1253.453 |  | 6.269 | 6.2209 | 6.7681 | 6.5544 | 6.0396 | 6.0327 | 5.9258 | 5.9167 | 49.7272 | 0.044754 |  | 62.069 | 100
19980923080000 | 1998-09-23 08:00 | 639.733 |  | 0.408 | 150.757 | 153.196 | 153.41 | 149.483 |  | 1280.703 | 1411.124 |  | 7.0754 | 7.0374 | 7.7576 | 7.5547 | 6.7788 | 6.7458 | 6.627 | 6.6675 | 56.2442 | 0.05062 |  | 62.069 | 100
19980923083000 | 1998-09-23 08:30 | 642.04 |  | 1.761 | 149.599 | 152.49 | 152.148 | 148.777 |  | 1293.454 | 1423.708 |  | 7.1587 | 7.0962 | 7.8584 | 7.6172 | 6.8496 | 6.8208 | 6.7017 | 6.7368 | 56.8394 | 0.051155 |  | 62.069 | 100
19980923090000 | 1998-09-23 09:00 | 639.786 |  | 0.413 | 148.987 | 152.556 | 151.512 | 147.853 |  | 1307.454 | 1439.125 |  | 7.1709 | 7.1343 | 7.8682 | 7.6538 | 6.8628 | 6.8528 | 6.7354 | 6.7673 | 57.0455 | 0.051341 |  | 62.069 | 100
19980923093000 | 1998-09-23 09:30 | 641.568 |  | 2.01 | 148.955 | 151.917 | 151.49 | 146.967 |  | 1298.537 | 1429.291 |  | 7.1313 | 7.1099 | 7.8408 | 7.644 | 6.8445 | 6.8337 | 6.7178 | 6.7559 | 56.8779 | 0.05119 |  | 62.069 | 100
19980923100000 | 1998-09-23 10:00 | 641.332 |  | 0.29 | 148.428 | 153.241 | 150.972 | 149.033 |  | 1310.454 | 1439.791 |  | 7.1763 | 7.1091 | 7.8743 | 7.6135 | 6.8711 | 6.8215 | 6.7048 | 6.7354 | 56.906 | 0.051215 |  | 62.069 | 100
19980923103000 | 1998-09-23 10:30 | 642.591 |  | 2.008 | 148.819 | 152.815 | 151.322 | 148.607 |  | 1304.621 | 1432.958 |  | 7.1877 | 7.103 | 7.8943 | 7.6248 | 6.8801 | 6.8276 | 6.7056 | 6.7375 | 56.9606 | 0.051265 |  | 62.069 | 100
19980923110000 | 1998-09-23 11:00 | 641.385 |  | 0.166 | 148.639 | 151.533 | 151.196 | 148.562 |  | 1303.371 | 1428.291 |  | 7.1633 | 7.1152 | 7.8682 | 7.605 | 6.8582 | 6.8208 | 6.7048 | 6.7268 | 56.8623 | 0.051176 |  | 62.069 | 100
19980923113000 | 1998-09-23 11:30 | 643.77 |  | 1.393 | 148.475 | 151.02 | 150.911 | 146.565 |  | 1304.037 | 1433.708 |  | 7.1626 | 7.0894 | 7.8689 | 7.5928 | 6.8542 | 6.814 | 6.6934 | 6.7231 | 56.7984 | 0.051119 |  | 62.069 | 100
19980923120000 | 1998-09-23 12:00 | 580.699 |  | 0 | 148.216 | 151.079 | 150.339 | 146.376 |  | 1132.282 | 1238.786 |  | 6.4417 | 6.3645 | 6.9795 | 6.6643 | 6.1738 | 6.125 | 6.0378 | 6.041 | 50.8276 | 0.045745 |  | 62.069 | 100
19980923123000 | 1998-09-23 12:30 | 529.974 |  | 1.434 | 147.217 | 149.298 | 149.234 | 145.833 |  | 1059.114 | 1160.2 |  | 6.0098 | 5.9487 | 6.4111 | 6.1311 | 5.7825 | 5.7649 | 5.677 | 5.6404 | 47.3655 | 0.042629 |  | 62.069 | 100
19980923130000 | 1998-09-23 13:00 | 472.277 |  | 0 | 147.989 | 150.178 | 150.26 | 146.961 |  | 968.278 | 1060.447 |  | 5.5283 | 5.4124 | 5.8091 | 5.4834 | 5.3086 | 5.314 | 5.2361 | 5.1423 | 43.2342 | 0.038911 |  | 62.069 | 100
19980923133000 | 1998-09-23 13:30 | 474.007 |  | 1.187 | 147.818 | 150.809 | 150.246 | 148.334 |  | 975.611 | 1070.614 |  | 5.5261 | 5.4092 | 5.7671 | 5.4763 | 5.2986 | 5.2971 | 5.2209 | 5.127 | 43.1223 | 0.03881 |  | 62.069 | 100
19980923140000 | 1998-09-23 14:00 | 475.134 |  | 0 | 148.405 | 150.555 | 150.824 | 148.327 |  | 961.778 | 1055.447 |  | 5.4626 | 5.3589 | 5.7107 | 5.4023 | 5.2354 | 5.2605 | 5.1721 | 5.0842 | 42.6867 | 0.038418 |  | 62.069 | 100
19980923143000 | 1998-09-23 14:30 | 474.112 |  | 1.64 | 149.021 | 150.419 | 151.458 | 148.439 |  | 973.778 | 1067.781 |  | 5.5032 | 5.3918 | 5.7495 | 5.4536 | 5.2551 | 5.2896 | 5.2102 | 5.1262 | 42.9792 | 0.038681 |  | 62.069 | 100
19980923150000 | 1998-09-23 15:00 | 536.423 |  | 0 | 148.435 | 149.552 | 150.87 | 147.077 |  | 1051.28 | 1153.116 |  | 6.0256 | 5.9236 | 6.4338 | 6.1409 | 5.7625 | 5.7581 | 5.6641 | 5.6055 | 47.3141 | 0.042583 |  | 62.069 | 100
19980923153000 | 1998-09-23 15:30 | 536.292 |  | 1.884 | 148.864 | 151.362 | 151.322 | 148.639 |  | 1056.03 | 1158.533 |  | 5.9839 | 5.8906 | 6.3796 | 6.0859 | 5.7373 | 5.7083 | 5.6177 | 5.5779 | 46.9812 | 0.042283 |  | 62.069 | 100
19980923160000 | 1998-09-23 16:00 | 530.472 |  | 0.085 | 148.761 | 151.063 | 151.323 | 148.588 |  | 1049.447 | 1150.366 |  | 5.9609 | 5.8464 | 6.3408 | 6.0317 | 5.7136 | 5.6877 | 5.5947 | 5.5391 | 46.7149 | 0.042043 |  | 62.069 | 100
19980923163000 | 1998-09-23 16:30 | 412.351 |  | 1.519 | 148.559 | 149.149 | 150.715 | 146.674 |  | 850.024 | 930.86 |  | 5.0156 | 4.8813 | 5.1179 | 4.7913 | 4.7898 | 4.821 | 4.7524 | 4.6167 | 38.786 | 0.034907 |  | 62.069 | 100
19980923170000 | 1998-09-23 17:00 | 420.163 |  | 0.085 | 147.351 | 150.206 | 149.674 | 148.226 |  | 842.191 | 926.36 |  | 4.918 | 4.7693 | 4.9941 | 4.6753 | 4.6982 | 4.7432 | 4.6692 | 4.519 | 37.9863 | 0.034188 |  | 62.069 | 100
19980923173000 | 1998-09-23 17:30 | 429.705 |  | 1.517 | 148.455 | 151.573 | 150.888 | 148.603 |  | 905.109 | 996.779 |  | 5.2415 | 5.1416 | 5.4407 | 5.1704 | 5.03 | 5.1094 | 5.0286 | 4.8652 | 41.0274 | 0.036925 |  | 62.069 | 100
19980923180000 | 1998-09-23 18:00 | 466.693 |  | 0.086 | 149.48 | 151.455 | 151.895 | 149.227 |  | 951.027 | 1045.113 |  | 5.426 | 5.3125 | 5.6382 | 5.375 | 5.179 | 5.2026 | 5.1262 | 5.053 | 42.3125 | 0.038081 |  | 62.069 | 100
19980923183000 | 1998-09-23 18:30 | 519.908 |  | 0.291 | 149.514 | 151.728 | 152.016 | 149.5 |  | 1063.281 | 1168.784 |  | 5.9868 | 5.8777 | 6.3843 | 6.0859 | 5.7344 | 5.7153 | 5.6274 | 5.571 | 46.9828 | 0.042285 |  | 62.069 | 100
19980923190000 | 1998-09-23 19:00 | 528.375 |  | 0 | 149.081 | 150.712 | 151.71 | 148.237 |  | 1053.28 | 1163.283 |  | 5.9785 | 5.8586 | 6.3645 | 6.0708 | 5.7183 | 5.7014 | 5.6145 | 5.5657 | 46.8723 | 0.042185 |  | 62.069 | 100
19980923193000 | 1998-09-23 19:30 | 527.327 |  | 1.639 | 148.233 | 151.181 | 150.576 | 148.211 |  | 1048.947 | 1154.366 |  | 5.9868 | 5.8845 | 6.3875 | 6.0845 | 5.7412 | 5.7312 | 5.6404 | 5.5994 | 47.0555 | 0.04235 |  | 62.069 | 100
19980923200000 | 1998-09-23 20:00 | 478.699 |  | 20.714 | 148.154 | 150.088 | 150.847 | 145.88 |  | 953.611 | 1051.364 |  | 5.5032 | 5.3811 | 5.748 | 5.4443 | 5.2612 | 5.2781 | 5.1956 | 5.1072 | 42.9187 | 0.038627 |  | 62.069 | 100
19980923203000 | 1998-09-23 20:30 | 391.353 |  | 20.254 | 147.942 | 149.788 | 150.074 | 148.551 |  | 757.355 | 821.94 |  | 3.2296 | 4.3945 | 4.5654 | 4.1956 | 4.3701 | 4.4275 | 4.3672 | 4.2024 | 33.7523 | 0.030377 |  | 62.069 | 100
19980923210000 | 1998-09-23 21:00 | 335.019 |  | 0 | 147.093 | 149.711 | 149.597 | 147.731 |  | 689.936 | 748.355 |  | 1.6618 | 0.0078 | 5.2529 | 5.0142 | 4.9233 | 5.0042 | 4.9133 | 4.7952 | 31.5727 | 0.028415 |  | 62.069 | 100
19980923213000 | 1998-09-23 21:30 | 337.692 |  | 1.639 | 147.989 | 152.367 | 150.467 | 150.882 |  | 710.187 | 770.105 |  | 1.6465 | 0.0078 | 5.2192 | 4.9341 | 4.8699 | 4.9402 | 4.8486 | 4.7234 | 31.1897 | 0.028071 |  | 62.069 | 100
19980923220000 | 1998-09-23 22:00 | 329.802 |  | 0 | 149.157 | 150.557 | 151.677 | 149.319 |  | 707.187 | 767.522 |  | 0.0047 | 0.007 | 5.4695 | 5.2375 | 5.0759 | 5.1934 | 5.1086 | 4.9568 | 31.0534 | 0.027948 |  | 62.069 | 100
19980923223000 | 1998-09-23 22:30 | 334.232 |  | 1.431 | 148.351 | 150.649 | 150.73 | 149.164 |  | 703.604 | 761.355 |  | 0.0032 | 0.0093 | 5.6177 | 5.356 | 5.175 | 5.2322 | 5.1492 | 5.0469 | 31.5895 | 0.028431 |  | 62.069 | 100
19980923230000 | 1998-09-23 23:00 | 337.928 |  | 0 | 148.375 | 150.624 | 150.652 | 148.148 |  | 711.104 | 767.939 |  | 0.0032 | 0.007 | 5.5513 | 5.2949 | 5.1248 | 5.1934 | 5.1118 | 5.0012 | 31.2876 | 0.028159 |  | 62.069 | 100
19980923233000 | 1998-09-23 23:30 | 338.557 |  | 1.309 | 148.767 | 148.865 | 150.743 | 147.38 |  | 688.853 | 745.938 |  | 0.004 | 0.0085 | 5.5642 | 5.304 | 5.1201 | 5.1833 | 5.104 | 4.9995 | 31.2876 | 0.028159 |  | 62.069 | 100
19980924000000 | 1998-09-24 | 338.872 |  | 0 | 147.555 | 150.103 | 150.112 | 149.113 |  | 687.603 | 744.605 |  | 0.004 | 0.0078 | 5.5078 | 5.2925 | 5.0935 | 5.1721 | 5.0896 | 4.9966 | 31.1639 | 0.028048 |  | 62.069 | 100
19980924003000 | 1998-09-24 00:30 | 340.104 |  | 1.556 | 148.439 | 151.119 | 151.057 | 149.633 |  | 688.603 | 744.938 |  | 0.0047 | 0.0078 | 5.5481 | 5.2712 | 5.1086 | 5.1804 | 5.0867 | 4.9836 | 31.1911 | 0.028072 |  | 62.069 | 100
19980924010000 | 1998-09-24 01:00 | 340.419 |  | 0 | 148.813 | 151.067 | 151.299 | 149.087 |  | 686.353 | 743.688 |  | 0.0032 | 0.0085 | 5.4978 | 5.2576 | 5.082 | 5.1704 | 5.0828 | 4.9851 | 31.0874 | 0.027979 |  | 62.069 | 100
19980924013000 | 1998-09-24 01:30 | 339.423 |  | 1.8 | 148.813 | 150.129 | 150.903 | 149.881 |  | 690.603 | 747.188 |  | 0.004 | 0.0093 | 5.5398 | 5.2957 | 5.1179 | 5.1895 | 5.1011 | 5.0012 | 31.2585 | 0.028133 |  | 62.069 | 100
19980924020000 | 1998-09-24 02:00 | 328.806 |  | 0 | 149.307 | 152.356 | 151.775 | 150.624 |  | 717.854 | 778.022 |  | 0.004 | 0.0078 | 5.8496 | 5.6472 | 5.3879 | 5.4321 | 3.7949 | 5.2437 | 31.3672 | 0.02823 |  | 62.069 | 100
19980924023000 | 1998-09-24 02:30 | 328.36 |  | 1.309 | 149.741 | 150.169 | 151.964 | 149.674 |  | 724.021 | 784.273 |  | 0.0032 | 0.0078 | 5.9006 | 5.6274 | 5.3894 | 5.4199 | 3.7759 | 5.2522 | 31.3764 | 0.028239 |  | 62.069 | 100
19980924030000 | 1998-09-24 03:00 | 336.801 |  | 0 | 148.586 | 150.572 | 151.059 | 148.344 |  | 728.771 | 793.856 |  | 0.0032 | 0.0085 | 5.9121 | 5.6428 | 5.3979 | 5.3987 | 3.7881 | 5.2407 | 31.392 | 0.028253 |  | 62.069 | 100
19980924033000 | 1998-09-24 03:30 | 335.726 |  | 1.554 | 148.967 | 150.324 | 151.312 | 150.324 |  | 728.188 | 793.273 |  | 0.004 | 0.0085 | 5.6848 | 5.4314 | 5.2253 | 5.2688 | 5.2644 | 5.114 | 32.0012 | 0.028801 |  | 62.069 | 100
19980924040000 | 1998-09-24 04:00 | 340.34 |  | 0 | 148.468 | 148.566 | 151.253 | 148.071 |  | 714.521 | 775.606 |  | 0.0032 | 0.0078 | 5.6917 | 5.4275 | 5.2339 | 5.2659 | 5.2522 | 5.0935 | 31.9757 | 0.028778 |  | 62.069 | 100
19980924043000 | 1998-09-24 04:30 | 337.981 |  | 1.64 | 147.701 | 150.469 | 149.998 | 149.231 |  | 717.521 | 778.856 |  | 0.0032 | 0.0093 | 5.7161 | 5.4185 | 5.2375 | 5.2673 | 5.2576 | 5.1033 | 32.0128 | 0.028812 |  | 62.069 | 100
19980924050000 | 1998-09-24 05:00 | 342.883 |  | 0 | 148.3 | 149.829 | 150.798 | 149.334 |  | 712.52 | 775.439 |  | 0.004 | 0.0085 | 5.6626 | 5.4207 | 5.2124 | 5.2583 | 5.2429 | 5.0842 | 31.8936 | 0.028704 |  | 62.069 | 100
19980924053000 | 1998-09-24 05:30 | 341.887 |  | 2.13 | 148.286 | 150.964 | 150.904 | 148.983 |  | 706.604 | 764.439 |  | 0.004 | 0.0093 | 5.6726 | 5.4084 | 5.2139 | 5.2551 | 5.2444 | 5.085 | 31.8927 | 0.028703 |  | 62.069 | 100
19980924060000 | 1998-09-24 06:00 | 485.803 |  | 0.292 | 149.496 | 153.672 | 151.71 | 150.454 |  | 1034.446 | 1140.533 |  | 5.7351 | 5.6252 | 6.0234 | 5.7961 | 5.4702 | 5.5129 | 5.4993 | 5.3438 | 45.006 | 0.040505 |  | 62.069 | 100
19980924063000 | 1998-09-24 06:30 | 606.703 |  | 2.254 | 151.01 | 153.878 | 153.782 | 151.65 |  | 1249.036 | 1365.373 |  | 6.8506 | 6.7803 | 7.4287 | 7.2358 | 6.5232 | 6.5034 | 6.5042 | 6.4058 | 54.232 | 0.048809 |  | 62.069 | 100
19980924070000 | 1998-09-24 07:00 | 645.658 |  | 0.41 | 150.69 | 152.548 | 153.51 | 149.083 |  | 1301.871 | 1427.041 |  | 7.177 | 7.0894 | 7.8606 | 7.6028 | 6.8452 | 6.7925 | 6.8047 | 6.7139 | 56.8861 | 0.051197 |  | 62.069 | 100
19980924073000 | 1998-09-24 07:30 | 642.565 |  | 1.637 | 149.225 | 150.789 | 151.781 | 148.314 |  | 1291.204 | 1418.374 |  | 7.1343 | 7.0686 | 7.8218 | 7.5759 | 6.8191 | 6.7795 | 6.7825 | 6.6909 | 56.6726 | 0.051005 |  | 62.069 | 100
19980924080000 | 1998-09-24 08:00 | 646.969 |  | 0.412 | 148.669 | 151.584 | 151.258 | 147.623 |  | 1306.287 | 1433.958 |  | 7.1221 | 7.0564 | 7.7783 | 7.5342 | 6.8047 | 6.7817 | 6.7864 | 6.6865 | 56.5503 | 0.050895 |  | 62.069 | 100
19980924083000 | 1998-09-24 08:30 | 647.021 |  | 1.514 | 148.829 | 150.774 | 151.237 | 148.052 |  | 1289.62 | 1417.124 |  | 7.1443 | 7.0535 | 7.8103 | 7.5349 | 6.8245 | 6.7925 | 6.7964 | 6.6819 | 56.6383 | 0.050974 |  | 62.069 | 100
19980924090000 | 1998-09-24 09:00 | 648.305 |  | 0.41 | 148.321 | 151.022 | 150.655 | 148.299 |  | 1283.203 | 1409.707 |  | 7.1235 | 7.0276 | 7.8042 | 7.5088 | 6.8108 | 6.7673 | 6.7749 | 6.665 | 56.4821 | 0.050834 |  | 62.069 | 100
19980924093000 | 1998-09-24 09:30 | 648.437 |  | 1.515 | 148.753 | 151.739 | 151.166 | 148.273 |  | 1286.12 | 1409.457 |  | 7.1458 | 7.0435 | 7.8157 | 7.5166 | 6.8237 | 6.7712 | 6.7742 | 6.6675 | 56.5582 | 0.050902 |  | 62.069 | 100
19980924100000 | 1998-09-24 10:00 | 651.923 |  | 0.53 | 148.992 | 150.774 | 151.447 | 147.804 |  | 1290.537 | 1416.124 |  | 7.1519 | 7.0405 | 7.8225 | 7.5432 | 6.8352 | 6.7849 | 6.791 | 6.6765 | 56.6457 | 0.050981 |  | 62.069 | 100
19980924103000 | 1998-09-24 10:30 | 650.429 |  | 22.384 | 148.64 | 151.269 | 151.34 | 148.299 |  | 1294.87 | 1418.541 |  | 7.1411 | 7.0564 | 7.8286 | 7.5439 | 6.8367 | 6.7971 | 6.7993 | 6.6833 | 56.6864 | 0.051018 |  | 62.069 | 100
19980924110000 | 1998-09-24 11:00 | 648.908 |  | 20.251 | 148.815 | 152.038 | 151.341 | 147.83 |  | 1291.37 | 1415.624 |  | 7.1365 | 7.0466 | 7.8293 | 7.5425 | 6.8391 | 6.7932 | 6.8062 | 6.6926 | 56.686 | 0.051017 |  | 62.069 | 100
19980924113000 | 1998-09-24 11:30 | 650.56 |  | 1.636 | 148.768 | 151.269 | 151.287 | 147.062 |  | 1288.62 | 1416.791 |  | 7.1191 | 7.0496 | 7.8096 | 7.5371 | 6.8169 | 6.7817 | 6.791 | 6.675 | 56.58 | 0.050922 |  | 62.069 | 100
19980924120000 | 1998-09-24 12:00 | 649.773 |  | 0.408 | 148.454 | 151.945 | 150.871 | 147.49 |  | 1288.204 | 1414.957 |  | 7.1106 | 7.0388 | 7.7881 | 7.5264 | 6.8079 | 6.7749 | 6.7825 | 6.6589 | 56.4881 | 0.050839 |  | 62.069 | 100
19980924123000 | 1998-09-24 12:30 | 640.153 |  | 1.76 | 148.785 | 152.115 | 151.015 | 148.403 |  | 1241.786 | 1360.872 |  | 6.8811 | 6.8008 | 7.5127 | 7.1831 | 6.582 | 6.5088 | 6.5117 | 6.4119 | 54.3921 | 0.048953 |  | 62.069 | 100
19980924130000 | 1998-09-24 13:00 | 574.04 |  | 0.167 | 147.824 | 150.357 | 149.87 | 147.139 |  | 1144.866 | 1254.369 |  | 6.4033 | 6.3196 | 6.9192 | 6.6169 | 6.147 | 6.1035 | 6.1128 | 5.9854 | 50.6077 | 0.045547 |  | 62.069 | 100
19980924133000 | 1998-09-24 13:30 | 571.131 |  | 1.395 | 148.318 | 150.8 | 150.414 | 147.83 |  | 1132.866 | 1245.286 |  | 6.385 | 6.321 | 6.9038 | 6.6262 | 6.1426 | 6.1035 | 6.1135 | 5.9944 | 50.59 | 0.045531 |  | 62.069 | 100
19980924140000 | 1998-09-24 14:00 | 576.033 |  | 0.082 | 148.642 | 151.218 | 150.988 | 147.505 |  | 1144.699 | 1259.12 |  | 6.4065 | 6.3171 | 6.9146 | 6.637 | 6.144 | 6.0959 | 6.106 | 5.9829 | 50.604 | 0.045544 |  | 62.069 | 100
19980924143000 | 1998-09-24 14:30 | 570.816 |  | 1.637 | 148.844 | 151.543 | 151.257 | 148.078 |  | 1140.283 | 1250.786 |  | 6.3735 | 6.3157 | 6.8887 | 6.6079 | 6.1211 | 6.0906 | 6.0981 | 5.9861 | 50.4817 | 0.045434 |  | 62.069 | 100
19980924150000 | 1998-09-24 15:00 | 572.179 |  | 0.084 | 148.87 | 151.687 | 151.373 | 149.212 |  | 1145.45 | 1253.453 |  | 6.4111 | 6.3218 | 6.9275 | 6.6162 | 6.1462 | 6.0913 | 6.1006 | 5.9854 | 50.6001 | 0.04554 |  | 62.069 | 100
19980924153000 | 1998-09-24 15:30 | 573.018 |  | 2.002 | 148.539 | 150.97 | 151.2 | 148.495 |  | 1141.783 | 1253.369 |  | 6.3857 | 6.3179 | 6.9016 | 6.6169 | 6.1265 | 6.0876 | 6.0989 | 5.97 | 50.5051 | 0.045455 |  | 62.069 | 100
19980924160000 | 1998-09-24 16:00 | 573.202 |  | 0.082 | 148.55 | 151.713 | 151.133 | 148.743 |  | 1145.116 | 1251.703 |  | 6.3667 | 6.3003 | 6.8779 | 6.6003 | 6.1211 | 6.0762 | 6.092 | 5.9692 | 50.4037 | 0.045363 |  | 62.069 | 100
19980924163000 | 1998-09-24 16:30 | 525.125 |  | 1.762 | 148.213 | 150.15 | 150.333 | 146.685 |  | 1038.696 | 1141.699 |  | 5.9646 | 5.8862 | 6.3508 | 6.064 | 5.7222 | 5.7039 | 5.7168 | 5.5664 | 46.9749 | 0.042277 |  | 62.069 | 100
19980924170000 | 1998-09-24 17:00 | 524.6 |  | 0 | 147.906 | 151.166 | 150.285 | 147.948 |  | 1045.697 | 1149.2 |  | 5.9136 | 5.8296 | 6.2952 | 6.0151 | 5.6633 | 5.6633 | 5.6633 | 5.5229 | 46.5663 | 0.04191 |  | 62.069 | 100
19980924173000 | 1998-09-24 17:30 | 527.982 |  | 1.757 | 148.8 | 151.61 | 151.104 | 148.392 |  | 1052.697 | 1157.7 |  | 5.8845 | 5.8174 | 6.2554 | 6.0066 | 5.6421 | 5.636 | 5.645 | 5.5032 | 46.3902 | 0.041751 |  | 62.069 | 100
19980924180000 | 1998-09-24 18:00 | 524.443 |  | 0 | 148.938 | 150.764 | 151.488 | 147.793 |  | 1048.78 | 1152.95 |  | 5.8579 | 5.8022 | 6.2249 | 5.9685 | 5.6062 | 5.6206 | 5.6267 | 5.4917 | 46.1987 | 0.041579 |  | 62.069 | 100
19980924183000 | 1998-09-24 18:30 | 595.143 |  | 1.879 | 149.329 | 152.77 | 151.878 | 150.047 |  | 1183.784 | 1293.287 |  | 6.5972 | 6.5103 | 7.1619 | 6.8679 | 6.3171 | 6.2708 | 6.2813 | 6.1677 | 52.1742 | 0.046957 |  | 62.069 | 100
19980924190000 | 1998-09-24 19:00 | 594.356 |  | 0.081 | 149.408 | 151.713 | 151.896 | 148.99 |  | 1193.368 | 1307.621 |  | 6.6194 | 6.5376 | 7.2046 | 6.9138 | 6.3484 | 6.2952 | 6.302 | 6.1958 | 52.4168 | 0.047175 |  | 62.069 | 100
19980924193000 | 1998-09-24 19:30 | 596.978 |  | 1.877 | 148.604 | 152.781 | 151.276 | 149.068 |  | 1265.453 | 1390.123 |  | 6.8413 | 6.8359 | 7.5166 | 7.2991 | 6.6086 | 6.585 | 6.5911 | 6.4722 | 54.7498 | 0.049275 |  | 62.069 | 100
19980924200000 | 1998-09-24 20:00 | 646.077 |  | 0.16 | 150.051 | 151.661 | 152.463 | 148.443 |  | 1341.705 | 1471.959 |  | 7.1274 | 7.093 | 7.8376 | 7.6021 | 6.8313 | 6.8184 | 6.8291 | 6.7139 | 56.8528 | 0.051168 |  | 62.069 | 100
19980924203000 | 1998-09-24 20:30 | 647.1 |  | 1.88 | 148.949 | 151.244 | 151.659 | 147.283 |  | 1336.455 | 1467.792 |  | 7.1267 | 7.0786 | 7.8315 | 7.583 | 6.8352 | 6.8025 | 6.8208 | 6.6995 | 56.7778 | 0.0511 |  | 62.069 | 100
19980924210000 | 1998-09-24 21:00 | 612.785 |  | 0.283 | 148.454 | 150.124 | 150.759 | 147.402 |  | 1224.952 | 1332.288 |  | 6.7429 | 6.6804 | 7.3479 | 7.0427 | 6.446 | 6.3904 | 6.3972 | 6.3142 | 53.3617 | 0.048026 |  | 62.069 | 100
19980924213000 | 1998-09-24 21:30 | 469.55 |  | 1.511 | 147.047 | 148.418 | 149.239 | 144.705 |  | 936.194 | 1024.196 |  | 5.3054 | 5.198 | 5.5046 | 5.1316 | 5.0759 | 5.0591 | 5.0522 | 4.9043 | 41.2311 | 0.037108 |  | 62.069 | 100
19980924220000 | 1998-09-24 22:00 | 372.662 |  | 0 | 145.419 | 147.948 | 147.448 | 145.473 |  | 736.854 | 795.94 |  | 0.0032 | 1.8861 | 5.7107 | 5.4612 | 5.2903 | 5.3445 | 5.3452 | 5.1277 | 34.1689 | 0.030752 |  | 62.069 | 100
19980924223000 | 1998-09-24 22:30 | 403.176 |  | 2.005 | 147.11 | 150.346 | 149.237 | 149.356 |  | 775.522 | 841.024 |  | 0.0024 | 0.0078 | 6.4194 | 6.1616 | 5.7764 | 5.7869 | 5.7815 | 5.6489 | 35.5849 | 0.032026 |  | 62.069 | 100
19980924230000 | 1998-09-24 23:00 | 399.086 |  | 0.082 | 148.816 | 150.609 | 151.452 | 149.123 |  | 778.606 | 849.774 |  | 0.0032 | 0.007 | 6.3538 | 6.0952 | 5.7373 | 5.7258 | 5.7258 | 5.5818 | 35.2299 | 0.031707 |  | 62.069 | 100
19980924233000 | 1998-09-24 23:30 | 383.882 |  | 0.082 | 148.619 | 150.402 | 151.338 | 148.917 |  | 735.438 | 798.273 |  | 0.0032 | 0.0078 | 6.0205 | 5.7373 | 5.4353 | 5.4307 | 5.4253 | 5.314 | 33.3741 | 0.030037 |  | 62.069 | 100
19980925000000 | 1998-09-25 | 318.975 |  | 0 | 148.06 | 149.061 | 150.42 | 147.328 |  | 657.936 | 703.02 |  | 0.0032 | 0.0093 | 5.2612 | 5.0056 | 4.8997 | 4.9858 | 4.9729 | 4.7852 | 29.9229 | 0.026931 |  | 62.069 | 100
19980925003000 | 1998-09-25 00:30 | 316.459 |  | 1.637 | 147.907 | 151.196 | 150.085 | 149.711 |  | 662.186 | 713.354 |  | 0.0032 | 0.007 | 5.1729 | 4.927 | 4.8372 | 4.9263 | 4.908 | 4.7065 | 29.4881 | 0.026539 |  | 62.069 | 100
19980925010000 | 1998-09-25 01:00 | 320.129 |  | 20.701 | 149.088 | 150.062 | 151.233 | 150.309 |  | 658.269 | 709.854 |  | 0.004 | 0.0078 | 5.1995 | 4.9158 | 4.844 | 4.9126 | 4.8997 | 4.7126 | 29.496 | 0.026546 |  | 62.069 | 100
19980925013000 | 1998-09-25 01:30 | 316.118 |  | 19.919 | 148.572 | 150.361 | 151.175 | 148.876 |  | 662.936 | 717.521 |  | 0.0032 | 0.007 | 5.2583 | 4.9819 | 4.8965 | 4.9546 | 4.9446 | 4.7439 | 29.79 | 0.026811 |  | 62.069 | 100
19980925020000 | 1998-09-25 02:00 | 316.695 |  | 0 | 148.669 | 150.882 | 150.828 | 150.139 |  | 664.936 | 716.604 |  | 0.0024 | 0.0078 | 5.2217 | 4.9941 | 4.8721 | 4.9507 | 4.9431 | 4.7471 | 29.739 | 0.026765 |  | 62.069 | 100
19980925023000 | 1998-09-25 02:30 | 316.328 |  | 2.411 | 148.963 | 150.294 | 151.216 | 150.294 |  | 659.436 | 709.52 |  | 0.0024 | 0.0078 | 5.1895 | 4.9194 | 4.8408 | 4.9104 | 4.9011 | 4.7173 | 29.4887 | 0.02654 |  | 62.069 | 100
19980925030000 | 1998-09-25 03:00 | 314.519 |  | 0 | 148.522 | 149.552 | 151.428 | 149.304 |  | 660.019 | 711.77 |  | 0.0032 | 0.0085 | 5.2102 | 4.9675 | 4.8691 | 4.9392 | 4.9348 | 4.741 | 29.6735 | 0.026706 |  | 62.069 | 100
19980925033000 | 1998-09-25 03:30 | 317.638 |  | 1.922 | 148.611 | 150.815 | 150.908 | 149.33 |  | 661.102 | 714.771 |  | 0.0032 | 0.0078 | 5.1743 | 4.9492 | 4.8469 | 4.9402 | 4.9302 | 4.7371 | 29.5889 | 0.02663 |  | 62.069 | 100
19980925040000 | 1998-09-25 04:00 | 315.725 |  | 0 | 148.554 | 150.372 | 150.908 | 150.619 |  | 669.686 | 722.271 |  | 0.0024 | 0.0078 | 5.1926 | 4.9714 | 4.8547 | 4.9417 | 4.9348 | 4.7341 | 29.6395 | 0.026676 |  | 62.069 | 100
19980925043000 | 1998-09-25 04:30 | 315.043 |  | 2.413 | 148.553 | 151.465 | 151.423 | 149.98 |  | 658.769 | 711.437 |  | 0.004 | 0.0078 | 5.2095 | 4.9722 | 4.8652 | 4.9575 | 4.9485 | 4.7517 | 29.7164 | 0.026745 |  | 62.069 | 100
19980925050000 | 1998-09-25 05:00 | 316.8 |  | 0 | 148.584 | 151.14 | 151.224 | 149.16 |  | 663.102 | 712.937 |  | 0.0032 | 0.0085 | 5.1797 | 4.9751 | 4.8364 | 4.9546 | 4.947 | 4.7524 | 29.6569 | 0.026691 |  | 62.069 | 100
19980925053000 | 1998-09-25 05:30 | 321.046 |  | 2.291 | 148.751 | 151.244 | 150.843 | 149.758 |  | 665.269 | 713.187 |  | 0.0047 | 0.0093 | 5.2131 | 4.9714 | 4.8608 | 4.9385 | 4.9348 | 4.7449 | 29.6775 | 0.02671 |  | 62.069 | 100
19980925060000 | 1998-09-25 06:00 | 423.833 |  | 0.082 | 148.997 | 152.821 | 151.562 | 150.346 |  | 844.524 | 922.776 |  | 0.0047 | 2.1523 | 6.4966 | 6.2454 | 5.8137 | 5.8389 | 5.8289 | 5.6978 | 38.0783 | 0.03427 |  | 62.069 | 100
19980925063000 | 1998-09-25 06:30 | 416.964 |  | 2.372 | 150.181 | 150.49 | 152.572 | 149.5 |  | 857.358 | 938.694 |  | 4.8638 | 4.7805 | 4.9546 | 4.689 | 4.6462 | 4.7212 | 4.718 | 4.5374 | 37.9107 | 0.03412 |  | 62.069 | 100
19980925070000 | 1998-09-25 07:00 | 424.934 |  | 0 | 148.598 | 151.444 | 151.293 | 149.216 |  | 840.774 | 920.11 |  | 4.8828 | 4.7866 | 4.9736 | 4.7166 | 4.6609 | 4.7371 | 4.7341 | 4.5449 | 38.0366 | 0.034233 |  | 62.069 | 100
19980925073000 | 1998-09-25 07:30 | 529.476 |  | 2.249 | 149.44 | 153.084 | 151.758 | 151.351 |  | 1040.947 | 1144.033 |  | 5.9229 | 5.8174 | 6.2974 | 6.009 | 5.6655 | 5.6443 | 5.6411 | 5.5161 | 46.5137 | 0.041862 |  | 62.069 | 100
19980925080000 | 1998-09-25 08:00 | 532.045 |  | 0.166 | 149.854 | 151.702 | 152.308 | 149.227 |  | 1105.698 | 1219.702 |  | 6.1211 | 6.1111 | 6.585 | 6.3591 | 5.8884 | 5.9075 | 5.9097 | 5.7725 | 48.6544 | 0.043789 |  | 62.069 | 100
19980925083000 | 1998-09-25 08:30 | 577.553 |  | 2.249 | 150.109 | 152.744 | 152.537 | 149.526 |  | 1188.784 | 1302.704 |  | 6.4294 | 6.3843 | 6.9756 | 6.6941 | 6.1738 | 6.1477 | 6.1455 | 6.0464 | 50.9968 | 0.045897 |  | 62.069 | 100
19980925090000 | 1998-09-25 09:00 | 571.026 |  | 0.081 | 149.357 | 150.686 | 151.837 | 147.221 |  | 1171.2 | 1287.954 |  | 6.4614 | 6.4033 | 6.9802 | 6.7224 | 6.1829 | 6.1638 | 6.1692 | 6.0601 | 51.1433 | 0.046029 |  | 62.069 | 100
19980925093000 | 1998-09-25 09:30 | 629.72 |  | 2.249 | 149.13 | 152.352 | 151.623 | 149.382 |  | 1283.453 | 1410.957 |  | 6.9932 | 6.9221 | 7.6829 | 7.3975 | 6.7109 | 6.6499 | 6.6528 | 6.5544 | 55.5637 | 0.050007 |  | 62.069 | 100
19980925100000 | 1998-09-25 10:00 | 632.76 |  | 0.284 | 149.12 | 152.389 | 151.865 | 148.428 |  | 1291.287 | 1423.124 |  | 7.0046 | 6.939 | 7.6699 | 7.4067 | 6.7146 | 6.6621 | 6.6682 | 6.5698 | 55.6349 | 0.050071 |  | 62.069 | 100
19980925103000 | 1998-09-25 10:30 | 627.675 |  | 1.757 | 148.744 | 151.295 | 151.061 | 148.573 |  | 1285.12 | 1410.374 |  | 7.0068 | 6.9412 | 7.6836 | 7.4043 | 6.7185 | 6.6758 | 6.6758 | 6.5781 | 55.6841 | 0.050116 |  | 62.069 | 100
19980925110000 | 1998-09-25 11:00 | 648.908 |  | 0.163 | 148.145 | 151.868 | 150.485 | 149.393 |  | 1301.787 | 1434.541 |  | 7.1487 | 7.1091 | 7.875 | 7.6125 | 6.8657 | 6.8367 | 6.8352 | 6.7246 | 57.0075 | 0.051307 |  | 62.069 | 100
19980925113000 | 1998-09-25 11:30 | 609.692 |  | 1.757 | 148.126 | 150.564 | 150.733 | 147.098 |  | 1231.535 | 1350.789 |  | 6.7864 | 6.717 | 7.3806 | 7.1313 | 6.498 | 6.4736 | 6.4712 | 6.3699 | 53.828 | 0.048445 |  | 62.069 | 100
19980925120000 | 1998-09-25 12:00 | 608.276 |  | 0.163 | 148.17 | 151.269 | 150.498 | 147.309 |  | 1227.535 | 1341.372 |  | 6.7971 | 6.7415 | 7.4028 | 7.1443 | 6.5132 | 6.4995 | 6.5002 | 6.3821 | 53.9807 | 0.048583 |  | 62.069 | 100
19980925123000 | 1998-09-25 12:30 | 610.924 |  | 1.879 | 148.429 | 151.177 | 150.971 | 147.959 |  | 1239.286 | 1352.455 |  | 6.7917 | 6.7375 | 7.406 | 7.1504 | 6.5088 | 6.4729 | 6.4783 | 6.3691 | 53.9147 | 0.048523 |  | 62.069 | 100
19980925130000 | 1998-09-25 13:00 | 611.71 |  | 0.159 | 148.805 | 151.399 | 151.08 | 148.676 |  | 1230.869 | 1347.622 |  | 6.7627 | 6.6909 | 7.3708 | 7.0825 | 6.4812 | 6.4507 | 6.4521 | 6.3354 | 53.6263 | 0.048264 |  | 62.069 | 100
19980925133000 | 1998-09-25 13:30 | 649.957 |  | 1.756 | 149.204 | 151.945 | 151.713 | 148.728 |  | 1304.121 | 1431.791 |  | 7.126 | 7.0977 | 7.8376 | 7.6074 | 6.8306 | 6.8215 | 6.8252 | 6.7109 | 56.8569 | 0.051171 |  | 62.069 | 100
19980925140000 | 1998-09-25 14:00 | 652.474 |  | 0.405 | 148.867 | 151.424 | 151.502 | 147.464 |  | 1295.787 | 1425.374 |  | 7.1077 | 7.0703 | 7.8164 | 7.573 | 6.813 | 6.7932 | 6.7993 | 6.6865 | 56.6594 | 0.050993 |  | 62.069 | 100
19980925143000 | 1998-09-25 14:30 | 581.983 |  | 2.003 | 147.962 | 149.485 | 150.305 | 145.03 |  | 1168.45 | 1280.537 |  | 6.4766 | 6.4216 | 7.042 | 6.7666 | 6.2219 | 6.1868 | 6.189 | 6.0806 | 51.3851 | 0.046247 |  | 62.069 | 100
19980925150000 | 1998-09-25 15:00 | 581.485 |  | 0.16 | 147.554 | 151.347 | 149.623 | 148.129 |  | 1153.033 | 1262.37 |  | 6.4331 | 6.3638 | 6.9641 | 6.6772 | 6.1638 | 6.1218 | 6.125 | 6.0173 | 50.8661 | 0.045779 |  | 62.069 | 100
19980925153000 | 1998-09-25 15:30 | 514.193 |  | 22.252 | 148.959 | 149.733 | 151.172 | 147.257 |  | 972.278 | 1072.447 |  | 5.6091 | 5.4878 | 5.8984 | 5.5671 | 5.3491 | 5.2888 | 5.2871 | 5.1887 | 43.6761 | 0.039308 |  | 62.069 | 100
19980925160000 | 1998-09-25 16:00 | 470.206 |  | 19.917 | 147.112 | 149.289 | 149.273 | 146.814 |  | 947.611 | 1044.447 |  | 5.4688 | 5.3552 | 5.7473 | 5.4573 | 5.2217 | 5.2131 | 5.2087 | 5.0735 | 42.7456 | 0.038471 |  | 62.069 | 100
19980925163000 | 1998-09-25 16:30 | 468.292 |  | 1.675 | 148.032 | 150.604 | 150.299 | 148.129 |  | 952.527 | 1047.03 |  | 5.3613 | 5.2461 | 5.5818 | 5.3269 | 5.104 | 5.0996 | 5.1011 | 4.9661 | 41.7869 | 0.037608 |  | 62.069 | 100
19980925170000 | 1998-09-25 17:00 | 427.581 |  | 0 | 148.623 | 151.269 | 151.125 | 149.784 |  | 818.107 | 890.276 |  | 4.7654 | 4.6685 | 4.8774 | 4.5601 | 4.5464 | 4.512 | 4.5181 | 4.4189 | 36.8668 | 0.03318 |  | 62.069 | 100
19980925173000 | 1998-09-25 17:30 | 423.544 |  | 1.798 | 148.557 | 150.021 | 150.979 | 148.288 |  | 865.275 | 950.611 |  | 4.8982 | 4.7959 | 5.0439 | 4.7654 | 4.6677 | 4.686 | 4.6821 | 4.5425 | 38.0817 | 0.034274 |  | 62.069 | 100
19980925180000 | 1998-09-25 18:00 | 368.835 |  | 0 | 148.59 | 149.655 | 150.832 | 149.16 |  | 791.689 | 862.941 |  | 0.004 | 0.0078 | 6.0349 | 5.8137 | 5.4497 | 5.4971 | 5.4917 | 5.3154 | 33.6143 | 0.030253 |  | 62.069 | 100
19980925183000 | 1998-09-25 18:30 | 335.726 |  | 2.249 | 147.734 | 149.293 | 150.251 | 148.303 |  | 713.104 | 772.856 |  | 0.0047 | 0.0093 | 6.2432 | 5.9922 | 5.6016 | 3.9125 | 3.8629 | 5.4641 | 31.0905 | 0.027981 |  | 62.069 | 100
19980925190000 | 1998-09-25 19:00 | 329.645 |  | 0 | 147.679 | 150.32 | 150.189 | 148.34 |  | 725.437 | 787.523 |  | 0.004 | 0.0078 | 6.5454 | 6.3569 | 5.8198 | 2.131 | 4.0369 | 5.7305 | 30.6323 | 0.027569 |  | 62.069 | 100
19980925193000 | 1998-09-25 19:30 | 213.332 |  | 1.387 | 147.718 | 146.726 | 149.993 | 146.231 |  | 452.013 | 537.182 |  | 0.0032 | 0.0101 | 4.6211 | 4.4092 | 5.0903 | 0.0024 | -0.0006 | 4.9988 | 19.1345 | 0.017221 |  | 62.069 | 100
19980925200000 | 1998-09-25 20:00 | 212.257 |  | 0 | 146.226 | 148.015 | 148.298 | 148.015 |  | 499.764 | 531.849 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 5.9333 | 0.0017 | 0.0002 | 5.8303 | 11.7882 | 0.010609 |  | 62.069 | 100
19980925203000 | 1998-09-25 20:30 | 215.953 |  | 1.922 | 146.676 | 148.613 | 148.744 | 148.861 |  | 536.515 | 542.849 |  | 0.004 | 0.0085 | 0.0055 | 0.0063 | -0.0014 | 0.0009 | 0.0002 | 0.004 | 0.028 | 2.52e-05 |  | 62.069 | 100
19980925210000 | 1998-09-25 21:00 | 155.162 |  | 0 | 147.512 | 150.867 | 149.957 | 151.114 |  | 576.6 | 486.847 |  | 0.004 | 0.0078 | 0.0032 | 0.0055 | -0.0014 | 0.0009 | 0.0002 | 0.004 | 0.0242 | 2.178e-05 |  | 62.069 | 100
19980925213000 | 1998-09-25 21:30 | 0 |  | 1.389 | 141.688 | 111.27 | 143.977 | 110.283 |  | 910.443 | 962.694 |  | 0.0032 | 0.007 | 0.0047 | 0.0063 | -0.0021 | 0.0024 | 0.0002 | 0.0024 | 0.0241 | 2.169e-05 |  | 62.069 | 100
19980925220000 | 1998-09-25 22:00 | -0.026 |  | 1.02 | 121.968 | 116.295 | 124.309 | 113.333 |  | 1440.958 | 1587.296 |  | 0.0024 | 0.0085 | 0.0047 | 0.0085 | -0.0006 | 0.0017 | 0.0002 | 0.0032 | 0.0286 | 2.574e-05 |  | 62.069 | 100
19980925223000 | 1998-09-25 22:30 | 0 |  | 2.003 | 109.095 | 95.299 | 110.431 | 93.576 |  | 1501.293 | 1661.131 |  | 0.004 | 0.0085 | 0.0032 | 0.0063 | 0.0009 | 0.0002 | 0.0002 | 0.0032 | 0.0265 | 2.385e-05 |  | 62.069 | 100
19980925230000 | 1998-09-25 23:00 | -0.026 |  | 0.656 | 91.755 | 81.514 | 92.801 | 79.797 |  | 1499.043 | 1656.798 |  | 0.004 | 0.0085 | 0.0047 | 0.0063 | -0.0006 | 0.0002 | -0.0006 | 0.0032 | 0.0257 | 2.313e-05 |  | 62.069 | 100
19980925233000 | 1998-09-25 23:30 | 0 |  | 0 | 79.06 | 70.62 | 79.831 | 68.664 |  | 1503.626 | 1662.381 |  | 0.004 | 0.007 | 0.004 | 0.0055 | -0.0021 | 0.0002 | -0.0021 | 0.0055 | 0.022 | 1.98e-05 |  | 62.069 | 100
19980926000000 | 1998-09-26 | 0 |  | 0 | 68.967 | 62.2 | 69.553 | 60.737 |  | 1495.293 | 1657.214 |  | 0.0047 | 0.0078 | 0.004 | 0.0047 | -0.0029 | 0.0009 | 0.0002 | 0.0024 | 0.0218 | 1.962e-05 |  | 62.069 | 100
19980926003000 | 1998-09-26 00:30 | 0 |  | 0 | 60.996 | 55.431 | 61.453 | 54.458 |  | 1491.209 | 1656.298 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | -0.0014 | 0.0002 | -0.0014 | 0.004 | 0.0227 | 2.043e-05 |  | 62.069 | 100
19980926010000 | 1998-09-26 01:00 | -0.026 |  | 0 | 54.352 | 49.14 | 54.717 | 48.654 |  | 1472.626 | 1632.714 |  | 0.0024 | 0.007 | 0.004 | 0.0055 | 0.0017 | 0.0032 | 0.0002 | 0.0024 | 0.0264 | 2.376e-05 |  | 62.069 | 100
19980926013000 | 1998-09-26 01:30 | 0 |  | 0 | 49.09 | 45.094 | 49.38 | 44.125 |  | 1468.375 | 1638.047 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | -0.0029 | 0.0002 | 0.0002 | 0.0063 | 0.0242 | 2.178e-05 |  | 62.069 | 100
19980926020000 | 1998-09-26 02:00 | -0.026 |  | 0 | 44.88 | 39.937 | 45.076 | 39.937 |  | 1475.959 | 1640.964 |  | 0.004 | 0.0085 | 0.0055 | 0.0047 | -0.0014 | 0.0009 | -0.0014 | 0.0032 | 0.024 | 2.16e-05 |  | 62.069 | 100
19980926023000 | 1998-09-26 02:30 | 0 |  | 0 | 41.245 | 47.543 | 41.431 | 48.513 |  | 353.427 | 530.099 |  | 0.0032 | 0.0078 | 0.0032 | 0.0063 | -0.0029 | 0.0009 | 0.0002 | 0.0024 | 0.0211 | 1.899e-05 |  | 62.069 | 100
19980926030000 | 1998-09-26 03:00 | 0.026 |  | 0 | 48.169 | 46.381 | 48.512 | 46.866 |  | 446.513 | 682.103 |  | 0.004 | 0.0085 | 0.0047 | 0.0047 | -0.0014 | 0.0009 | 0.0002 | 0.0032 | 0.0248 | 2.232e-05 |  | 62.069 | 100
19980926033000 | 1998-09-26 03:30 | -0.026 |  | 0 | 44.883 | 37.482 | 45.663 | 38.207 |  | 444.179 | 688.603 |  | 0.0024 | 0.0078 | 0.0047 | 0.0063 | -0.0044 | 0.0024 | 0.0002 | 0.0032 | 0.0226 | 2.034e-05 |  | 62.069 | 100
19980926040000 | 1998-09-26 04:00 | 0 |  | 0 | 38.181 | 32.56 | 39.188 | 33.523 |  | 443.513 | 696.353 |  | 0.0032 | 0.0078 | 0.0032 | 0.0047 | 0.0009 | 0.0009 | -0.0014 | 0.0032 | 0.0225 | 2.025e-05 |  | 62.069 | 100
19980926043000 | 1998-09-26 04:30 | -0.026 |  | 0 | 33.695 | 29.697 | 34.555 | 29.938 |  | 442.929 | 705.27 |  | 0.0032 | 0.0085 | 0.0047 | 0.0047 | -0.0006 | 0.0009 | -0.0006 | 0.0032 | 0.024 | 2.16e-05 |  | 62.069 | 100
19980926050000 | 1998-09-26 05:00 | -0.026 |  | 0 | 30.904 | 28.546 | 31.552 | 28.546 |  | 443.429 | 712.77 |  | 0.004 | 0.0085 | 0.0032 | 0.0047 | 0.0009 | 0.0002 | 0.0002 | 0.0017 | 0.0234 | 2.106e-05 |  | 62.069 | 100
19980926053000 | 1998-09-26 05:30 | 0 |  | 0 | 29.077 | 26.549 | 29.594 | 27.029 |  | 443.013 | 721.937 |  | 0.0024 | 0.0093 | 0.0047 | 0.0063 | 0.8295 | 0.0002 | -0.0014 | 0.0032 | 0.8542 | 0.00076878 |  | 62.069 | 100
19980926060000 | 1998-09-26 06:00 | 0 |  | 0 | 28.022 | 26.574 | 28.519 | 26.814 |  | 600.184 | 0.167 |  | 0.004 | 0.007 | 0.0047 | 0.0063 | -0.0021 | 0.0009 | 0.0002 | 0.004 | 0.025 | 2.25e-05 |  | 62.069 | 100
19980926063000 | 1998-09-26 06:30 | 0 |  | 0 | 27.855 | 26.384 | 28.14 | 26.864 |  | 600.184 | 0.417 |  | 0.0047 | 0.007 | 0.0047 | 0.0063 | 0.4556 | -0.0006 | 0.0002 | 0.004 | 0.4819 | 0.00043371 |  | 62.069 | 100
19980926070000 | 1998-09-26 07:00 | 0 |  | 0 | 27.543 | 25.614 | 27.768 | 26.334 |  | 600.017 | 0.333 |  | 0.0047 | 0.0085 | 0.0032 | 0.0055 | 1.7419 | 1.5321 | 0.0009 | 0.004 | 3.3008 | 0.0029707 |  | 62.069 | 100
19980926073000 | 1998-09-26 07:30 | -0.026 |  | 0 | 26.949 | 24.125 | 27.227 | 25.564 |  | 852.941 | 0.25 |  | 0.004 | 0.007 | 0.004 | 0.0078 | 2.2294 | 0.0024 | -0.0014 | 0.0032 | 2.2564 | 0.0020308 |  | 62.069 | 100
19980926080000 | 1998-09-26 08:00 | 0 |  | 0 | 25.963 | 23.886 | 26.381 | 25.085 |  | 143.254 | 0.083 |  | 0.0032 | 0.0078 | 0.0055 | 0.0063 | 2.4904 | 0.0009 | 0.0002 | 0.0032 | 2.5175 | 0.0022658 |  | 62.069 | 100
19980926083000 | 1998-09-26 08:30 | -0.026 |  | 0 | 25.832 | 24.895 | 26.14 | 24.655 |  | 351.093 | 0.083 |  | 0.0024 | 0.0085 | 0.004 | 0.0063 | 2.6666 | 0.0009 | 0.0009 | 0.004 | 2.6936 | 0.0024242 |  | 62.069 | 100
19980926090000 | 1998-09-26 09:00 | -0.026 |  | 0 | 25.912 | 24.226 | 25.889 | 24.945 |  | 353.177 | 0 |  | 0.0032 | 0.0101 | 0.0055 | 0.0055 | 2.8123 | 0.0017 | -0.0021 | 0.0032 | 2.8394 | 0.0025555 |  | 62.069 | 100
19980926093000 | 1998-09-26 09:30 | -0.026 |  | 0 | 26.054 | 25.085 | 25.762 | 24.365 |  | 354.094 | 0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.0063 | 2.9313 | 0.0009 | -0.0006 | 0.0047 | 2.9576 | 0.0026618 |  | 62.069 | 100
19980926100000 | 1998-09-26 10:00 | 0 |  | 0 | 26.066 | 24.44 | 25.567 | 24.92 |  | 354.927 | -0.167 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 3.0259 | 0.0009 | 0.0002 | 0.004 | 3.0537 | 0.0027483 |  | 62.069 | 100
19980926103000 | 1998-09-26 10:30 | 0 |  | 0 | 26.06 | 24.58 | 25.564 | 25.539 |  | 356.177 | 0.333 |  | 0.0024 | 0.0085 | 0.004 | 0.0063 | 3.1235 | 0.0002 | 0.0002 | 0.0032 | 3.1483 | 0.0028335 |  | 62.069 | 100
19980926110000 | 1998-09-26 11:00 | -0.026 |  | 0 | 26.211 | 24.68 | 25.816 | 25.639 |  | 356.51 | 0.083 |  | 0.0024 | 0.0085 | 0.0063 | 0.0055 | 3.1991 | 0.0009 | 0.0002 | 3.4174 | 6.6403 | 0.0059763 |  | 62.069 | 100
19980926113000 | 1998-09-26 11:30 | -0.026 |  | 0 | 26.283 | 25.614 | 26.094 | 25.854 |  | 359.51 | 0 |  | 0.004 | 0.0085 | 0.004 | 0.004 | 3.2517 | 0.0009 | 0.0002 | 1.1903 | 4.4636 | 0.0040172 |  | 62.069 | 100
19980926120000 | 1998-09-26 12:00 | 0 |  | 0 | 26.244 | 24.605 | 26.32 | 25.804 |  | 361.094 | 0 |  | 0.004 | 0.007 | 0.0055 | 0.0078 | 3.3265 | 0.0017 | -0.0014 | 0.6349 | 3.986 | 0.0035874 |  | 62.069 | 100
19980926123000 | 1998-09-26 12:30 | 0 |  | 0 | 26.068 | 24.845 | 26.539 | 25.564 |  | 362.76 | 0.333 |  | 0.004 | 0.0078 | 0.004 | 0.0063 | 3.3899 | 0.0009 | 0.0002 | 1.1506 | 4.5637 | 0.0041073 |  | 62.069 | 100
19980926130000 | 1998-09-26 13:00 | 0 |  | 0 | 25.953 | 24.075 | 26.764 | 25.994 |  | 364.677 | 0.25 |  | 0.0032 | 0.0078 | 0.0047 | 0.0063 | 3.4395 | 0.0009 | -0.0014 | 1.8235 | 5.2845 | 0.004756 |  | 62.069 | 100
19980926133000 | 1998-09-26 13:30 | -0.026 |  | 0 | 25.833 | 24.505 | 27.143 | 27.144 |  | 363.927 | 0.083 |  | 0.0032 | 0.0085 | 0.0055 | 0.0063 | 3.4937 | -0.0006 | -0.0014 | 0.6136 | 4.1288 | 0.0037159 |  | 62.069 | 100
19980926140000 | 1998-09-26 14:00 | 0 |  | 0 | 25.826 | 24.365 | 27.501 | 26.284 |  | 364.01 | 0.417 |  | 0.0024 | 0.0078 | 0.0032 | 0.0063 | 3.5531 | 0.0002 | 0.0017 | 1.89 | 5.4647 | 0.0049182 |  | 62.069 | 100
19980926143000 | 1998-09-26 14:30 | -0.026 |  | 0 | 25.623 | 23.936 | 27.708 | 26.094 |  | 364.844 | 0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.0055 | 3.5996 | 0.0009 | -0.0006 | 1.9678 | 5.5889 | 0.00503 |  | 62.069 | 100
19980926150000 | 1998-09-26 15:00 | -0.026 |  | 0 | 25.578 | 23.142 | 27.483 | 26.259 |  | 366.511 | 0.083 |  | 0.0047 | 0.0085 | 0.0047 | 0.0055 | 3.6493 | 0.0002 | 0.0002 | 0.847 | 4.5201 | 0.0040681 |  | 62.069 | 100
19980926153000 | 1998-09-26 15:30 | -0.026 |  | 0 | 25.285 | 23.696 | 27.196 | 26.094 |  | 370.677 | 0.167 |  | 0.004 | 0.0078 | 0.004 | 0.0055 | 3.682 | 0.0009 | 0.0002 | 2.0044 | 5.7088 | 0.0051379 |  | 62.069 | 100
19980926160000 | 1998-09-26 16:00 | -0.026 |  | 0 | 25.285 | 24.29 | 26.917 | 25.489 |  | 372.677 | 0 |  | 0.0032 | 0.0085 | 0.0047 | 0.0047 | 3.7233 | 0.0017 | 0.0002 | 0.0032 | 3.7495 | 0.0033746 |  | 62.069 | 100
19980926163000 | 1998-09-26 16:30 | -0.026 |  | 0 | 25.249 | 23.167 | 26.664 | 25.564 |  | 376.094 | 0 |  | 0.0032 | 0.007 | 0.004 | 0.0055 | 3.7599 | 0.0002 | 0.0002 | 0.0024 | 3.7824 | 0.0034042 |  | 62.069 | 100
19980926170000 | 1998-09-26 17:00 | -0.026 |  | 0 | 25.09 | 24.175 | 26.54 | 25.374 |  | 378.344 | 0.167 |  | 0.0032 | 0.0078 | 0.004 | 0.004 | 3.7911 | 0.0002 | -0.0014 | 0.0047 | 3.8136 | 0.0034322 |  | 62.069 | 100
19980926173000 | 1998-09-26 17:30 | -0.026 |  | 0 | 25.07 | 23.546 | 26.314 | 24.984 |  | 379.428 | 0.083 |  | 0.0024 | 0.0085 | 0.0055 | 0.0047 | 3.8118 | 0.0002 | 0.0002 | 0.3816 | 4.2149 | 0.0037934 |  | 62.069 | 100
19980926180000 | 1998-09-26 18:00 | 0.026 |  | 0 | 25.07 | 23.621 | 26.279 | 24.82 |  | 381.844 | 0.25 |  | 0.0032 | 0.0078 | 0.004 | 0.0047 | 3.824 | 0.0009 | 0.0002 | 1.1812 | 5.026 | 0.0045234 |  | 62.069 | 100
19980926183000 | 1998-09-26 18:30 | 0 |  | 0 | 24.895 | 23.167 | 26.26 | 24.845 |  | 384.344 | 0.333 |  | 0.0047 | 0.0078 | 0.004 | 0.0047 | 3.8369 | 0.0002 | 0.0002 | 0.0032 | 3.8617 | 0.0034755 |  | 62.069 | 100
19980926190000 | 1998-09-26 19:00 | 0 |  | 0 | 24.837 | 23.167 | 26.109 | 24.605 |  | 388.011 | 0 |  | 0.0047 | 0.0078 | 0.004 | 0.0063 | 3.8636 | 0.0032 | 0.0002 | 0.0024 | 3.8922 | 0.003503 |  | 62.069 | 100
19980926193000 | 1998-09-26 19:30 | 0 |  | 0 | 24.754 | 24.125 | 26.086 | 25.564 |  | 391.178 | -0.083 |  | 0.0032 | 0.0085 | 0.0047 | 0.0063 | 3.8629 | 0.0009 | -0.0014 | 0.3137 | 4.1988 | 0.0037789 |  | 62.069 | 100
19980926200000 | 1998-09-26 20:00 | -0.026 |  | 0 | 25.32 | 24.415 | 26.485 | 25.614 |  | 393.261 | 0 |  | 0.004 | 0.0085 | 0.0032 | 0.0055 | 3.8621 | 0.0009 | 0.0002 | 0.4266 | 4.311 | 0.0038799 |  | 62.069 | 100
19980926203000 | 1998-09-26 20:30 | 0 |  | 0 | 25.297 | 23.986 | 26.772 | 25.664 |  | 395.845 | 0.167 |  | 0.004 | 0.0085 | 0.0047 | 0.0047 | 3.8705 | 0.0009 | -0.0021 | 0.4938 | 4.385 | 0.0039465 |  | 62.069 | 100
19980926210000 | 1998-09-26 21:00 | 0 |  | 0 | 25.034 | 23.406 | 26.821 | 26.044 |  | 398.178 | 0 |  | 0.004 | 0.007 | 0.0047 | 0.0055 | 3.8743 | 0.0009 | 0.0002 | 1.0339 | 4.9305 | 0.0044374 |  | 62.069 | 100
19980926213000 | 1998-09-26 21:30 | 0 |  | 0 | 24.835 | 23.506 | 26.776 | 25.185 |  | 143.087 | 0.25 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | 3.8904 | 0.0009 | -0.0021 | 0.4594 | 4.369 | 0.0039321 |  | 62.069 | 100
19980926220000 | 1998-09-26 22:00 | 0 |  | 0 | 24.783 | 23.506 | 26.572 | 25.664 |  | 471.347 | 0 |  | 0.004 | 0.0085 | 0.0032 | 0.0047 | 3.9308 | 0.0009 | 0.0002 | 0.7387 | 4.691 | 0.0042219 |  | 62.069 | 100
19980926223000 | 1998-09-26 22:30 | 0 |  | 0 | 24.836 | 26.764 | 26.539 | 26.044 |  | 477.764 | 0.333 |  | 0.004 | 0.0078 | 0.0055 | 0.0047 | 3.9331 | 0.0032 | 0.0009 | 0.9546 | 4.9138 | 0.0044224 |  | 62.069 | 100
19980926230000 | 1998-09-26 23:00 | 0 |  | 0 | 29.879 | 39.988 | 26.936 | 26.499 |  | 484.264 | 0.167 |  | 0.0032 | 0.007 | 0.004 | 0.0055 | 3.9308 | 0.0002 | 0.0009 | 1.1072 | 5.0588 | 0.0045529 |  | 62.069 | 100
19980926233000 | 1998-09-26 23:30 | -0.026 |  | 0 | 39.46 | 40.37 | 27.263 | 27.119 |  | 488.014 | 0.417 |  | 0.0024 | 0.0085 | 0.0047 | 0.0063 | 3.9292 | 0.0009 | -0.0021 | 1.037 | 4.9869 | 0.0044882 |  | 62.069 | 100
19980927000000 | 1998-09-27 | 0 |  | 0 | 39.802 | 36.441 | 27.648 | 28.255 |  | 488.764 | 0.417 |  | 0.0047 | 0.0078 | 0.0047 | 0.0047 | 3.9552 | 0.0009 | -0.0021 | 1.3681 | 5.344 | 0.0048096 |  | 62.069 | 100
19980927003000 | 1998-09-27 00:30 | 0 |  | 0 | 38.099 | 35.743 | 28.679 | 30.203 |  | 395.178 | 0.167 |  | 0.0032 | 0.0085 | 0.004 | 0.0047 | 3.9651 | 0.0009 | 0.0002 | 1.5229 | 5.5095 | 0.0049585 |  | 62.069 | 100
19980927010000 | 1998-09-27 01:00 | 0 |  | 0 | 37.255 | 35.286 | 29.866 | 30.71 |  | 293.508 | 0.25 |  | 0.0032 | 0.0093 | 0.0047 | 0.0047 | 3.9735 | 0.0002 | -0.0014 | 1.1652 | 5.1594 | 0.0046435 |  | 62.069 | 100
19980927013000 | 1998-09-27 01:30 | 0.026 |  | 0 | 36.09 | 33.142 | 30.719 | 31.216 |  | 295.925 | 0.083 |  | 0.0024 | 0.0085 | 0.0055 | 0.0055 | 3.9789 | 0.0009 | 0.0002 | 0.4663 | 4.4682 | 0.0040214 |  | 62.069 | 100
19980927020000 | 1998-09-27 02:00 | 0.026 |  | 0 | 34.101 | 30.875 | 31.325 | 31.597 |  | 296.259 | 0.333 |  | 0.0032 | 0.0078 | 0.0047 | 0.0047 | 3.9918 | 0.0002 | 0.0002 | 0.5884 | 4.601 | 0.0041409 |  | 62.069 | 100
19980927023000 | 1998-09-27 02:30 | 0 |  | 0 | 32.192 | 29.622 | 31.72 | 31.547 |  | 298.842 | 0.083 |  | 0.0032 | 0.007 | 0.0047 | 0.0047 | 4.001 | 0.0002 | -0.0014 | 0.6418 | 4.6612 | 0.0041951 |  | 62.069 | 100
19980927030000 | 1998-09-27 03:00 | 0 |  | 0 | 30.852 | 28.18 | 31.87 | 31.306 |  | 299.009 | 0.167 |  | 0.0024 | 0.0093 | 0.0032 | 0.0047 | 4.0283 | 0.0017 | -0.0014 | 0.8585 | 4.9067 | 0.004416 |  | 62.069 | 100
19980927033000 | 1998-09-27 03:30 | 0 |  | 0 | 29.755 | 27.295 | 31.772 | 30.178 |  | 299.925 | 0.167 |  | 0.0032 | 0.0078 | 0.0055 | 0.0047 | 4.0444 | 0.0009 | -0.0006 | 0.8264 | 4.8923 | 0.0044031 |  | 62.069 | 100
19980927040000 | 1998-09-27 04:00 | 0 |  | 0 | 28.83 | 26.334 | 31.478 | 29.938 |  | 297.925 | 0.083 |  | 0.0032 | 0.0078 | 0.0047 | 0.0047 | 4.0559 | 0.0009 | 0.0002 | 0.7944 | 4.8718 | 0.0043846 |  | 62.069 | 100
19980927043000 | 1998-09-27 04:30 | 0 |  | 0 | 28.03 | 26.234 | 31.032 | 29.837 |  | 299.259 | 0.333 |  | 0.0024 | 0.007 | 0.004 | 0.0055 | 4.075 | 0.0017 | 0.0002 | 0.7768 | 4.8726 | 0.0043853 |  | 62.069 | 100
19980927050000 | 1998-09-27 05:00 | -0.026 |  | 0 | 27.423 | 25.614 | 30.523 | 29.217 |  | 300.675 | 0.167 |  | 0.004 | 0.007 | 0.0055 | 0.0047 | 4.0825 | 0.0009 | -0.0006 | 0.7455 | 4.8495 | 0.0043645 |  | 62.069 | 100
Formulas:
TIME LINE = +[TIME LINE, row above]+B7

## 25-30 MAY
SUGGEST YOU PLOT THE FOLLOWING FOR THE PERIOD 25 - 30 MAY:
(1) | BOILER LOAD AGAINST TIME
(2) | PARTICULATE ASH OUT OF ESP AND FLUE GAS TEMPERATURES AGAINST TIME
(3) | FLUE GAS FLOW AND FLUE GAS TEMPERATURES AGAINST TIME
(4) | ESP EFFICIENCY AND FLUE GAS TEMPERATURES AGAINST TIME

## 02-07 SEPT
SUGGEST YOU PLOT THE FOLLOWING FOR THE PERIOD 02- 07 SEPTEMBER:
(1) | BOILER LOAD AGAINST TIME
(2) | PARTICULATE ASH OUT OF ESP AND FLUE GAS TEMPERATURES AGAINST TIME
(3) | FLUE GAS FLOW AND FLUE GAS TEMPERATURES AGAINST TIME
(4) | ESP EFFICIENCY AND FLUE GAS TEMPERATURES AGAINST TIME